## Executive Summary
Executive Summary: Group 4 Limited Operation & Interim Availability Interconnection System Impact Study
Interconnection Customer (GEN-2020-056) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by or within a three (3) year extension of the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades. This amount is a preliminary calculation which includes all pending higher queued Interconnection Requests and previously assigned upgrades that requires further study to substantiate. Interconnection Customers are notified of these preliminary Limited Operation amounts with the posting of the DISIS report.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Sensitivity Dispatch Tab; added to identify diapatch variations from DISIS manual
- Stability Analysis Tab; added to include Stability analysis events and results
- Short Circuit Analysis Tab; added to include Short Circuit analysis results for year 10 summer peak case only
Models Used in Study
Power Flow Analysis: 2019 ITP Series
Light: 2024 (24L)
Summer: 2020 (20SP), 2024 (24SP), 2029 (29SP)
Spring: 2020 (20G)
Winter: 2019 (19WP), 2024 (24WP)
Stability analysis: 2018 Series MDWG Dynamics
Light: 2021 (21L)
Summer: 2021 (21SP), 2028 (28SP)
Winter: 2019 (19WP)
Short Circuit Analysis: 2018 Series MDWG Dynamics
Summer: 2028 (28SP)
Author: SPP Generator Interconnection Department
Published: 11/18/2021

## Revision History
Revision History
Date | Author | Change Description
2021-10-21 | S&C | For SPP review
2021-10-28 | S&C | Final revision
2021-11-18 | SPP | SPP Review Complete

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Service | Area | POI | Status | Reactive Compensation Requirements
GEN-2020-056 | 04 - Northwest Kansas | NA | NA | Solar | 20 | 20 | ER | SUNC | RUSSELL3 115kV | IASIS Stage | 0.25
GEN-2020-056 | 04 - Northwest Kansas | NA | NA | Solar | 20 | 0 | NR | SUNC | RUSSELL3 115kV | IASIS Stage | 0.25
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 2.5 | 0 | ER | SPS | Wolfforth 115kV | DISIS STAGE
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 4.2 | 0 | ER/NR | SPS | SPS Erskine 115kV | DISIS STAGE
GEN-2016-005 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | SUNC | Clark-Thistle 345kV | DISIS STAGE
GEN-2016-034 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 90 | 0 | ER | WAPA | Laramie River Station (GEN-2016-023 Tap)-Sidney 345kV | DISIS STAGE
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | AEPW | Chisholm-Gracemont 345kV | Exclude
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | 0 | ER | SPS | Swisher 115kV | Exclude
GEN-2016-049 | 03 - Spearville | 18 | DIS-17-1 | Wind | 310.2 | 55.8 | ER | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 300 | 0 | ER | OKGE | Renfrow 345kV | DISIS STAGE
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 54 | 0 | ER/NR | SPS | Lakeview-Brownfield 69kV line | DISIS STAGE
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 108 | 0 | ER/NR | SPS | Bailey County 115kV | DISIS STAGE
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | SPS | Yoakum-Seagraves 115kV circuit | DISIS STAGE
GEN-2016-093 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 70 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 250.7 | 0 | ER/NR | WAPA | Fort Thompson-Leland Olds 345kV | Exclude
GEN-2016-107 | 01 - Woodward | 18 | DIS-17-1 | Wind | 141.75 | 0 | ER/NR | WFEC | Okeene-Cederdale 138kV Line | DISIS STAGE
GEN-2016-109 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | NPPD | Fairbury 115kV | DISIS STAGE
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER/NR | AEPW | Shidler 138kV | DISIS STAGE
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | 0 | ER/NR | NPPD | Turtle Creek 345kV | Exclude
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 64 | 0 | ER | SPS | Hobbs-Yoakum 230kV | DISIS STAGE
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | 0 | ER | SPS | Newhart 115kV | Exclude
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 42 | 0 | ER/NR | WERE | Creswell 69kV Sub | DISIS STAGE
GEN-2017-001 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 250 | 0 | ER/NR | NPPD | Sweetwater 345kV | DISIS STAGE
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SUNC | Elm Creek - Summit 345kV | DISIS STAGE
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 195 | 0 | ER | WERE | Marmaton - Litchfield 161kV | Exclude
GEN-2017-006 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 73.6 | 0 | ER | NPPD | Moore (GEN-2015-088 Tap)-Pauline 345kV | DISIS STAGE
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | 0 | ER | SPS | Pleasant Hill 230kV sub | Exclude
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | 23 | ER | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | Exclude
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302.5 | 0 | ER | WERE | Neosho - Caney River 345kV | Exclude
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | WAPA | Rhame 230kV Sub | Exclude
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 0 | ER/NR | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | Exclude
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SPS | Newhart-Potter County 230kV | DISIS STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Mingo 345kV | DISIS STAGE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Underwood - Philip Tap 230kV | Exclude
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 190 | 21.5 | ER/NR | SUNC | Thistle 345kV sub | Exclude
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 0 | ER/NR | WERE | Altoona- NE Parson 138kV | Exclude
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 0 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | Exclude
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | WFEC | Frogville 138kV sub | Exclude
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | 8 | ER/NR | SPS | Tolk 230kV | Exclude
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 0 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | Exclude
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | OKGE | El Reno SW 138kV switch station | Exclude
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | 0 | ER | NPPD | Wildhorse - Covalt 115kV | Exclude
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SPS | Finney - Lamar 345kV | Exclude
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | WFEC | Snyder 138kV | Exclude
GEN-2017-037 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 20 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | SPS | Needmore 230kV sub | Exclude
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | SPS | Cole 115kV | DISIS STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Neset 230kV | Exclude
GEN-2017-049 | 03 - Spearville | 18 | DIS-17-1 | Solar | 50 | 0 | ER | MIDW | Tap Pawnee Valley - Hanston 69kV | DISIS STAGE
GEN-2017-050 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 25 | 0.6 | ER | WERE | Tap Neosho â€“ Crawford 69kV | DISIS STAGE
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | 2.6 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | Exclude
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | 0 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | Exclude
GEN-2017-053 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 50 | 8.9 | ER | WFEC | Tap Hollister SW - PSO Walters 69kV | DISIS STAGE
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | 0 | ER/NR | LES | Wagener 115kV Sub | Exclude
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Hosston 69kV | Exclude
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | 27 | ER | SPS | Hereford Northeast 115kV | DISIS STAGE
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | 0 | ER/NR | SPS | TUCO 230kV | Exclude
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 29.9 | ER | EMDE | LaRussell Energy Center 161kV | Exclude
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 0 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | Exclude
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 0 | ER/NR | WAPA | Underwood - Wayside 230kV | Exclude
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-066 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 150.75 | 0 | ER/NR | WFEC | Oney 138kV Sub | DISIS STAGE
GEN-2017-067 | 01 - Woodward | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | ER/NR | WERE | Wichita 345kV | Exclude
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 3.6 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | GRDA | Dry Gulch 161kV sub | Exclude
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Pryor Junction 138kV sub | Exclude
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 0 | ER/NR | OKGE | Hugo-Sunnyside 345kV | Exclude
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | AEPW | Chamber Springs 161kV sub | Exclude
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | AEPW | Explorer Claremore Tap EXCLART4 | Exclude
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | Exclude
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 49.88 | 0 | ER | SPS | Hart Industrial 115kV sub | DISIS STAGE
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | 0 | ER | SPS | Tolk 230kV | Exclude
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 300 | 0 | ER | SPS | Amarillo South-Swisher 230kV | DISIS STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 28.8 | ER | EMDE | Asbury Plant 161kV | Exclude
GEN-2017-083 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 100 | 0 | ER/NR | SUNC | Mingo 115kV | Exclude
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 89.25 | 0 | ER | SPS | Newhart-Swisher 230kV | DISIS STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0 | ER/NR | NPPD | Friend 115kV | Exclude
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | WERE | Viola 345kV | Exclude
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | SPS | Clovis Interchange 115kV | Exclude
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 150 | ER | KCPL | Adrian 161kV sub | Exclude
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 26.25 | 0 | ER | SPS | Lamton 115kV | DISIS STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | WAPA | Fort Thompson-Huron 230kV | Exclude
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | WAPA | Underwood 115kV Sub | Exclude
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 0 | ER/NR | SPS | Texas County 115kV | DISIS STAGE
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | 0 | ER/NR | SPS | Hobbs 230kV | Exclude
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
AshburyRetired | 08 - North Oklahoma/South Central Kansas | 17.5 | DIS-17-1-PQ | Retired Coal | 198 |  | ER | EMDE | Asbury Plant 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  | ER | WAPA
ASGI-2016-009 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 3 |  | ER | SPS | Wolfforth 12.47kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | Exclude
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | Exclude
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | Exclude
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | Exclude
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-135 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-136 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-140 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-143 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-144 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-002 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.35 |  | ER | SPS | SP-Yuma 115kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 0 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | Exclude
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
ASGI-2015-006 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Solar | 9 |  | ER | SWPA | Tupelo 138kV
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Nelson 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  | ER/NR | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  | ER | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-029 | 01 - Woodward | 14 | DIS-15-1 | Wind | 161 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/ON SCHEDULE
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  | ER | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  | ER | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  | ER | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-030 | 02 - Hitchland | 11 | DIS-13-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  | ER | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 30 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  | ER | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  | ER | SPS | Pleasant Hill 69kV | Commerical Operation
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  | ER | SPS | Herring 115kV | Commerical Operation
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  | ER | SPS | Hendricks 69kV | Commerical Operation
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commerical Operation
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commerical Operation
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  | ER | WERE | Westar 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  | ER | AECI | Remington 138kV | GIA Executed
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  | ER | SPS | Martin 115kV | Commerical Operation
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  | ER | OTP

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Priority | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Capacity or Upgrade Details | Scenario 1: Status or Available MW | Scenario 2: Status or Available MW
GEN-2020-056 | DISIS-2020 | NA | NA | ERIS/NRIS | RUSSELL3 115kV | Interim Study | NA | 20 | 0
132937 | DISIS-2017-001-P2 | NA | NA | NA | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | Not In-Service | Not In-Service
132936 | DISIS-2017-001-P2 | NA | NA | NA | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | Not In-Service | Not In-Service
132955 | DISIS-2017-001-P2 | NA | NA | NA | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | Not In-Service | Not In-Service
132954 | DISIS-2017-001-P2 | NA | NA | NA | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | Not In-Service | Not In-Service
NA | DISIS-2017-001-P1 | NA | NA | NA | NTC 200220 (Rplan) | NA | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | Not In-Service | Not In-Service
122705 | DISIS-2016-002-2 | NA | NA | NA | Hoyt - JEC 345kV Rebuild (DISIS-2016-002-2) | NA | Rebuild the existing JEC - Hoyt 345 kV line as double circuit 345 kV with normal/minimal emergency rating of 1792 MVA. Network upgrade shared by four requests: GEN-2016-111 | Not In-Service | Not In-Service
122793 | DISIS-2016-002-2 | NA | NA | NA | Reno 345/115 kV Transformer Ckt 1 (DISIS-2016-002-2) | NA | Replace existing Reno transformer with one rated 400/440. | Not In-Service | Not In-Service
122794 | DISIS-2016-002-2 | NA | NA | NA | Reno 345/115 kV Transformer Ckt 2 (DISIS-2016-002-2) | NA | Replace existing Reno transformer with one rated 400/440 | Not In-Service | Not In-Service
Note on J1: NRIS capacity is limited by ERIS Results. The highlighted available MW amount in Column I is the maximum LOIS or Interim Capacity.

## Constraints Summary
SCENARIO | Generation Interconnection Number | Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading % | TC Voltage | VMIN | VMAX | Detail
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 24SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 369 | 382 | 113.62 |  |  |  | Upgrade EVANS N4 - MAIZE 4 138kV ckt 1 to minimum 435MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 19WP0 | Base Case | 280 | 308 | 103.14 |  |  |  | Upgrade CIRCLE 3 - CIRC TX-1 115kV ckt 1 to minimum 289MVA/321MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 20SP0 29SP0 | 80545: 530686 RICE 6 230 530688 BUFLOCRK6 230 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | 73.1 | 73.1 | 102.11 |  |  |  | Upgrade ROLLHLS3 - EHALLTP3 115kV ckt 1 to minimum 75MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 29SP0 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | 280 | 308 | 149.48 |  |  |  | Upgrade CIRCLE 6 230/115kV ckt 1 to minimum 461MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 29SP0 | Base Case | 280 | 308 | 101.66 |  |  |  | Upgrade CIRCLE 3 - CIRC TX-1 115kV ckt 1 to minimum 285MVA/474MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 19WP0 | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | 160 | 187 | 112.14 |  |  |  | Upgrade DGRASSE4 - ROSEVLY4 138kV ckt 1 to minimum 210MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 20SP0 24SP0 19WP0 29SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | 101 | 101 | 139.12 |  |  |  | Upgrade SEWARD 3 - ST-JOHN3 115kV ckt 1 to minimum 141MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 29SP0 | 105460: 525824 TUCO_TR1 1 13.2 998064 UPDATE LATER 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 525824 TUCO_TR1 1 13.2 998071 UPDATE LATER 230 1 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 | 516 | 559 | 102.43 |  |  |  | Upgrade POTTER_CO 7 345/230kV ckt 1 to minimum 573MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 24SP0 24WP0 | Base Case | 280 | 308 | 107.05 |  |  |  | Upgrade CIRCLE 3 - CIRC TX-1 115kV ckt 1 to minimum 300MVA/462MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533035 CHISHLM4 138 533054 MAIZE 4 138 1 | 24SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 369 | 382 | 107.9 |  |  |  | Upgrade CHISHLM4 - MAIZE 4 138kV ckt 1 to minimum 413MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 29SP0 | P42:345:OKGE:SB_BOER7304 | 516 | 559 | 106.54 |  |  |  | Upgrade POTTER_CO 6 - WAUK 90343-A 230kV ckt 1 to minimum 596MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 20SP0 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | 280 | 308 | 101.67 |  |  |  | Upgrade CIRCLE 6 230/115kV ckt 1 to minimum 314MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533416 RENO 3 115 533429 MOUNDRG3 115 1 | 24SP0 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 218 | 262 | 125.12 |  |  |  | Upgrade RENO 3 - MOUNDRG3 115kV ckt 1 to minimum 328MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 24SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 400 | 430 | 103.05 |  |  |  | Upgrade WICHITA7 345/138kV ckt 1 to minimum 444MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 24SP0 24WP0 | Base Case | 280 | 308 | 105.19 |  |  |  | Upgrade CIRCLE 6 230/115kV ckt 1 to minimum 295MVA/454MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 20SP0 | Base Case | 280 | 308 | 100.18 |  |  |  | Upgrade CIRCLE 3 - CIRC TX-1 115kV ckt 1 to minimum 281MVA/321MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533429 MOUNDRG3 115 997898 MOUN TX-2 115 1 | 24SP0 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 239 | 239 | 136.12 |  |  |  | Upgrade MOUNDRG3 - MOUN TX-2 115kV ckt 1 to minimum 326MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 24SP0 29SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | 101 | 101 | 121.59 |  |  |  | Upgrade GBENDTP3 - SEWARD 3 115kV ckt 1 to minimum 123MVA RateB rating.
S2 | G07_G077&G085 | 04NR | NRIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L0 19WP0 29SP0 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 319 | 351 | 141.18 |  |  |  | Upgrade SMOKYHL6 - SUMMIT 6 230kV ckt 1 to minimum 496MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533040 EVANS N4 138 997933 WICH TX-12 138 1 | 24SP0 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 400 | 430 | 102.95 |  |  |  | Upgrade EVANS N4 - WICH TX-12 138kV ckt 1 to minimum 443MVA RateB rating.
S2 | G07_G077&G085 | 04NR | NRIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 20G0 | 92479: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | 1076 | 1076 | 105.27 |  |  |  | Upgrade HOYT 7 - JEC N 7 345kV ckt 1 to minimum 1133MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533040 EVANS N4 138 997932 WICH TX-12 138 1 | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 400 | 430 | 112.79 |  |  |  | Upgrade EVANS N4 - WICH TX-12 138kV ckt 1 to minimum 485MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532796 WICHITA7 345 997932 WICH TX-12 138 1 | 29SP0 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | 400 | 430 | 113.39 |  |  |  | Upgrade WICHITA7 345/138kV ckt 1 to minimum 488MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 533013 MOUND 4 138 997898 MOUN TX-2 115 1 | 24SP0 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 250 | 275 | 118.91 |  |  |  | Upgrade MOUND 4 138/115kV ckt 1 to minimum 328MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 19WP0 | Base Case | 280 | 308 | 101.82 |  |  |  | Upgrade CIRCLE 6 230/115kV ckt 1 to minimum 286MVA/315MVA RateA/RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 19WP0 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | 1016 | 1016 | 104.34 |  |  |  | Upgrade NEOSHO 7 - LACYGNE7 345kV ckt 1 to minimum 1061MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Non-Converge | Non-Converge | 20SP0 24SP0 19WP0 24WP0 29SP0 | NA |  |  | NConv
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 6 GOLDN3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8751 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PUCKET 3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8123 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EUDORA 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9008 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KEENE 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8867 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-115 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8381 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOYT 7 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9078 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLINE 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8858 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EXIDE 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8568 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CITIES 3 115.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8875 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRINGH3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9171 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WILDCAT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9184 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CENCITY7 115.0kV | 29SP0 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 |  |  |  | 0.872 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIBLEY 5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8734 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HARBNGR7 345.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8439 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DOBSON 3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8443 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CHASE 3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8117 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AVENUECTY 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.849 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KETCHEM7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.799 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PRAIRIE3 115.0kV | 24WP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8643 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JOHNCR 3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7827 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CIRCLE 6 230.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8992 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STULL 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8923 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ROCKCRK2 69.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8808 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MC REAC2 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8216 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MC REAC3 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8216 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILL6 230.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8798 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S. WIND3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.838 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOONLTJ3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9234 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SANTAFJ2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8723 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SCRANTN3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8704 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S1263 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9402 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 2MADISN2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8719 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ST JOE 3 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8677 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-030-TAP 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8922 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WALKMYR3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.853 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OSAGE J3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8644 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ORRICK 5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8708 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ARNOLD 2 69.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9056 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | N-CIMRN3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8824 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-163 345.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9377 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILE3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.885 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DAVIS 3 115.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8895 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TRANSFORMER 345.0kV | 19WP0 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8787 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G14_001_1 345.0kV | 19WP0 29SP0 | P23:345:WERE:JEC_345-17:: |  |  |  | 0.9295 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MORRIS-3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8394 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HARBNGR3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8519 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 2MADISN3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8697 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEC U4 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9134 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SADLHRN3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8864 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CMRIVTP3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8918 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-046 345.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8962 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIBLEYPL 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8748 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SHAWNEE3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8813 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SALTCRK3 115.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8891 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HTI JCT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9109 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 27CROCO3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8808 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLINE 2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8927 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G14_001T 345.0kV | 19WP0 29SP0 | P23:345:WERE:JEC_345-17:: |  |  |  | 0.9295 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MUND 3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9233 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MW SOLV2 69.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9052 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-032-TAP 345.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8453 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | E-LIBER3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8989 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OSBORN7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.799 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NLIB 3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.891 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CHAPMAN3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.9127 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KSU E 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9163 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MURLEN 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8949 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G16-046-TAP 345.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8962 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EXIDE J3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8587 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | THISTLE7 345.0kV | 19WP0 29SP0 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.9187 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MIDLADS3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9079 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JOHNSON2 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.787 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EAST ST3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8603 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ECKLES-161 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8757 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLUMILS5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8788 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PAWNEE 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8634 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LARNED3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8628 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PRQN_WIND5 161.0kV | 29SP0 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8965 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KISMET 3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8977 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KU CAMP3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8967 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GARDNER5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8928 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SMOKYHLLS3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8568 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MIDWAY_5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.883 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CNTRLPL3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8963 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EMPEC 7 345.0kV | 29SP0 | P23:345:WERE:JEC_345-17:: |  |  |  | 0.9306 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PILE 3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.891 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MANTER 2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8506 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WGARDNR5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.894 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BRKRIDG5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8989 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NESCTY 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8912 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FAIRGDS3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8981 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BEELER 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8958 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | INDIANH3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8754 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | INDNOLA3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.874 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WMBROSJ3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.87 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEC W 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.885 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MANVILE3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.886 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SEWARD-3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8886 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SOUTHTN3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9209 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FLETCHR3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7621 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KERFORD3 115.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9187 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KSU W 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9163 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | F MONRO2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8931 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 4VAN N 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8697 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CARPENTER 7 345.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8439 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-016 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8717 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AMOCO 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8973 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PLSTVAL5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8941 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LBRTYST5 161.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8978 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEC U5 6 230.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.905 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-005-TAP 161.0kV | 29SP0 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.9269 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOUNDRG3 115.0kV | 19WP0 29SP0 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8902 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLAYCM25 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8931 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OLATHE 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8982 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MCDOWEL6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9091 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUMMIT 3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8629 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REFINRY3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8905 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2015-073 345.0kV | 29SP0 | P23:345:WERE:JEC_345-17:: |  |  |  | 0.9304 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILW3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.885 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HLLMRK 5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.889 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MNTCLLO3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9291 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TCHOPE 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8912 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIBLEY 7 345.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8561 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HUMBOLT5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9274 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WREN 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9082 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 41CALIF3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8779 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S1398 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9292 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRINT25 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8956 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DAKOTA_5 161.0kV | 29SP0 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8984 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SMANHAT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9054 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CITYSVC2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8778 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CARB-KW 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8769 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PARALEL3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9152 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ROCKCK7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8377 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-162 345.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9377 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WTCLF 3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8389 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PRATTWF7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9425 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 19THSTJ3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.897 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MCDOWEL3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9126 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLSPE 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8853 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WEMPORI3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8683 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWISVAL7 345.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9041 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EDUCATE3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8722 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FT JCT 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9163 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MWIRONJ2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8975 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ETHNOL 3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8894 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STRANGR3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9277 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-021-TAP 345.0kV | 19WP0 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.2639 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 29EVENG3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.873 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AUBURN 6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8863 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OSAGE 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8634 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SG11KOC2 69.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9192 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LANG 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8608 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRUCE 3 115.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9228 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JARBALO3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9268 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BENTON 7 345.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9365 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2017-052 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7684 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDWILO3 345.0kV | 19WP0 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.0632 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 3 VANBU2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8933 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 166TH 3 115.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9286 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SATMKEC3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8981 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | UNIONRG6 230.0kV | 19WP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9089 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NORTHST3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8618 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TRIBUNE3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7695 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NCFOUND3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9155 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CIRCLE 3 115.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8994 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CROOKED3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8807 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWITZER5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8959 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRANT 3 115.0kV | 24SP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8518 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WHEATLD3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.897 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIB REA1 345.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8561 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANZIO 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9126 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SAVANAH2 69.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8874 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SANTAFE2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8723 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WAVERLY3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9277 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NESSCTY3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8912 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ROSEHIL7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9461 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | QUARRY 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8933 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ODESSA 5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8699 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SEOTTWA5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8954 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PK_GOAB3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8123 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RENO 3 115.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8981 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JCTCTY 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9149 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ST-JOHN3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.881 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WMBROS 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.87 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRGHL 5 161.0kV | 24SP0 29SP0 | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 |  |  |  | 0.9133 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TONGATP3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9173 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BEARCRK3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7573 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S1399 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9312 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NORTONV2 69.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8919 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NINN1WF7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9425 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MCPHER 3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8928 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RENO 7 345.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.9025 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ULYSPLT3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8247 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NW LEAV3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9279 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEVEE 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9143 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HARTLND3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8787 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KSAVWTP3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8384 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SMAN_W_3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9054 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | P1 MPT PRI 345.0kV | 19WP0 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8794 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MWIRON 2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8975 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RVROAD 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8952 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STAGGHL3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9161 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DUNCAN 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8832 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G16-050-TAP 345.0kV | 19WP0 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.2798 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MULLNCR7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8216 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEX161 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8664 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DEERCRK2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8736 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MANTERT2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8525 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CNTRLXN3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8763 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | UNIONRG3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8926 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WATHENA2 69.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8699 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOONLIT3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.922 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KINSLEY3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8717 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JAGGARD3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9283 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KANARAD3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8696 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-122 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9122 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HILSBOR3 115.0kV | 19WP0 29SP0 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 |  |  |  | 0.8729 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EMCPHER6 230.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8897 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRGCRK3 115.0kV | 19WP0 29SP0 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 |  |  |  | 0.8792 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FRTLEAV3 115.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9239 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-073 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9205 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EEUREKA3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8539 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ASGI15_001_1 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8919 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ALXNDR 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8894 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HICKOCK3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8985 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-149 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9363 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-004-TAP 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9153 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PAWN-ED3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8694 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | READING3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8612 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WJCCTYW3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9156 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWNDTAP3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.838 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEARY 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9209 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HEIZER 6 230.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8908 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DVISTA 6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.914 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FORBES 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8774 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AXTELL 3 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.054 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NMANHT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9203 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEARY 7 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9064 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FLORENC3 115.0kV | 19WP0 29SP0 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 |  |  |  | 0.881 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RANSOM 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8977 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EMANHAT6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.917 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRDNCTY3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8377 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AMELIA 3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9169 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 2ND ELM2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8938 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOYT 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9106 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S ALMA 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8941 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JEC 6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.919 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SYRACUS3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7452 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EMCPHER3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.891 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GARDNCY2 69.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8487 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SHARNSP3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8118 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWLWRNC3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.898 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S.OTTWA5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8958 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BRMGHAM5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8934 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NATBEEF3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8971 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUMMIT 6 230.0kV | 19WP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9093 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SCHILNG3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8569 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOONLT 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8925 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRANTTP3 115.0kV | 24SP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8521 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JEC N 7 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.919 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NSI 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8835 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 87TH 7 345.0kV | 24SP0 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8977 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRTBEND6 230.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8907 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | THORNTN3 115.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9228 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STULL T3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8923 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SAT-TAP3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8981 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RICE 6 230.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8966 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MATTERS3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9149 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEOTI 3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8414 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 17&FAIR3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8724 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HAYNE3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8834 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HAWTH 7 345.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8638 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 19THST 3 115.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8964 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PEIL 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9186 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | P2 MPT PRI 345.0kV | 19WP0 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8797 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WJCCTY 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9156 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RTCHFLD5 161.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8935 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LAWHILL6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9044 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SALINA 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8578 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EDWARDS3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8703 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CRAIG 7 345.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8961 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SO GATE3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.858 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NASHUA 7 345.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8685 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NPHILPJ3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8583 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LBRTYWT5 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8931 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S GAGEE3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.875 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MAPLE J2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8942 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MUSCOTA2 69.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8728 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RILEY 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8957 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NINNESC3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8919 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEC U3 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9111 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VIOLA 7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.941 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BUFF_DUNES 7 345.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8776 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BUFFALO7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9205 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CIRCLVL3 115.0kV | 29SP0 | P23:345:WERE:JEC_345-17:: |  |  |  | 0.9192 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALLEY22 69.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8826 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ST JOHN3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8811 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLBY 2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 1.2794 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-088 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.799 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HASKELL3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8963 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-050 345.0kV | 19WP0 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.2798 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PLTCTY 5 161.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8998 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WMCPHER3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.895 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CEDARNL5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8936 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CORONAD3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8718 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STRANGR7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.916 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TRIB SW3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7746 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 6TH ST 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9058 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RICHMND5 161.0kV | 24SP0 19WP0 29SP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8654 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HUGOTON3 115.0kV | 24SP0 19WP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8537 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KINGMAN7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9415 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BIG BOW 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8017 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NEKOMA 3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8943 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OAKGRV 5 161.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8987 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BONITA 3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9184 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 12&CLAY3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.87 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 4VAN 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8697 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CIM-PLT3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8825 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOLT_REACT7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8463 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MIDLADN3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9079 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RICHFLD2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8447 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TCSEVRN3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.91 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | QUINTON3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8707 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WALNUT 2 69.0kV | 24SP0 29SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.907 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G15_021_1 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7827 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MORRIS 6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9052 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SHERWOD3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.879 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LWRNCHL3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9117 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SEMCRDE3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8833 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SELKIRK3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8196 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | E-PINE 3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8989 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SEWARD 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8948 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WILLIAM3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7466 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NCTYSVC2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.878 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILL5 161.0kV | 19WP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8826 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | N TYLER3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.871 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BNSF 5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.8933 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | W-LIBER3 115.0kV | 24SP0 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 |  |  |  | 0.8917 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LANG 7 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8608 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NTHLAND3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.878 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRAINVL5 161.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.8999 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUMMIT 7 345.0kV | 19WP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9115 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NMANHT6 230.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9177 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PENTAGN3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9283 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FMC 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9039 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 4VAN S 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8697 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WICHITA7 345.0kV | 29SP0 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 |  |  |  | 0.9171 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EFAIRMNT3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9252 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EDMOND5 161.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8998 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MIDWY2 2 69.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8829 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RULETON3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8991 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CRAWFRD3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.856 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ELLIS 2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8864 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-052-TAP 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7684 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G16-111-TAP 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9019 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GANO 3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.871 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IRSKDOL3 115.0kV | 19WP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8386 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WALNUT 3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.914 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MWIRNJ22 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8975 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HALLMRK3 115.0kV | 24SP0 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 |  |  |  | 0.9216 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NSI TAP3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8841 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOOKJCT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8849 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MARMTNE5 161.0kV | 29SP0 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.9129 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLSPW 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8882 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BISMARK3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9028 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S1280 5 161.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.9345 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | POSTROCK7 345.0kV | 19WP0 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 1.2502 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 4CORNER3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.876 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEC 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.885 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AUBURN 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8808 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | E MADSN2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8932 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HTI 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9107 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EMANHAT3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9144 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FINNEY 7 345.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8728 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLAYGEN3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.886 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEC E 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.885 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOUND 4 138.0kV | 29SP0 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9045 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOCKBRD3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8986 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HICKOCK2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.893 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CHENEY 2 69.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9265 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WM BROS3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8787 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MC REAC1 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8216 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MORRIS 7 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9061 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MARMTNW5 161.0kV | 29SP0 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.913 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DAVIS 2 69.0kV | 29SP0 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.8977 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 54&MERI3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8893 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MIDLAND6 230.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9041 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GALE 2 69.0kV | 29SP0 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 |  |  |  | 0.9162 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MORRIS 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8979 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PRATT 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8952 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RANSOM 2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8943 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BALDCRK3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9039 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LAMAR7 345.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8338 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLAYCTR3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.89 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PRAXAIR2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.891 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G17-030-SWYD 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.839 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WTCLFTP3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8392 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLARKCOUNTY7 345.0kV | 19WP0 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8787 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWISVAL6 230.0kV | 24SP0 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8945 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PHILIPS3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8588 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 29 GAGE3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8724 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JOHNCR 2 69.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8559 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PIONEER3 115.0kV | 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8468 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLAYCM15 161.0kV | 24SP0 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8977 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEC 2 69.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8775 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NORTHVW3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8692 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PALMER3 115.0kV | 19WP0 29SP0 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7827 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AEC 3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8823 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | G16-122-TAP 345.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.9068 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2017-030 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.839 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TIMBRLN3 115.0kV | 24SP0 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9254 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EABILEN3 115.0kV | 29SP0 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.8871 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VAUGHN 3 115.0kV | 29SP0 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 |  |  |  | 0.8638 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BULLCRK5 161.0kV | 29SP0 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 |  |  |  | 0.894 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOLT 7 345.0kV | 19WP0 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 |  |  |  | 0.8463 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CLAYCSS3 115.0kV | 29SP0 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 |  |  |  | 0.886 | 0.93 | 1.05

## All Thermal
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONITORED ELEMENT | RATEA (MVA) | RATEB (MVA) | TDF | TC% LOADING (% MVA) | CONTINGENCY | Footprint | BC LOADING (% MVA) | LOADING Diff (% MVA)
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 6e-05 | 166.69 | P23:500:EES-EAI:WH_BLF:B7914 | External | 166.7 | -0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 140.3 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.31 | -0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0003 | 114.96 | P23:500:EES-EAI:WH_BLF:B7914 | External | 114.96 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 105.27 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | Internal | 105.15 | 0.12
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 111.1 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 111.09 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0003 | 113.4 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.4 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00052 | 125.69 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 125.68 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0003 | 117.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 117.79 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.0005 | 110.41 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 110.44 | -0.03
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00052 | 125.69 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 125.68 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 102.28 | 104728: 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Internal | 102.16 | 0.12
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 121.05 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 121.04 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.0005 | 110.87 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 110.86 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 130.2 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 130.2 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 101.89 | 92478: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Internal | 101.76 | 0.13
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 130.2 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 130.2 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 102.28 | 92347: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Internal | 102.16 | 0.12
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 105.27 | 92350: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | Internal | 105.15 | 0.12
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0003 | 112.85 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.85 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00023 | 142.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.99 | 0
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00052 | 125.69 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 125.68 | 0.01
Thermal | 04NR | S2 | 20G0 | G04_G056 | FROM -> TO | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | 1076 | 0.07961 | 105.27 | 92479: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Internal | 105.15 | 0.12
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.48 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 140.44 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.2 | P13:13-115:ALTW:AUTO-SINGLE:PRCRK3G:PRARCK7:1 | External | 121.18 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 105.41 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 105.36 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.33 | P11:HV:EES::PIRKEY 1:1 | External | 101.3 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00059 | 100.64 | Base Case | External | 100.63 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.29 | P23:345:ALTW:MITCHLCO:1140 | External | 175.29 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.98 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 100.97 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 110.17 | 631166 NUTHTCH5 161 631171 WHISWIL5 161 1: 631166 NUTHTCH5 161 631171 WHISWIL5 161 1 | External | 110.14 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 156.85 | 613330 RICE 5 161 693755 JADE AVE 161 1: 613330 RICE 5 161 693755 JADE AVE 161 1 | External | 156.83 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.18 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 138.11 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 1 | 150 | 150 | 5e-05 | 102.22 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 102.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 5e-05 | 111.96 | P23:345-161:XEL:ADAMS_I:681_S | External | 111.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 115.98 | 104731: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 115.97 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.41 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 138.34 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.01 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 120.98 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 104.35 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 104.26 | 0.09
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 5e-05 | 112.8 | P12:115:XEL:JIM-HLC | External | 112.8 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636618 SB 56 #2 8 69.0 2 | 125 | 125 | 7e-05 | 114.89 | Base Case | External | 114.89 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00047 | 121.01 | P23:345:MEC:ATCHISON CO 903 | External | 120.98 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 179.8 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 179.76 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 111.74 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 111.69 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00059 | 102.73 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 102.72 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 128.35 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 128.32 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0012 | 143.13 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 143.08 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.73 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 102.73 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00016 | 102.37 | P12:161:ITCM:LORE5-SALEM N5:IA-NE | External | 102.37 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 120.93 | P23:345:ALTW:MITCHLCO:1150 | External | 120.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 184.16 | P23:345-161:XEL:ADAMS_I:681_S | External | 184.16 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 4e-05 | 104.15 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 104.15 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 115.54 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 115.5 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 104.23 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.18 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 150.17 | Base Case | External | 150.15 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 179.2 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 179.17 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.25 | P23:345:GRE:PVS 19JB3 | External | 175.25 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.08 | P11:34:ALTW:AUTO-SINGLE:H007_WF9:1 | External | 104.07 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 132.64 | P11:HV:EES::PIRKEY 1:1 | External | 132.58 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.36 | P23:345:ALTW:MITCHLCO:1130 | External | 175.37 | -0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.35 | P11:6:XEL:AUTO-SINGLE:HOLCOMBG:1 | External | 102.34 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 118.64 | Base Case | External | 118.62 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0105 | 113.99 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 113.96 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 1 | 112 | 112 | 2e-05 | 114.76 | Base Case | External | 114.76 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.15 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 104.15 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 | 315.9 | 315.9 | 0.00026 | 191.85 | Base Case | External | 191.85 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.54 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 121.52 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.09 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 104.09 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 131.03 | 92347: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 131 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 128.03 | 345441 1PENOGEN1 13.8 3WXFMR PENO GSU12 1: 345441 1PENOGEN1 13.8 998849 PENO GSU12 13.8 1 345442 1PENOGEN2 13.8 998849 PENO GSU12 13.8 1 345440 5PENOCREK 161 998849 PENO GSU12 13.8 1 345441 1PENOGEN1 13.8 998852 PENO GSU12 13.8 1 345442 1PENOGEN2 13.8 998852 PENO GSU12 13.8 1 345440 5PENOCREK 161 998852 PENO GSU12 13.8 1 345441 1PENOGEN1 13.8 998856 PENO GSU12 13.8 1 345442 1PENOGEN2 13.8 998856 PENO GSU12 13.8 1 345440 5PENOCREK 161 998856 PENO GSU12 13.8 1 | External | 127.99 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 141.82 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 2: 602030 WHT 14 5 161 997625 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997625 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997625 WHT 14 5 13.8 2 602030 WHT 14 5 161 997632 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997632 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997632 WHT 14 5 13.8 2 | External | 141.81 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 142.11 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 142.1 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 103.03 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 102.95 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 127.3 | 92349: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 127.27 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 117.38 | P11:6:XEL:AUTO-SINGLE:HOLCOMBG:1 | External | 117.38 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.42 | 81747: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 139.4 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00016 | 102.4 | P12:345:AMMO::AUDRAIN:SPS:1 | External | 102.4 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 162.6 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 162.57 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 112.59 | P11:24:AEPW:PIRKEY 1 | External | 112.56 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 182.87 | P12:161:DPC:RCE-HAR5 | External | 182.87 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 120.73 | P11:HV:EES::TURKCOAL:1 | External | 120.71 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.32 | 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1: 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1 | External | 102.32 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00034 | 146.13 | P23:345-161:XEL:ADAMS_I:681_S | External | 146.12 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 130.83 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 130.79 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.23 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 110.22 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 8e-05 | 117.3 | P22:345:XEL:ADAMS 3 N1:MN | External | 117.29 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630176 ROCKCK 8 69.0 631062 ROCKCKW5 161 1 | 112 | 112 | 0.00016 | 102.91 | P13:161-69:ITCM:ROCK CK5 T2:IA-EC | External | 102.9 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 5e-05 | 112.8 | P12:115:XEL:JIM-HLC & 5E18 | External | 112.8 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | 105877: 659105 LELAND_O-BE3 345 659111 LELAND_2-BEG 20.0 1 | External | 102.41 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.37 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 121.34 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 123.32 | P23:345-161:XEL:ADAMS_I:681_S | External | 123.31 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 73.1 | 73.1 | 0.20788 | 100.62 | 80545: 530686 RICE 6 230 530688 BUFLOCRK6 230 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00048 | 105.65 | P23:345:ALTW:MITCHLCO:1130 | External | 105.62 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 125.39 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 125.38 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00884 | 117.08 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 117.05 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | 213 | 213 | 0.00048 | 353.08 | Base Case | External | 353.08 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00055 | 102.31 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 102.29 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 325 | 325 | 0.0001 | 2943.33 | P12:161:ITCM:E CALMS5-DEWITT5:IA-EC | External | 2943.33 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.25 | 92348: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 116.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.09 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 104.09 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 112.88 | 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1: 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1 | External | 112.87 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 112.59 | P11:HV:EES::PIRKEY 1:1 | External | 112.56 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.01 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 104 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.15 | 631171 WHISWIL5 161 631225 WHISWILLW E5 161 1: 631171 WHISWIL5 161 631225 WHISWILLW E5 161 1 | External | 107.12 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 105.83 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 105.75 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.51 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 132.51 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631063 ROCK CK5 161 631065 BVR CHN L1 5 161 1 | 200 | 237 | 0.00025 | 110.2 | P13:69-161:ALTW:AUTO-SINGLE:ROCKCKE8:ROCKCK5:1 | External | 110.19 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00017 | 100.63 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 100.61 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00066 | 156.66 | P12:161:DPC:RCE-HAR5 | External | 156.65 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 127.05 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 127.03 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 178.96 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 178.92 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.96 | P12:161:XEL:JEF-WHT | External | 140.95 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.76 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 154.74 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.33 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 100.31 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 113.11 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 113.07 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 105.79 | Base Case | External | 105.78 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.4 | P12:161:XEL:JEF-WHT | External | 111.37 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 103.6 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 103.53 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.4 | P11:24:AEPW:PIRKEY 1 | External | 139.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.05 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 104.04 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00061 | 101.06 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1: 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | External | 101.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.8 | P11:13:XEL:AUTO-SINGLE:FEN84G:4 | External | 115.77 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.98 | 605492 WBYRON 8 69 613070 BYRON 5 161 1: 605492 WBYRON 8 69.0 613070 BYRON 5 161 1 | External | 103.98 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01037 | 112.99 | P23:345-161:XEL:ADAMS_I:680_S | External | 112.95 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 4e-05 | 143.7 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 143.7 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.05 | P11:HV:EES::TURKCOAL:1 | External | 104.04 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 142.11 | P13:13-13-161:XEL:AUTO-SINGLE:WHT51G:WHT52G:WHT145:1 | External | 142.1 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0105 | 112.55 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 112.51 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00109 | 112.82 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 112.79 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 8e-05 | 103.44 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 103.44 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.24 | P11:115:XEL:AUTO-SINGLE:JIMFLS7:2 | External | 132.24 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00012 | 104.7 | 105823: 652515 HURON 7 115 660009 BTAP WP7 115 1 660003 HURONWP7 115 660009 BTAP WP7 115 1 660009 BTAP WP7 115 660040 DAKOTACCESS7 115 1 652515 HURON 7 115 652528 WOONSKT7 115 1 652515 HURON 7 115 655481 REDFELD-ER7 115 1 652515 HURON 7 115 660003 HURONWP7 115 1 652284 HURON 8 69.0 652515 HURON 7 115 1 652515 HURON 7 115 997158 HU KV1A 115 1 652515 HURON 7 115 997157 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 1 652507 FTTHOMP4 230 652514 HURON 4 230 2 652514 HURON 4 230 652530 WATERTN4 230 2 652514 HURON 4 230 652614 CARPENTER 4 230 1 652514 HURON 4 230 659205 BROADLND-BE4 230 1 652514 HURON 4 230 997158 HU KV1A 115 1 652514 HURON 4 230 997157 HU KV1B 115 2 652528 WOONSKT7 115 659123 STORLA__-BE7 115 1 652528 WOONSKT7 115 655355 WOONSKT-ER8 69.0 2 652284 HURON 8 69.0 655063 SW341-ER8 69.0 1 652284 HURON 8 69.0 655066 SW352-ER8 69.0 1 652284 HURON 8 69.0 655067 SW353-ER8 69.0 1 652282 HURON429 13.3 997157 HU KV1B 115 2 652281 HURON419 13.3 997158 HU KV1A 115 1 652515 HURON 7 115 997165 HU KV1A 115 1 652515 HURON 7 115 997164 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 2 652514 HURON 4 230 997165 HU KV1A 115 1 652514 HURON 4 230 997164 HU KV1B 115 2 652282 HURON429 13.3 997164 HU KV1B 115 2 652281 HURON419 13.3 997165 HU KV1A 115 1 652515 HURON 7 115 997156 HU KV1A 115 1 652515 HURON 7 115 997155 HU KV1B 115 2 652514 HURON 4 230 997156 HU KV1A 115 1 652514 HURON 4 230 997155 HU KV1B 115 2 652282 HURON429 13.3 997155 HU KV1B 115 2 652281 HURON419 13.3 997156 HU KV1A 115 1 | External | 104.69 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631032 SQUARED7 115 1 | 164 | 164 | 0.00064 | 175.08 | P22:345:XEL:ADAMS 3 N1:MN | External | 175.07 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 179.03 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 179 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 2 | 150 | 150 | 5e-05 | 102.22 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 102.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 178.98 | P11:24:AEPW:PIRKEY 1 | External | 178.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.96 | P13:230:EES:ND:6UCARBD%:1(1) | External | 103.95 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 325 | 325 | 0.00031 | 2939.53 | Base Case | External | 2939.53 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.23 | P11:HV:EES::PIRKEY 1:1 | External | 154.22 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.63 | P11:HV:EES::TURKCOAL:1 | External | 100.62 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 139.7 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 139.63 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.73 | P11:345:AMMO::RACCOONCREEK:1 | External | 115.7 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 125.04 | P23:345:ALTW:MITCHLCO:1160 | External | 125.02 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 133.91 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 133.92 | -0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00041 | 167.22 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 167.18 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 128.03 | 345443 1PENOGEN3 13.8 3WXFMR PENO GSU34 1: 345443 1PENOGEN3 13.8 998848 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998848 PENO GSU34 13.8 1 345440 5PENOCREK 161 998848 PENO GSU34 13.8 1 345443 1PENOGEN3 13.8 998851 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998851 PENO GSU34 13.8 1 345440 5PENOCREK 161 998851 PENO GSU34 13.8 1 345443 1PENOGEN3 13.8 998855 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998855 PENO GSU34 13.8 1 345440 5PENOCREK 161 998855 PENO GSU34 13.8 1 | External | 127.99 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997528 CHL115-69-1 69.0 1 | 140 | 140 | 6e-05 | 138.06 | Base Case | External | 138.06 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01276 | 132.17 | P23:345-161:XEL:ADAMS_I:680_S | External | 132.11 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.18 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 138.08 | 0.1
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 116.28 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 116.24 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0105 | 112.59 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 112.56 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.75 | 92358: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 102.75 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0001 | 102.56 | P23:345:ALTW:MITCHLCO:1130 | External | 102.55 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00978 | 118.83 | P22:345:XEL:ADAMS 3 N1:MN | External | 118.81 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.25 | 104742: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 | External | 116.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 5e-05 | 111.96 | P23:345-161:XEL:ADAMS_I:680_S | External | 111.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00021 | 142.24 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 142.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00072 | 179.77 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 179.73 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.49 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 101.47 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 125.01 | P23:345:ALTW:MITCHLCO:1150 | External | 124.98 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.51 | 92415: 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 102.46 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.59 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 107.6 | -0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00145 | 135.62 | Base Case | External | 135.58 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 118.64 | Base Case | External | 118.64 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 129.86 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 129.83 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 117.38 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 117.37 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 126.49 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 126.47 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.77 | P13:13-115:ALTW:AUTO-SINGLE:PRCRK3G:PRARCK7:1 | External | 101.74 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 109.86 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 109.82 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 103.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.81 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 100.79 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00056 | 102.73 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1: 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | External | 102.72 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 1 | 150 | 150 | 5e-05 | 102.22 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 102.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00011 | 106.21 | P22:345:XEL:ADAMS 3 N1:MN | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 9e-05 | 103.3 | P23:345:ALTW:MITCHLCO:1130 | External | 103.3 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00015 | 101.2 | Base Case | External | 101.2 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 176.57 | Base Case | External | 176.53 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 100 | P11:001:MKEC:SHOOTINGSTARWIND:105:539100(1) | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.7 | 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1: 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1 | External | 115.67 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00048 | 105.86 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 105.83 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.37 | P12:HV:EES::TURK 4%:1(1) | External | 102.36 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.09 | P11:34:ALTW:AUTO-SINGLE:H008_WF9:1 | External | 104.09 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.35 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 114.31 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.81 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 102.81 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.1 | P13:161-13:MEC:AUTO-SINGLE:ELFARM5:ELFARMG2:1 | External | 107.07 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.25 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 102.24 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.05 | P11:24:AEPW:PIRKEY 1 | External | 104.05 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0001 | 105.68 | P23:345:ALTW:MITCHLCO:1140 | External | 105.67 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.84 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 110.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | 112 | 133.9 | 1e-05 | 125.09 | Base Case | External | 125.09 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630249 WINDSOR8 69.0 613420 WINDSOR5 161 1 | 75 | 94 | 4e-05 | 118.22 | Base Case | External | 118.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 1 | 112 | 112 | 2e-05 | 124.35 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 124.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 0.00012 | 115.99 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 115.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.05 | 92452: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 133.15 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 133.09 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 117.37 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 117.34 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 102.63 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | Internal | 101.26 | 1.37
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630340 ROSEHLW8 69.0 631034 ROSEHLW5 161 1 | 75 | 75 | 8e-05 | 110.52 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 110.51 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.12 | P11:69:DPC:AUTO-SINGLE:FLAMBEAU:1 | External | 132.12 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 115.62 | P23:345:ALTW:MITCHLCO:1150 | External | 115.58 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0003 | 160.18 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 160.17 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 131.82 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 131.76 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 605662 LUFKIN 69.0 681545 LUFKIN 161 6 | 112 | 128.8 | 4e-05 | 111.56 | Base Case | External | 111.56 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00042 | 121.84 | P23:345:ALTW:MITCHLCO:1140 | External | 121.82 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 112.93 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 112.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00075 | 100.06 | P12:161:DPC:RCE-HAR5 | External | 100.06 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0003 | 161.47 | P23:345:ALTW:MITCHLCO:1160 | External | 161.45 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 132.51 | P11:HV:EES::TURKCOAL:1 | External | 132.45 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.44 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 102.44 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | P11:345:UMZB:# 32 #: AVS IN ND. ANTELOPE VALLEY 2 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 153.97 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 153.95 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00036 | 118.84 | Base Case | External | 118.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681528 HARMONY5 161 680026 HARMNY 69.0 1 | 112 | 136.6 | 0.00011 | 110.99 | P12:161:DPC:RCE-HAR5 | External | 110.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.78 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 110.78 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.72 | Base Case | External | 138.66 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.69 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 102.68 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.23 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 121.2 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00114 | 117.32 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 117.28 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 114.03 | P11:24:AEPW:PIRKEY 1 | External | 114 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | P13:345-18:AEPW:OEC 7_#1 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15338 | 104.19 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 102.6 | 1.59
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15089 | 100.91 | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.54 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 108.51 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.97 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 101.94 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 110.86 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 110.82 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 120.8 | P11:HV:EES::PIRKEY 1:1 | External | 120.77 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00217 | 103.95 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.92 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.36 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 139.35 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.72 | 92472: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 116.71 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00021 | 109.45 | P23:345-161:XEL:ADAMS_I:680_S | External | 109.44 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.92 | 629110 GR JCT 9 34.5 631074 GR JCT 5 161 1: 629110 GR JCT 9 34.5 631074 GR JCT 5 161 1 | External | 115.89 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00115 | 112.82 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 112.79 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.96 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 154.93 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 114.35 | P23:345-161:XEL:ADAMS_I:680_S | External | 114.32 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 1e-05 | 108.66 | P22:345:XEL:ADAMS 3 N1:MN | External | 108.65 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.04 | P12:HV:EES::PIRKEY 4:1 | External | 104.04 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631099 WYOMING5 161 630022 WYOMING8 69.0 1 | 63 | 63 | 1e-05 | 114.86 | Base Case | External | 114.86 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.74 | P11:HV:EES::TURKCOAL:1 | External | 116.71 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 115.75 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 115.71 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630902 VINTON 8 69.0 631087 VINTON 5 161 1 | 100 | 100 | 0.0002 | 106.43 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 106.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636618 SB 56 #2 8 69.0 2 | 125 | 125 | 4e-05 | 112.1 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 112.1 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.004 | 102.37 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 102.29 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 111.96 | P12:161:XEL:JEF-WHT | External | 111.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.84 | P11:24:AEPW:PIRKEY 1 | External | 116.82 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.54 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 101.54 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00268 | 102.99 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 102.93 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00021 | 105.79 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 105.79 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00109 | 103.52 | P22:345:XEL:ADAMS 3 N1:MN | External | 103.5 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 103.23 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 103.2 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07019 | 105.08 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 103.8 | 1.28
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.06 | P11:HV:EES::PIRKEY 1:1 | External | 107.03 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 116.47 | Base Case | External | 116.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.21 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 116.18 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.63 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 139.64 | -0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15338 | 101.67 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 100.32 | 1.35
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.51 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 132.51 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.26 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 175.26 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00061 | 178.88 | P23:345:MEC:ATCHISON CO 903 | External | 178.83 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0001 | 102.55 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 102.54 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.23 | P11:115:XEL:AUTO-SINGLE:JIMFLS7:1 | External | 132.23 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | P12:345:AMMO::AUDRAIN:SPS:1 | External | 103.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 105.9 | P13:41-115:OTP:AUTO-SINGLE:HETLAND9:HETLAND7:1 | External | 105.9 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00015 | 111.62 | Base Case | External | 111.62 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 117.04 | P23:345:ALTW:MITCHLCO:1130 | External | 117 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01068 | 115.09 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 115.06 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 120.76 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 120.73 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 | 112 | 128.8 | 4e-05 | 102.08 | Base Case | External | 102.08 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 8e-05 | 101.93 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 101.91 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00028 | 144.01 | Base Case | External | 144 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.22 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 102.21 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.25 | 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1: 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1 | External | 111.22 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.3 | 631225 WHISWILLW E5 161 630733 G947_WF9 34.5 1: 631225 WHISWILLW E5 161 630733 G947_WF9 34.5 1 | External | 107.27 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.35 | P13:6-115:XEL:AUTO-SINGLE:HOLCOMBG:HOLCOMB7:1 | External | 102.34 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 125.26 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 125.25 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.15 | P12:161:ALTW:AUTO-SINGLE:WHISWIL5:WHISWILLWE5:1 | External | 107.12 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 117.09 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 117.05 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.3 | P11:0:ALTW:AUTO-SINGLE:G573G2:1 | External | 107.27 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 131.72 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 131.67 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 117.37 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 117.34 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0098 | 117.9 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 117.87 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.4 | P11:13:XEL:AUTO-SINGLE:FEN84G:4 | External | 102.4 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 117.38 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 117.38 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 113.21 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 113.17 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.45 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 108.41 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 124.77 | P23:345:ALTW:MITCHLCO:1130 | External | 124.74 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 115.54 | 92347: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 115.5 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.67 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 101.66 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 115.08 | P23:345:ALTW:MITCHLCO:1130 | External | 115.04 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 135.77 | Base Case | External | 135.77 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 141.98 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 141.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.3 | P13:34-161:ALTW:AUTO-SINGLE:G947_WF9:WHISWILLWE5:1 | External | 107.27 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 112.88 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 112.87 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 133.15 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 133.09 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00012 | 101.53 | 105823: 652515 HURON 7 115 660009 BTAP WP7 115 1 660003 HURONWP7 115 660009 BTAP WP7 115 1 660009 BTAP WP7 115 660040 DAKOTACCESS7 115 1 652515 HURON 7 115 652528 WOONSKT7 115 1 652515 HURON 7 115 655481 REDFELD-ER7 115 1 652515 HURON 7 115 660003 HURONWP7 115 1 652284 HURON 8 69.0 652515 HURON 7 115 1 652515 HURON 7 115 997158 HU KV1A 115 1 652515 HURON 7 115 997157 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 1 652507 FTTHOMP4 230 652514 HURON 4 230 2 652514 HURON 4 230 652530 WATERTN4 230 2 652514 HURON 4 230 652614 CARPENTER 4 230 1 652514 HURON 4 230 659205 BROADLND-BE4 230 1 652514 HURON 4 230 997158 HU KV1A 115 1 652514 HURON 4 230 997157 HU KV1B 115 2 652528 WOONSKT7 115 659123 STORLA__-BE7 115 1 652528 WOONSKT7 115 655355 WOONSKT-ER8 69.0 2 652284 HURON 8 69.0 655063 SW341-ER8 69.0 1 652284 HURON 8 69.0 655066 SW352-ER8 69.0 1 652284 HURON 8 69.0 655067 SW353-ER8 69.0 1 652282 HURON429 13.3 997157 HU KV1B 115 2 652281 HURON419 13.3 997158 HU KV1A 115 1 652515 HURON 7 115 997165 HU KV1A 115 1 652515 HURON 7 115 997164 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 2 652514 HURON 4 230 997165 HU KV1A 115 1 652514 HURON 4 230 997164 HU KV1B 115 2 652282 HURON429 13.3 997164 HU KV1B 115 2 652281 HURON419 13.3 997165 HU KV1A 115 1 652515 HURON 7 115 997156 HU KV1A 115 1 652515 HURON 7 115 997155 HU KV1B 115 2 652514 HURON 4 230 997156 HU KV1A 115 1 652514 HURON 4 230 997155 HU KV1B 115 2 652282 HURON429 13.3 997155 HU KV1B 115 2 652281 HURON419 13.3 997156 HU KV1A 115 1 | External | 101.53 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 167.16 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 167.13 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00953 | 114.37 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 114.35 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 110.11 | Base Case | External | 110.08 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 120.99 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 120.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 120.92 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 120.89 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 131.08 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 131.04 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.49 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 140.43 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00059 | 102.73 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 102.72 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00132 | 147.02 | P23:345:ALTW:MITCHLCO:1130 | External | 146.98 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 131.08 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 131.04 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636617 SB 56 #1 8 69.0 1 | 125 | 125 | 2e-05 | 122.27 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 122.27 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.12 | P11:13:DPC:AUTO-SINGLE:ELKMDGEN:1 | External | 140.1 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.83 | 92471: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 116.82 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00016 | 102.05 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 102.01 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.79 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 154.79 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00953 | 117.21 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 117.18 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.76 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 101.73 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 117.38 | P13:6-115:XEL:AUTO-SINGLE:HOLCOMBG:HOLCOMB7:1 | External | 117.38 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630340 ROSEHLW8 69.0 631034 ROSEHLW5 161 1 | 75 | 75 | 8e-05 | 110.62 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 110.62 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 112.94 | P13:161-34:ALTW:AUTO-SINGLE:WHISWIL5:G573_WFA9:1 | External | 112.9 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 113.94 | P13:138-24:AEPW:TURK 4 | External | 113.91 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 139.7 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 139.63 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0017 | 182.07 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 182.02 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.86 | 92358: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 110.86 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 0.00018 | 109.38 | P13:161:WAUW:# 3114 #: HV IN MT. HV TX KZ1A FAULT | External | 109.38 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0098 | 117.91 | P23:345:ALTW:MITCHLCO:1150 | External | 117.88 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.31 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 140.29 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 141.19 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 141.15 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.13 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 108.09 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.05 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 104.04 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00015 | 103.32 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 103.32 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01068 | 113.89 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 113.86 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00379 | 105.41 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 105.36 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 141.82 | P13:13-13-161:XEL:AUTO-SINGLE:WHT53G:WHT54G:WHT145:2 | External | 141.81 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 151.93 | Base Case | External | 151.91 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.78 | 92666: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 116.77 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 141.79 | P13:13-13-161:XEL:AUTO-SINGLE:WHT55G:WHT56G:WHT565:1 | External | 141.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681528 HARMONY5 161 680026 HARMNY 69.0 1 | 112 | 136.6 | 1e-05 | 125.69 | Base Case | External | 125.69 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.18 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 138.08 | 0.1
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636618 SB 56 #2 8 69.0 2 | 125 | 125 | 4e-05 | 112.01 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 112.01 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.98 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | External | 103.98 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0105 | 116.85 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 116.82 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.00042 | 102.57 | P23:345:ALTW:MITCHLCO:1140 | External | 102.56 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 130.94 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 130.87 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.97 | P23:345:MEC:ATCHISON CO 903 | External | 103.97 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 178.96 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 178.92 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00042 | 121.92 | P23:345:ALTW:MITCHLCO:1150 | External | 121.9 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.58 | P13:34-161:MEC:AUTO-SINGLE:WALLLK9:WALLLK5:2 | External | 114.54 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 149.59 | Base Case | External | 149.59 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.18 | 631173 G573_WFB9 34.5 631171 WHISWIL5 161 1: 631173 G573_WFB9 34.5 631171 WHISWIL5 161 1 | External | 107.15 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 113.93 | P13:138-24:AEPW:PIRKEY 4 | External | 113.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15089 | 100.91 | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.00016 | 123.07 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 123.07 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00066 | 140.11 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 140.1 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | 105882: 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 101.83 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 101.75 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00124 | 121.89 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 121.85 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 128.03 | P13:013-161:AMMO::PENOCREEK:2 | External | 127.99 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 117.36 | P23:345:ALTW:MITCHLCO:1160 | External | 117.32 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.34 | P13:161-69:ITCM:ROCKCKW5 T3:IA-EC | External | 102.34 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 156.85 | P13:161-34:ALTW-WPS:AUTO-SINGLE:RICE5:G551_TAP:1 | External | 156.83 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 178.98 | P11:HV:EES::PIRKEY 1:1 | External | 178.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.45 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 108.41 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 4e-05 | 109.15 | P12:161:DPC:RCE-HAR5 | External | 109.15 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00047 | 101.56 | P23:345:MEC:ATCHISON CO 903 | External | 101.53 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630281 LORE E 8 69.0 631056 LORE 5 161 1 | 61 | 75 | 2e-05 | 104.13 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 104.13 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 111.84 | P11:115:XEL:AUTO-SINGLE:FIBROMN7:1 | External | 111.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 112.47 | P13:138-24:AEPW:PIRKEY 4 | External | 112.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.79 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 100.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.56 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 101.53 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00824 | 116.66 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 116.63 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.14 | P11:13:XEL:AUTO-SINGLE:WHT51G:1 | External | 140.12 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00021 | 109.45 | P23:345-161:XEL:ADAMS_I:681_S | External | 109.44 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.2 | 631017 PRAR CK7 115 630787 PR CRK3G 13.2 1: 631017 PRAR CK7 115 630787 PR CRK3G 13.2 1 | External | 121.18 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.38 | P11:13:XEL:AUTO-SINGLE:WHT52G:2 | External | 102.38 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 126.65 | P22:345:XEL:ADAMS 3 N1:MN | External | 126.62 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615396 GRE-PRKWDB17 115 997566 PAR115-69-1 69.0 1 | 140 | 140 | 0.00015 | 165.48 | Base Case | External | 165.48 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 162.6 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 162.57 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.98 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 102.97 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00011 | 103.16 | P22:345:XEL:ADAMS 3 N1:MN | External | 103.15 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636617 SB 56 #1 8 69.0 1 | 125 | 125 | 2e-05 | 122.31 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 122.3 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 5e-05 | 127.35 | P12:115:XEL:JIM-HLC & 5E18 | External | 127.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.7 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 113.66 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 601002 ADAMS 3 345 997686 ADAMS 3 161 9 | 300 | 334.6 | 0.00118 | 107.84 | P12:161:DPC:RCE-HAR5 | External | 107.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631032 SQUARED7 115 1 | 164 | 164 | 0.00068 | 175.18 | P11:13:ALTW:AUTO-SINGLE:PRCRK3G:3 | External | 175.18 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.38 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 102.37 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630176 ROCKCK 8 69.0 631062 ROCKCKW5 161 1 | 112 | 112 | 2e-05 | 105.03 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 105.03 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.12 | P11:13:DPC:AUTO-SINGLE:ELKMDGEN:2 | External | 140.1 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15539 | 101.99 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal | 101.02 | 0.97
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | 106126: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 0.00012 | 115.99 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 115.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.65 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 114.61 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 9e-05 | 103.19 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 103.19 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 115.61 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 115.57 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00913 | 113.6 | P23:345:MEC:ATCHISON CO 903 | External | 113.57 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00884 | 114.25 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 114.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | 92361: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 100.18 | Base Case | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.6 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 139.59 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 105.57 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | Internal | 104.28 | 1.29
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 7e-05 | 132.17 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External | 132.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00118 | 111.35 | P12:161:DPC:RCE-HAR5 | External | 111.34 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0098 | 117.91 | P23:345:ALTW:MITCHLCO:1160 | External | 117.88 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 1 | 112 | 112 | 2e-05 | 124.35 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 124.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.93 | P13:161-34:MEC:AUTO-SINGLE:WALLLK5:WALLLK9:1 | External | 114.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00109 | 112.18 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 112.15 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.39 | P12:230:MP-XEL:BRC-RCR | External | 102.39 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00824 | 119.61 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 119.58 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 135.1 | Base Case | External | 135.06 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00153 | 140.66 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 140.62 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997484 WEB AB 161 1 | 560 | 560 | 0.00209 | 122.13 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 122.11 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | 197 | 197 | 0.00071 | 101.44 | P12:115:ITCM:PRAR CK7-E CALMS7:IA-EC | External | 101.42 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.16 | P13:161-34:ALTW:AUTO-SINGLE:WHISWIL5:G573_WFA9:1 | External | 107.12 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.97 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 103.96 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.43 | P11:0:ALTW:AUTO-SINGLE:G947_GEN:1 | External | 107.4 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 115.54 | 104728: 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | External | 115.5 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 4e-05 | 143.7 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 143.7 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 130.94 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 130.87 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.11 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 139.09 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | P13:138-14.4:AEPW:N.E.S.-4 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 8e-05 | 109.4 | P22:345:XEL:ADAMS 3 N1:MN | External | 109.4 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.18 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 138.11 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.39 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 121.36 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 130.64 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 130.58 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 2e-05 | 104.2 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 104.2 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631032 SQUARED7 115 1 | 164 | 164 | 0.00031 | 157.68 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 157.67 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.43 | P13:13-13-161:XEL:AUTO-SINGLE:WHT55G:WHT56G:WHT565:1 | External | 102.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615433 GRE-BURNVIL7 115 997560 115/69 69.0 2 | 82.2 | 82.2 | 1e-05 | 105.17 | Base Case | External | 105.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 605366 PINE LK8 69.0 603151 PINE LK7 115 2 | 112 | 128.8 | 1e-05 | 104.76 | Base Case | External | 104.76 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01059 | 134.75 | P23:345:MEC:ATCHISON CO 903 | External | 134.69 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 139.36 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 139.36 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.62 | P11:34:ALTW:AUTO-SINGLE:H007_WF9:1 | External | 101.61 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.07 | P11:0:ALTW:AUTO-SINGLE:G573G2:1 | External | 113.04 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.47 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 107.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.35 | P12:115:XEL:JIM-HLC & 5E18 | External | 102.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.58 | 84365: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 116.57 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.27 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 101.25 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | 92363: 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00978 | 118.5 | P22:345:XEL:ADAMS 3 N1:MN | External | 118.46 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.25 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 111.22 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.47 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 101.45 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 108.27 | Base Case | External | 108.27 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.34 | 92469: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 102.33 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 155.41 | P11:13:XEL:AUTO-SINGLE:FEN84G:4 | External | 155.4 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 9e-05 | 173.03 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 173.03 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0105 | 112.59 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 112.56 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.51 | P13:34-161:ALTW:AUTO-SINGLE:GRJCT9:GRJCT5:1 | External | 111.48 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 155.06 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 155.05 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 100.12 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.96 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 154.93 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 107.92 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 107.91 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 112.94 | P12:161:ALTW:AUTO-SINGLE:WHISWIL5:WHISWILLWE5:1 | External | 112.9 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 2 | 150 | 150 | 5e-05 | 102.22 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 102.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00044 | 121.06 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 121.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 103.75 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 103.71 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 115.75 | 631166 NUTHTCH5 161 631171 WHISWIL5 161 1: 631166 NUTHTCH5 161 631171 WHISWIL5 161 1 | External | 115.71 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07079 | 109.14 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal | 107.8 | 1.34
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07034 | 106.61 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal | 105.31 | 1.3
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | 92366: 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00042 | 105.6 | P23:345:ALTW:MITCHLCO:1160 | External | 105.59 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630902 VINTON 8 69.0 631087 VINTON 5 161 1 | 100 | 100 | 0.00016 | 104.78 | P22:345:XEL:ADAMS 3 N1:MN | External | 104.78 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.38 | 92469: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 110.37 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 104.4 | Base Case | External | 104.37 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 122.14 | P23:345-161:XEL:ADAMS_I:680_S | External | 122.12 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00119 | 120.75 | P12:161:DPC:RCE-HAR5 | External | 120.74 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 179.36 | Base Case | External | 179.36 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 109.7 | 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1: 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1 | External | 109.7 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00042 | 122.43 | P22:345:XEL:ADAMS 3 N1:MN | External | 122.41 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 6e-05 | 142.32 | Base Case | External | 142.32 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631063 ROCK CK5 161 631065 BVR CHN L1 5 161 1 | 200 | 237 | 0.00025 | 110.2 | 630174 ROCKCKE8 69 631063 ROCK CK5 161 1: 630174 ROCKCKE8 69.0 631063 ROCK CK5 161 1 | External | 110.19 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.13 | 104736: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 116.11 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630340 ROSEHLW8 69.0 631034 ROSEHLW5 161 1 | 75 | 75 | 8e-05 | 110.62 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 110.62 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.31 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 140.29 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.00042 | 102.64 | P23:345:ALTW:MITCHLCO:1150 | External | 102.62 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 605366 PINE LK8 69.0 603151 PINE LK7 115 1 | 112 | 128.8 | 1e-05 | 105.82 | Base Case | External | 105.82 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.39 | P11:138:OKGE:BKRBKR_GSU29 | External | 106.39 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00061 | 101.06 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External | 101.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 110.17 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 110.14 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00884 | 114.25 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 114.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 5e-05 | 129.67 | Base Case | External | 129.67 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0105 | 114.03 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 114 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00044 | 101.62 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 101.59 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00016 | 105.26 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 105.2 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.74 | 104731: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 102.74 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 130.64 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 130.58 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | 105881: 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 109.43 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 109.42 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | 106624: 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.15 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 104.15 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 117.37 | P23:345:ALTW:MITCHLCO:1150 | External | 117.33 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.86 | 104742: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 | External | 110.86 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 6e-05 | 135.1 | Base Case | External | 135.1 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00099 | 140.98 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 140.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.34 | P12:161:ITCM:E CALMS5-DEWITT5:IA-EC | External | 102.34 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.41 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 140.37 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0016 | 153.78 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 153.73 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.00042 | 103.06 | P22:345:XEL:ADAMS 3 N1:MN | External | 103.05 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.77 | 92342: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 114.73 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 103.47 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 103.42 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 7e-05 | 115.64 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 115.64 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 106.21 | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00848 | 144.83 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 144.76 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 141.19 | 631166 NUTHTCH5 161 631171 WHISWIL5 161 1: 631166 NUTHTCH5 161 631171 WHISWIL5 161 1 | External | 141.15 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.27 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 175.27 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | P13:345-18:AEPW:OEC 7_#4 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00195 | 148.39 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 148.34 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.00046 | 100.1 | Base Case | External | 100.08 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 138.37 | Base Case | External | 138.34 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.25 | 104729: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 116.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.06 | 81747: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 104.05 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 179.8 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 179.76 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 112.93 | 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1: 603282 LS POWER 7 115 600018 LSSTEAMG 13.2 1 | External | 112.91 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.84 | P11:HV:EES::PIRKEY 1:1 | External | 116.82 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 125.39 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 125.38 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.48 | 92382: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.43 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.69 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 115.66 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.96 | P11:13.8:AMMO:1GOSCK 2:2 | External | 103.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.7 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 115.67 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00132 | 147.6 | P23:345:ALTW:MITCHLCO:1150 | External | 147.56 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 132.41 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 132.38 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.82 | P12:161:XEL:JEF-WHT | External | 115.8 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 109.48 | Base Case | External | 109.45 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00071 | 112.07 | P12:115:ITCM:PRAR CK7-E CALMS7:IA-EC | External | 112.06 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.79 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 154.78 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 112.94 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 112.91 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00018 | 102.46 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 102.46 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0105 | 116.8 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 116.78 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.13 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 104.13 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 100.02 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 117.09 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 117.05 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.67 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 101.66 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.74 | P13:138-24:AEPW:PIRKEY 4 | External | 116.71 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 101.29 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 101.26 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.01203 | 100.44 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 100.42 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.00016 | 123.07 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 123.07 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.0003 | 108.06 | P23:345-161:XEL:ADAMS_I:681_S | External | 108.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 7e-05 | 107.7 | P12:115:OTP-GRE::BIGSTON7:TORONTO7 | External | 107.7 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.37 | P13:138-24:AEPW:PIRKEY 4 | External | 102.37 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.36 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 108.33 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 128.35 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 128.32 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 116.24 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 116.19 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630281 LORE E 8 69.0 631056 LORE 5 161 1 | 61 | 75 | 2e-05 | 104.13 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 104.13 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 116.24 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 116.19 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00124 | 121.34 | P23:345:ALTW:MITCHLCO:1130 | External | 121.3 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | P13:13-13-161:XEL:AUTO-SINGLE:WHT53G:WHT54G:WHT145:2 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0004 | 123.74 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 123.72 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.23 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 110.22 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.25 | P11:13:XEL:AUTO-SINGLE:WHT54G:4 | External | 140.23 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.38 | P11:13:XEL:AUTO-SINGLE:FEN84G:4 | External | 111.34 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0105 | 116.85 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 116.82 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 105.7 | 92669: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal | 104.45 | 1.25
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00268 | 102.99 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 102.93 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 107.71 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.68 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 122.55 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 122.52 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 178.91 | 81747: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 178.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.7 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 113.66 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.86 | P11:34:ALTW:AUTO-SINGLE:H008_WF9:1 | External | 100.84 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01294 | 132.49 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 132.43 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.92 | P13:069:MEC:ELECTRIFARM BC | External | 115.89 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.19 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 121.17 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00058 | 166.85 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 166.82 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0004 | 104.53 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 104.5 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00065 | 139.36 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 139.35 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00021 | 154.96 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 154.94 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 102.38 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 102.3 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06885 | 103.73 | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 102.44 | 1.29
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 155.14 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 155.12 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 603153 HYDROLN7 115 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.51 | Base Case | External | 132.5 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.65 | 631052 LANSING L1 5 161 631053 LANSING L2 5 161 1: 631052 LANSING L1 5 161 631053 LANSING L2 5 161 1 | External | 104.65 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | 1061261: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.0002 | 109.66 | P22:345:XEL:ADAMS 3 N1:MN | External | 109.65 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 106.21 | 1061260: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00884 | 117.08 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 117.05 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 104.67 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 104.6 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 101.53 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 101.52 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 139.04 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 138.97 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.26 | P11:HV:EES::TURKCOAL:1 | External | 101.23 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 109.31 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 109.26 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 102.44 | Base Case | External | 102.38 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00913 | 114.85 | P23:345:MEC:ATCHISON CO 903 | External | 114.82 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 126.4 | P12:161:XEL:JEF-WHT | External | 126.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 148.96 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 148.93 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 105.25 | P11:HV:EES::TURKCOAL:1 | External | 105.2 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 102.79 | P23:345-161:XEL:ADAMS_I:681_S | External | 102.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 100.12 | 92669: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.0001 | 115.62 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 115.62 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.97 | 672581 GLASLYN 6 138 672596 BRADA 6 138 1: 672581 GLASLYN 6 138 672596 BRADA 6 138 1 | External | 103.96 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00055 | 121.7 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 121.68 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.54 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 121.52 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 4e-05 | 108.65 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 108.65 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 122.14 | P23:345-161:XEL:ADAMS_I:681_S | External | 122.12 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.02 | 605492 WBYRON 8 69 613070 BYRON 5 161 1: 605492 WBYRON 8 69.0 613070 BYRON 5 161 1 | External | 154 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.96 | P12:115:XEL:IVH-CHE | External | 103.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 178.91 | P12:HV:EES::PIRKEY 4:1 | External | 178.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.01 | P23:345:ALTW:MITCHLCO:1160 | External | 104.01 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 101.94 | P11:HV:EES::JTEC GEN#2 1:2 | External | 101.86 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 7e-05 | 132.17 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1: 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | External | 132.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 102.99 | 620209 HETLAND7 115 620109 HETLAND9 41.6 1: 620209 HETLAND7 115 620109 HETLAND9 41.6 1 | External | 102.98 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.19 | P11:HV:EES::TURKCOAL:1 | External | 154.18 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 114.43 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 114.4 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636617 SB 56 #1 8 69.0 1 | 125 | 125 | 2e-05 | 122.31 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 122.3 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 103.49 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 103.41 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 135.01 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 134.94 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.36 | P12:765:AEP:AEP ROCKP-AEP JEFF 765 | External | 102.36 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00011 | 546.76 | Base Case | External | 546.76 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 102.99 | P13:41-115:OTP:AUTO-SINGLE:HETLAND9:HETLAND7:1 | External | 102.98 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 7e-05 | 155.83 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 155.81 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00042 | 104.84 | P23:345:ALTW:MITCHLCO:1130 | External | 104.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 4e-05 | 108.81 | Base Case | External | 108.81 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.46 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 107.43 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.73 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 102.68 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.95 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 101.92 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.2 | 81747: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 102.15 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.96 | 336175 6UCARBD% 230 336177 1UCARBGT2! 13.8 1: 336175 6UCARBD% 230 336177 1UCARBGT2! 13.8 1 | External | 103.95 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00018 | 101.28 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 101.26 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631032 SQUARED7 115 1 | 164 | 164 | 0.0006 | 168.77 | P12:115:ITCM:PRAR CK7-E CALMS7:IA-EC | External | 168.77 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 106.21 | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.84 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 110.83 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.29 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 140.25 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630176 ROCKCK 8 69.0 631062 ROCKCKW5 161 1 | 112 | 112 | 2e-05 | 105.03 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 105.03 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 2 | 112 | 112 | 2e-05 | 124.36 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 124.35 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2 | External | 102.41 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.54 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 108.51 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 103.27 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.27 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 113.21 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 113.17 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 103.18 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 103.11 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06914 | 106.16 | P12:115:MKEC:MEDICINELODGE-SHOOTINGSTARTAP:: | Internal | 104.87 | 1.29
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 130.38 | 345443 1PENOGEN3 13.8 3WXFMR PENO GSU34 1: 345443 1PENOGEN3 13.8 998848 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998848 PENO GSU34 13.8 1 345440 5PENOCREK 161 998848 PENO GSU34 13.8 1 345443 1PENOGEN3 13.8 998851 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998851 PENO GSU34 13.8 1 345440 5PENOCREK 161 998851 PENO GSU34 13.8 1 345443 1PENOGEN3 13.8 998855 PENO GSU34 13.8 1 345444 1PENOGEN4 13.8 998855 PENO GSU34 13.8 1 345440 5PENOCREK 161 998855 PENO GSU34 13.8 1 | External | 130.32 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.99 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 100.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 106.21 | 106126: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 131.72 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 131.67 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 124.96 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 124.93 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.33 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | External | 102.33 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 630902 VINTON 8 69.0 631087 VINTON 5 161 1 | 100 | 100 | 0.00017 | 102.54 | Base Case | External | 102.54 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 3e-05 | 127.33 | P23:345:MEC:ATCHISON CO 903 | External | 127.3 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 167.16 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 167.13 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 112.48 | P13:138-24:AEPW:TURK 4 | External | 112.45 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 103.23 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 103.2 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00884 | 112.87 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.84 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 155.79 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 155.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 117.18 | P23:345-161:XEL:ADAMS_I:681_S | External | 117.15 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00025 | 141.98 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 141.97 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.51 | P11:6:XEL:AUTO-SINGLE:HOLCOMBG:1 | External | 132.51 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.22 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 102.21 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.58 | 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2: 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2 | External | 114.54 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.73 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 102.73 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 9e-05 | 173.22 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 173.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636617 SB 56 #1 8 69.0 1 | 125 | 125 | 2e-05 | 118.08 | Base Case | External | 118.08 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 9e-05 | 131.52 | Base Case | External | 131.52 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.41 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 140.37 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631063 ROCK CK5 161 631065 BVR CHN L1 5 161 1 | 200 | 237 | 0.00025 | 126.51 | Base Case | External | 126.5 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0001 | 105.7 | P23:345:ALTW:MITCHLCO:1130 | External | 105.69 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 120.65 | P23:345:ALTW:MITCHLCO:1130 | External | 120.62 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 680110 GENOA 69.0 9 | 67.2 | 82 | 2e-05 | 168.35 | Base Case | External | 168.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 109.86 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 109.82 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00376 | 105.2 | P12:345:AMMO::AUDRAIN:SPS:1 | External | 105.14 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 103.57 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 103.53 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0105 | 114.03 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 114 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 139.06 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 138.99 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.0003 | 108.06 | P23:345-161:XEL:ADAMS_I:680_S | External | 108.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.66 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 116.65 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 141.98 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 141.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.43 | 602031 WHT 56 5 161 3WXFMR WHT 56 5 1: 602031 WHT 56 5 161 997623 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997623 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997623 WHT 56 5 13.8 1 602031 WHT 56 5 161 997630 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997630 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997630 WHT 56 5 13.8 1 602031 WHT 56 5 161 997624 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997624 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997624 WHT 56 5 13.8 1 | External | 102.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 128.71 | P11:34:ALTW:AUTO-SINGLE:H007_WF9:1 | External | 128.71 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.4 | P13:13-161:DPC:AUTO-SINGLE:ELKMDGEN:ELKMND5:1 | External | 102.4 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.43 | P13:13-13-161:XEL:AUTO-SINGLE:WHT51G:WHT52G:WHT145:1 | External | 102.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631032 SQUARED7 115 1 | 164 | 164 | 0.00068 | 173.02 | Base Case | External | 173.02 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 116.32 | 104734: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 116.31 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | P23:345:ALTW:MITCHLCO:1150 | External | 103.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 112.47 | P11:HV:EES::TURKCOAL:1 | External | 112.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 114.53 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 114.5 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 154.76 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 154.74 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 127.46 | Base Case | External | 127.46 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.32 | P12:HV:EES::6BIG_CAJUN1%:6FANCY_PT%:1 | External | 102.32 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 139.98 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 139.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 107.47 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 107.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.96 | 336175 6UCARBD% 230 336176 1UCARBGT1! 13.8 1: 336175 6UCARBD% 230 336176 1UCARBGT1! 13.8 1 | External | 103.95 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.39 | P42:345:OKGE:SB_CION7384 | External | 106.38 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 155.79 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 155.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00015 | 102.43 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 102.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.48 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 102.47 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 108.86 | P11:115:XEL:AUTO-SINGLE:FIBROMN7:1 | External | 108.85 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01223 | 135.76 | P23:345:ALTW:MITCHLCO:1160 | External | 135.69 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 140.76 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 140.75 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 130.83 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 130.79 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 4e-05 | 104.9 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 104.89 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.8 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 101.77 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00064 | 132.65 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 132.62 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 124.14 | Base Case | External | 124.14 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 125.23 | Base Case | External | 125.2 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 122.55 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 122.52 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.28 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 110.27 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 115.33 | 104739: 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 115.29 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00056 | 102.73 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External | 102.72 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.74 | 81747: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 100.72 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.35 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 102.34 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 9e-05 | 103.23 | P23:345:ALTW:MITCHLCO:1140 | External | 103.23 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.77 | 104722: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 114.73 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00042 | 104.74 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 104.73 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 9e-05 | 132.51 | P13:6-115:XEL:AUTO-SINGLE:HOLCOMBG:HOLCOMB7:1 | External | 132.51 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.83 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 114.79 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0012 | 113.59 | P23:345-161:XEL:ADAMS_I:681_S | External | 113.58 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 103.24 | 1061260: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 | External | 103.23 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 106.21 | 1061261: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 | External | 106.2 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 110.85 | 104731: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 110.84 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.22 | P23:345:ALTW:MITCHLCO:1150 | External | 175.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.36 | P11:13:XEL:AUTO-SINGLE:BFT86G:6 | External | 102.35 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.01 | P23:345:ALTW:MITCHLCO:1130 | External | 104.01 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 1 | 112 | 112 | 2e-05 | 124.27 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 124.26 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | 112 | 133.9 | 1e-05 | 125.22 | Base Case | External | 125.22 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 2 | 112 | 112 | 2e-05 | 114.77 | Base Case | External | 114.77 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 2 | 112 | 112 | 2e-05 | 124.36 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 124.35 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631063 ROCK CK5 161 631065 BVR CHN L1 5 161 1 | 200 | 237 | 0.00025 | 110.18 | 630175 ROCKCKW8 69 631062 ROCKCKW5 161 1: 630175 ROCKCKW8 69.0 631062 ROCKCKW5 161 1 | External | 110.18 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 105.9 | 620209 HETLAND7 115 620109 HETLAND9 41.6 1: 620209 HETLAND7 115 620109 HETLAND9 41.6 1 | External | 105.9 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01068 | 117.96 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 117.93 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997484 WEB AB 161 1 | 560 | 560 | 0.00209 | 122.99 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 122.97 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 105.37 | Base Case | External | 105.36 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 113.06 | P12:161:XEL:JEF-WHT | External | 113.03 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 102.79 | P23:345-161:XEL:ADAMS_I:680_S | External | 102.77 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615400 GRE-PRKWDB27 115 997565 PAR115-69-2 69.0 2 | 140 | 140 | 0.00015 | 164.1 | Base Case | External | 164.1 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.47 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 101.45 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 128.79 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 128.75 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 101.66 | P11:HV:EES::FLINTCR1:1 | External | 101.58 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 106.4 | P11:18:AEPW:OECSTM 1 | External | 106.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 5e-05 | 127.35 | P12:115:XEL:JIM-HLC | External | 127.35 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 7e-05 | 115.01 | Base Case | External | 115.01 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 178.96 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 178.92 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | P12:765:AEP:AEP ROCKP-AEP JEFF 765 | External | 103.98 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615572 GRE-MEDINA 7 115 997537 115/69 69.0 1 | 84 | 84 | 7e-05 | 113.52 | Base Case | External | 113.52 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.0001 | 115.62 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 115.62 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.19 | P11:0:ALTW:AUTO-SINGLE:G947_GEN:1 | External | 113.15 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00059 | 102.74 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 102.73 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 117.35 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 117.32 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0021 | 176.41 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 176.36 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 138.62 | 672581 GLASLYN 6 138 672596 BRADA 6 138 1: 672581 GLASLYN 6 138 672596 BRADA 6 138 1 | External | 138.61 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 4e-05 | 117.08 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 117.08 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.83 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 139.83 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00953 | 113.02 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 112.99 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 132.41 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 132.38 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 184.16 | P23:345-161:XEL:ADAMS_I:680_S | External | 184.16 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.5 | 92455: 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External | 102.44 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 120.93 | P23:345:ALTW:MITCHLCO:1160 | External | 120.89 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00884 | 112.87 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.84 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 109.7 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 109.7 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 138.41 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 138.34 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00099 | 128.11 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 128.07 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.34 | 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1: 600168 CORNELL HYD 7.20 603154 CORNELL HYD7 115 1 | External | 102.34 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.55 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 121.53 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 106.01 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal | 104.72 | 1.29
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00383 | 105.43 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 105.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 103.99 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.15 | 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1: 600129 HOLCOMB G 6.90 603150 HOLCOMB7 115 1 | External | 139.14 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00066 | 116.67 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | External | 116.66 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 140.53 | P11:13:XEL:AUTO-SINGLE:WHT52G:2 | External | 140.51 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 179.33 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 179.28 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01223 | 135.67 | P23:345:ALTW:MITCHLCO:1150 | External | 135.61 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 139.84 | 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2: 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2 | External | 139.8 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 137.97 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External | 137.9 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 105.18 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | Internal | 103.77 | 1.41
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.5 | P12:161:XEL:JEF-WHT | External | 102.5 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00044 | 102.82 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 102.81 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 8e-05 | 103.44 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 103.44 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.47 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 108.42 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 116.28 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 116.24 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 101.19 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 101.18 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.85 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 114.79 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.27 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 175.27 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.67 | P11:HV:EES::PIRKEY 1:1 | External | 100.66 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00184 | 136.19 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 136.15 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00132 | 147.59 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 147.55 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00376 | 106.31 | 81737: 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 2 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 1 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 2 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 106.26 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00015 | 100.81 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 100.79 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.48 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 140.44 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 4e-05 | 104.88 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 104.88 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00124 | 121.9 | P23:345:ALTW:MITCHLCO:1150 | External | 121.86 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.97 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 101.94 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 116.59 | Base Case | External | 116.58 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 102.14 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 102.11 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 344290 5CARBID T 161 631084 VIELE 5 161 1 | 136 | 136 | 8e-05 | 115.33 | 92356: 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 115.29 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0001 | 128.03 | P13:013-161:AMMO::PENOCREEK:1 | External | 127.99 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 164.69 | Base Case | External | 164.66 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00913 | 117.71 | P23:345:MEC:ATCHISON CO 903 | External | 117.68 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 102.4 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal | 101.08 | 1.32
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0003 | 160.3 | P23:345:ALTW:MITCHLCO:1130 | External | 160.28 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0098 | 117.65 | P23:345:ALTW:MITCHLCO:1130 | External | 117.62 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00061 | 101.06 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External | 101.04 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00034 | 146.66 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 146.64 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.47 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 108.42 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 123.32 | P23:345-161:XEL:ADAMS_I:680_S | External | 123.31 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.42 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 2: 602030 WHT 14 5 161 997625 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997625 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997625 WHT 14 5 13.8 2 602030 WHT 14 5 161 997632 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997632 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997632 WHT 14 5 13.8 2 | External | 102.42 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 0.00017 | 102.43 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 102.43 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00382 | 102.78 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 102.73 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.16 | 636235 WALL LK5 161 636237 CENTURY B1 9 34.5 1: 636235 WALL LK5 161 636237 CENTURY B1 9 34.5 1 | External | 140.13 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 9e-05 | 103.17 | P23:345:ALTW:MITCHLCO:1150 | External | 103.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 137.48 | P22:345:XEL:ADAMS 3 N1:MN | External | 137.42 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 114.53 | 104749: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | External | 114.5 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00377 | 105.42 | P11:HV:EES::PIRKEY 1:1 | External | 105.36 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01223 | 135.46 | P23:345:ALTW:MITCHLCO:1130 | External | 135.4 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.0001 | 175.17 | P23:345:ALTW:MITCHLCO:1160 | External | 175.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.05 | P11:HV:EES::PIRKEY 1:1 | External | 104.05 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636402 HILLS 8 69.0 2 | 112 | 112 | 2e-05 | 124.28 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 124.27 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07019 | 105.08 | P42:345:SPS:FINNEY_OR70_19L | Internal | 103.8 | 1.28
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 7e-05 | 172.96 | P11:34:ALTW:AUTO-SINGLE:H008_WF9:1 | External | 172.96 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 111.51 | P13:069:MEC:ELECTRIFARM BC | External | 111.48 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.08 | P13:34-161:ALTW:AUTO-SINGLE:G947_WF9:WHISWILLWE5:1 | External | 113.04 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 103.99 | P23:345:ALTW:MITCHLCO:1140 | External | 103.98 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 113.75 | 92675: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 113.75 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 121.39 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 121.36 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 100 | 134 | 3e-05 | 104.12 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 104.12 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00138 | 110.78 | 104853: 562711 G15_023_1 345 640510 HOLT.CO3 345 1 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | External | 110.77 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 106.21 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal | 104.86 | 1.35
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00063 | 139.93 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External | 139.92 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 102.75 | 104742: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 | External | 102.75 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.75 | P13:138-24:AEPW:TURK 4 | External | 116.72 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 102.06 | 8670: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | Internal | 100.84 | 1.22
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00396 | 102.28 | 92674: 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | External | 102.2 | 0.08
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.93 | 636235 WALL LK5 161 636237 CENTURY B1 9 34.5 1: 636235 WALL LK5 161 636237 CENTURY B1 9 34.5 1 | External | 114.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 680110 GENOA 69.0 8 | 67.2 | 78.6 | 2e-05 | 159 | Base Case | External | 159 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 602033 HYDROLN5 161 997629 HYDROLN5 115 6 | 187 | 215.1 | 7e-05 | 132.17 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External | 132.17 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01266 | 139.06 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 138.99 | 0.07
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0001 | 105.69 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 105.68 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.83 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 114.79 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 325 | 325 | 0.00014 | 2958.19 | P13:161-69:ITCM:ROCK CK5 T2:IA-EC | External | 2958.19 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 127.05 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 127.03 | 0.02
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 140.49 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 140.43 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | 213 | 213 | 0.00059 | 355.75 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 355.75 | 0
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 114.85 | 104733: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 114.79 | 0.06
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00978 | 121.9 | P22:345:XEL:ADAMS 3 N1:MN | External | 121.87 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00057 | 102.74 | P22:345:XEL:ADAMS 3 N1:MN | External | 102.73 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00824 | 115.83 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 115.79 | 0.04
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 115.92 | P13:34-161:ALTW:AUTO-SINGLE:GRJCT9:GRJCT5:1 | External | 115.89 | 0.03
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00054 | 179.89 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 179.84 | 0.05
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0012 | 113.59 | P23:345-161:XEL:ADAMS_I:680_S | External | 113.58 | 0.01
Thermal | 00NR | S2 | 20SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00021 | 146.95 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 146.94 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 121.53 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 121.53 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 3e-05 | 150.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 150.59 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.12 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 114.11 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 100.08 | P23:345:GRE:PVS 19JB4 | External | 100.07 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00012 | 101.64 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 101.63 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.02 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 114.01 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 106.51 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 106.51 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 138.69 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.69 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00075 | 106.99 | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 106.98 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00098 | 109.5 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 109.49 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 103.29 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 103.28 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00134 | 106.33 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 106.32 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 107.04 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 107.03 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 102.01 | P13:69-161:ALTW:AUTO-SINGLE:LUCAS8:LUCAS5:1 | External | 102.01 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.4 | 92386: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 106.41 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00213 | 103.22 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997726 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997726 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997733 RIVERTON 69.0 1 547469 RIV4525 161 997733 RIVERTON 69.0 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 | External | 103.27 | -0.05
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 103.29 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 103.28 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 102.16 | P23:345:MEC:MONTEZUMA 903 | External | 102.15 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00026 | 120.01 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 120 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00028 | 104.55 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.55 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 100.74 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998338 COLAUTO3 138 1 512705 COLLINS4 138 998346 COLAUTO3 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 | External | 100.72 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 102.99 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 156.31 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 156.3 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00159 | 107.76 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 107.79 | -0.03
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00023 | 167.41 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 167.41 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 102.54 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.54 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00012 | 122.66 | P12:161:ALTW:AUTO-SINGLE:PARNEL5:WILLIAMSBRG5:1 | External | 122.66 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 102.75 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 102.74 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.52 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 109.52 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 100.89 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 100.89 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00031 | 116.48 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 116.47 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 102.01 | P12:161:ALTW:AUTO-SINGLE:OTTUMWA5:LUCAS5:1 | External | 102.01 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00047 | 125.18 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 125.17 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.86 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 113.87 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 118.93 | P23:345:MEC:LOUISA 964 | External | 118.92 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.0056 | 100.18 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 100.19 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00047 | 125.18 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 125.17 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 228.1 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 228.01 | 0.09
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00035 | 154.16 | P13:115-161:ALTW:AUTO-SINGLE:STONPT7:STONPT5:1 | External | 154.14 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.68 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 114.69 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 101 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14 | External | 101 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.11 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 101.11 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.13 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 114.12 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00035 | 154.2 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 154.19 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 105.62 | 92398: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541163 DOGWDCT1 18.0 541225 PHILL 5 161 1 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 541164 DOGWDCT2 18.0 541225 PHILL 5 161 1 | External | 105.56 | 0.06
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0002 | 128.5 | P12:115:ALTW:AUTO-SINGLE:STONPT7:6ST7:1 | External | 128.49 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00028 | 112.95 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.95 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.28 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 114.27 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.95 | P12:HV:EES::3ELD JACKSON:3ELDORADO.E!:1 | External | 101.95 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00044 | 208.15 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 208.13 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 125.11 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 125.1 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 101.43 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 101.43 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00023 | 167.41 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 167.41 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 102.99 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00044 | 106.31 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 106.31 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00031 | 116.48 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 116.47 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.68 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 114.69 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00028 | 114.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 114.14 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00026 | 104.04 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 104.03 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.15 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 113.14 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 101.08 | P12:138:GRDA:CLEVLND-COLLINS | External | 101.06 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 103.84 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 103.83 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.68 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 114.69 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00026 | 142.79 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 142.78 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00022 | 119.52 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 119.51 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 104.52 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 104.51 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.23 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.22 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.33 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 106.32 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.34 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 106.5 | -0.16
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 228.1 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 228.01 | 0.09
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 103.43 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 103.42 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.88 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 113.87 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00014 | 119.29 | P12:161:ALTW-MEC:AUTO-SINGLE:JASPER5:NEANKNY5:1 | External | 119.28 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.11 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.11 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00054 | 107.97 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 107.97 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00015 | 113.71 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 113.7 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 103.24 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 103.24 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 103.43 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 103.42 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.78 | P13:13-115:ALTW:AUTO-SINGLE:SUTHLCT2:M-TOWN7:1 | External | 113.78 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.0056 | 123.99 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 123.94 | 0.05
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00044 | 208.15 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 208.13 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.41 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 106.4 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.23 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 106.21 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 121.9 | P13:69-161:ALTW:AUTO-SINGLE:HIAWATAJ18:HIAWATA5:1 | External | 121.89 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.27 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.26 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 123.87 | P23:345:MEC:HILLS 984 | External | 123.87 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 5e-05 | 100.53 | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1: 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | External | 100.53 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00054 | 106.02 | P12:161:AECI-INDN:ECKLES-5LEVASY:: | External | 106.01 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.86 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 113.87 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00044 | 106.31 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 106.31 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.52 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 102.52 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 100.05 | P23:345:GRE:PVS 19JB1 | External | 100.05 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.39 | 104730: 532852 JEC 6 230 532651 JEC U1 26.0 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | External | 114.38 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 102.75 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 102.74 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00033 | 116.23 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 116.21 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 122.04 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 122.03 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 101.08 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 101.06 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 107.57 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 107.57 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.86 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 113.87 | -0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.24 | 92478: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 114.23 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.95 | 337552 3ELD JACKSON 115 337553 3ELDORADO.E! 115 1: 337552 3ELD JACKSON 115 337553 3ELDORADO.E! 115 1 | External | 101.95 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 119.51 | P21:345:CE-MEC:AUTO-SINGLE:QUAD6-7:SUB913:1 | External | 119.5 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 118.83 | P23:345:XEL:SPS 8S72 HNA | External | 118.83 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00014 | 127.01 | P13:69-161:ALTW:AUTO-SINGLE:VINTON8:VINTON5:1 | External | 127.01 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 104.45 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 104.44 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 119.91 | P21:345:ALTW-MEC:AUTO-SINGLE:NEWHILLSITC3:HILLS3:1 | External | 119.9 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0002 | 131.01 | P13:69-161:ALTW:AUTO-SINGLE:PARNEL8:PARNEL5:1 | External | 131 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0002 | 131.01 | 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1: 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1 | External | 131 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00026 | 104.04 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 104.03 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.28 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 114.27 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.18 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | External | 114.17 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.87 | P11:13:ALTW:AUTO-SINGLE:SUTHLCT1:1C | External | 113.87 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.02 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | External | 114.01 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00026 | 142.79 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 142.78 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00014 | 127.01 | 630902 VINTON 8 69 631087 VINTON 5 161 1: 630902 VINTON 8 69.0 631087 VINTON 5 161 1 | External | 127.01 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00062 | 101.91 | P12:69:GRDA:PAWNEEGR-CLEVDSTK | External | 101.9 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.52 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 109.52 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0002 | 126.57 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 126.57 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 103.25 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 103.24 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0002 | 131.01 | P13:34-161:ALTW:AUTO-SINGLE:PARNEL9:PARNEL5:1 | External | 131 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00012 | 127.78 | P12:161:ALTW:AUTO-SINGLE:PLAZA5:M-TOWN5:1 | External | 127.78 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00099 | 100.57 | 103887: 301999 2PARKMDWS 69.0 512703 PARKMEDTP 69.0 1 512703 PARKMEDTP 69.0 512870 COLNSGR2 69.0 1 512703 PARKMEDTP 69.0 512871 SKIATTP2 69.0 1 300994 2GREEN 69.0 512874 GREENTP2 69.0 1 512872 SKIATOK2 69.0 512873 SKIATCTY2 69.0 1 512871 SKIATTP2 69.0 512872 SKIATOK2 69.0 1 512876 OSAGEK2 69.0 512877 CLEVDSTK2 69.0 1 512875 PRUEK2 69.0 512876 OSAGEK2 69.0 1 512871 SKIATTP2 69.0 512874 GREENTP2 69.0 1 512874 GREENTP2 69.0 512875 PRUEK2 69.0 1 300927 2CLEVLND 69.0 512876 OSAGEK2 69.0 1 | External | 100.55 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00026 | 138.81 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:M-TOWN5:1 | External | 138.8 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.06 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.06 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.0001 | 126.37 | P12:161:ALTW:AUTO-SINGLE:JASPER5:LAUREL_5:1 | External | 126.37 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.27 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 114.26 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 119.99 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 119.98 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.39 | 92349: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 114.38 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00035 | 154.2 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 154.19 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 112.82 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.81 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 2e-05 | 100.71 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 100.71 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00063 | 100.77 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 100.77 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00026 | 105.58 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 105.58 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 105.72 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 105.7 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00044 | 109.27 | P11:024:DPC:ALMA2:6 | External | 109.26 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.77 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 106.76 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 122.36 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 122.36 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00059 | 106.22 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 106.22 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.44 | 92463: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 106.44 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 122.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 122.53 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.41 | 300948 2SFORKK 69 300165 4SFORKK 138 1: 300948 2SFORKK 69.0 300165 4SFORKK 138 1 | External | 100.39 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 110.13 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 110.13 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 122.17 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.17 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 113.1 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 113.1 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00025 | 142.81 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 142.8 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00257 | 114.29 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 114.24 | 0.05
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 111.18 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 111.18 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.42 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.41 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.88 | P13:13-115:ALTW:AUTO-SINGLE:SUTHLCT1:M-TOWN7:1 | External | 113.87 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.4 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 114.39 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 105.13 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 105.12 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 123.04 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 123.04 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00044 | 109.27 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 109.26 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00022 | 141.34 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.34 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 125.32 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 125.31 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 126.4 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 126.4 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 116.82 | Base Case | External | 116.81 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.43 | 300165 4SFORKK 138 301339 4SFORKKTP 138 1: 300165 4SFORKK 138 301339 4SFORKKTP 138 1 | External | 100.41 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 123.62 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA | External | 123.62 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 228.1 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 228.01 | 0.09
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00035 | 154.16 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 154.14 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00157 | 106.76 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External | 106.78 | -0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 120.17 | P23:345:MEC:HILLS 9114 | External | 120.17 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00164 | 103.46 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External | 103.44 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00055 | 106.03 | 92154: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 106.02 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.11 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.11 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 101.43 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 101.43 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 4e-05 | 115.58 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 115.58 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.11 | P23:345:MEC:MONTEZUMA 902 | External | 101.11 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 113.95 | P11:345:MEC:GDMEC ST | External | 113.94 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 114.06 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.06 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997052 GLENHAM TR1 115 1 | 25 | 31 | 0.0002 | 112.91 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.91 | 0
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00098 | 103.37 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 103.36 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 125.11 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 125.1 | 0.01
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00033 | 116.31 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 116.29 | 0.02
Thermal | 04HVER | S1 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 111.18 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 111.18 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00099 | 116.5 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 118.23 | -1.73
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01244 | 117.85 | Base Case | External | 122.5 | -4.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00021 | 129.73 | P23:500:EES-EAI:WH_BLF:B7914 | External | 129.72 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01035 | 106.7 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 107.24 | -0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 121.14 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00086 | 100.68 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 100.62 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00188 | 123.38 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 125.13 | -1.75
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 2e-05 | 106.66 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01167 | 131.12 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 8e-05 | 132.18 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00454 | 105.66 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 108.25 | -2.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 400 | 430 | 0.03002 | 103.05 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 103.11 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00332 | 104.49 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 105.26 | -0.77
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 235.41 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.86 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00037 | 113.28 | P23:345:MEC:LOUISA 954 | External | 115.7 | -2.42
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 109.11 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 113.28 | -4.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 109.65 | Base Case | External | 110.91 | -1.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 117.89 | P23:345:MEC:GDMEC 901 | External | 123.06 | -5.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 176.8 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 181.26 | -4.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00455 | 104.37 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 107.44 | -3.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00074 | 119.96 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 122.25 | -2.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00076 | 142.55 | P23:345:ITCM:HCKRYCK:FUT2 | External | 143.26 | -0.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00179 | 123.34 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 128.79 | -5.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00177 | 121.17 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 125.14 | -3.97
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 147.11 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 149.14 | -2.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533013 MOUND 4 138 997898 MOUN TX-2 115 1 | 250 | 275 | 0.0685 | 118.91 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 121.58 | -2.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533416 RENO 3 115 533429 MOUNDRG3 115 1 | 218 | 262 | 0.07816 | 125.12 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 128.83 | -3.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00035 | 106.95 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 107.31 | -0.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00015 | 103.33 | P23:345-161:XEL:ADAMS_I:680_S | External | 106.79 | -3.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00132 | 126.82 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 132.25 | -5.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01148 | 121.28 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 122.79 | -1.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00099 | 116.5 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 118.23 | -1.73
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00076 | 142.55 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 143.26 | -0.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00737 | 122.86 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 124.85 | -1.99
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00031 | 129.03 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 128.44 | 0.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00202 | 101.5 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 5e-05 | 116.2 | P23:345:XEL:8N22 SHC | External | 118.43 | -2.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00266 | 119.55 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 119.66 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00028 | 102.27 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External | 104.78 | -2.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00174 | 113.5 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 112.78 | 0.72
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00021 | 132.21 | P23:500:EES-EAI:WH_BLF:B7914 | External | 132.2 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07018 | 105.83 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal | 106.42 | -0.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 4e-05 | 127.32 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 130.56 | -3.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00331 | 117.82 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 119.9 | -2.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636204 DR NE 5 161 636210 WASHBRN5 161 1 | 272 | 272 | 0.00013 | 105.63 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 108.38 | -2.75
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00109 | 103.75 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 107.3 | -3.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00161 | 104.14 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00288 | 100.68 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 101.11 | -0.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00098 | 117.28 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 119.67 | -2.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 147.25 | Base Case | External | 150.85 | -3.6
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 112.26 | P12:161:DPC:RCE-HAR5 | External | 109.13 | 3.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 5e-05 | 110.51 | P23:345:XEL:8N22 SHC | External | 111.88 | -1.37
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00188 | 123.38 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 125.13 | -1.75
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533416 RENO 3 115 533429 MOUNDRG3 115 1 | 218 | 262 | 0.07816 | 125.12 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 128.83 | -3.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01148 | 115.1 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 116.48 | -1.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 681528 HARMONY5 161 1 | 240 | 264 | 0.0006 | 104.37 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 105.27 | -0.9
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00257 | 116.55 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 117.54 | -0.99
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00032 | 127.54 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 128.01 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 235.41 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 234.86 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 114.02 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 113.23 | 0.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00228 | 127.36 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 129.81 | -2.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00032 | 115.48 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 179.27 | P11:024:DPC:ALMA2:6 | External | 183.81 | -4.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00127 | 104.9 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 106.74 | -1.84
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 115.52 | 608676 HIBBARD7 115 608680 WNTR ST7 115 1: 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00672 | 109.33 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 111.82 | -2.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00094 | 151.6 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 147.99 | 3.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 149.82 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 152.38 | -2.56
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 4e-05 | 127.32 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 130.56 | -3.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00096 | 121.05 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.34 | -2.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0113 | 127.93 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 129.69 | -1.76
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.05 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998338 COLAUTO3 138 1 512705 COLLINS4 138 998346 COLAUTO3 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 | External | 101.35 | -0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 104.57 | Base Case | External | 108.49 | -3.92
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 122.84 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 123.07 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 103.46 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 103.94 | -0.48
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00172 | 117.21 | P23:345:MEC:GDMEC 901 | External | 122.03 | -4.82
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00084 | 135.93 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 136.19 | -0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15191 | 100.25 | 92668: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00502 | 115.51 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 119.42 | -3.91
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 200.92 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 202.2 | -1.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03685 | 113.62 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 113.61 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00028 | 118.38 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 126.91 | -8.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00044 | 116.65 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 116.84 | -0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00187 | 148.45 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 152.5 | -4.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 8e-05 | 122.8 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 126.93 | -4.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 125.12 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 130.57 | -5.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00124 | 111.18 | P23:345:AMIL::HERLEMAN:1 | External | 112.16 | -0.98
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00765 | 107.55 | P23:345:MEC:GRIMES 901 | External | 109.76 | -2.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00114 | 114.87 | Base Case | External | 111.66 | 3.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00289 | 111.53 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 115.21 | -3.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 143.88 | P23:345:MEC:GDMEC 901 | External | 149.11 | -5.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 113.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.83 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 103.5 | P11:345:AMMO::CALLAWAY:1 | External | 104.09 | -0.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00288 | 101.22 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 101.61 | -0.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00019 | 110.43 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 111.13 | -0.7
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00023 | 101.31 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 101.32 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00066 | 102.21 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 109.14 | -6.93
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01035 | 107.46 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 107.7 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00523 | 113.96 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 115.05 | -1.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635701 SYCAMOR5 161 997479 DAG9T1 161 1 | 500 | 550 | 0.00278 | 114.06 | P23:345:MEC:SYCAMORE 902 | External | 115.71 | -1.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00023 | 101.31 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 101.32 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00076 | 142.55 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 143.26 | -0.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00112 | 107.67 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 113.32 | -5.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08886 | 129.2 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 130.23 | -1.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00096 | 121.05 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 123.34 | -2.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 197.27 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997578 345-161 161 1 | 500 | 500 | 0.00038 | 105.79 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 106.3 | -0.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 2e-05 | 106.66 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00096 | 121.05 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.34 | -2.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 111.54 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 110.74 | 0.8
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 112.27 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 111.46 | 0.81
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00099 | 119.3 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 121.74 | -2.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03685 | 113.62 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 113.61 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00057 | 100.29 | P23:345:XEL:8S50 HMP | External | 101.78 | -1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 107.65 | P23:345-161:XEL:ADAMS_I:681_S | External | 103.62 | 4.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00805 | 118.94 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01035 | 107.47 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 107.71 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 126.06 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 131.32 | -5.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00066 | 101.46 | P11:HV:EES::1WAT U3!:1 | External | 108.41 | -6.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00068 | 108 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 109.09 | -1.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00075 | 120.16 | P23:345:XEL:8S22 WLM | External | 123.4 | -3.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00192 | 130.06 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 135.17 | -5.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01244 | 117.93 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 121.67 | -3.74
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01035 | 122.56 | Base Case | External | 123.95 | -1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00027 | 102.97 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.79 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00044 | 103.61 | P23:345:XEL:8S51 HMP | External | 105.29 | -1.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533035 CHISHLM4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03685 | 107.9 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 107.6 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00019 | 110.43 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 111.13 | -0.7
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 114.68 | P23:345-161:XEL:ADAMS_I:681_S | External | 110.67 | 4.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 122.72 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 122.98 | -0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07471 | 116.56 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 116.94 | -0.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 117.89 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00837 | 123.4 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 125.9 | -2.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 146.97 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 148.92 | -1.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 122.72 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 122.98 | -0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00041 | 100.05 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 101.35 | -1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 7e-05 | 128.03 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 129.2 | -1.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00163 | 119.22 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 119.82 | -0.6
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 113.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.68 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00031 | 129.12 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 128.53 | 0.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 118.53 | P11:024:DPC:ALMA2:6 | External | 121.12 | -2.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00144 | 109.14 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00074 | 119.96 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 122.25 | -2.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00483 | 111.09 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 112.61 | -1.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00177 | 114.15 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 113.41 | 0.74
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635700 SYCAMOR3 345 997479 DAG9T1 161 1 | 500 | 550 | 0.00278 | 115.77 | P23:345:MEC:SYCAMORE 902 | External | 117.74 | -1.97
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 114.51 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 121.95 | -7.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00208 | 114.97 | P23:345:XEL:8S81 SSL | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00203 | 114.18 | P23:345:XEL:SPS 8S72 HNA | External | 116.18 | -2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 126.06 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 131.32 | -5.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 122.06 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.05 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00033 | 117.35 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 119.75 | -2.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00206 | 158.19 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 163.38 | -5.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 114.51 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 121.95 | -7.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00112 | 106.72 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 112.39 | -5.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00027 | 104.86 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 6e-05 | 109.64 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 110.49 | -0.85
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00027 | 101.73 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.54 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 104.15 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.1 | -9.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 116.81 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 118.55 | -1.74
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 113.55 | Base Case | External | 114.27 | -0.72
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00014 | 108.64 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 113.26 | -4.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00161 | 102.66 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 102.15 | 0.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 116.12 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 118.36 | -2.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 112.64 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 111.85 | 0.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00139 | 133.02 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 138.26 | -5.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00032 | 115.66 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 117.97 | -2.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00015 | 103.33 | P23:345-161:XEL:ADAMS_I:681_S | External | 106.79 | -3.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00175 | 100.68 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.24 | -1.56
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 142.23 | Base Case | External | 144.84 | -2.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 109.87 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External | 112.39 | -2.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00072 | 104.91 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 104.07 | 0.84
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 104.15 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.1 | -9.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08886 | 129.2 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 130.23 | -1.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 681528 HARMONY5 161 1 | 240 | 264 | 0.0006 | 104.37 | P12:161:ITCM:AUTOSINGLE:LANSINGW:GENOA:1 | External | 105.27 | -0.9
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.41 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 101.68 | -0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0113 | 130.59 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 131.58 | -0.99
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 2e-05 | 106.66 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00109 | 103.75 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 107.3 | -3.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 681528 HARMONY5 161 1 | 240 | 264 | 0.0006 | 104.37 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 105.27 | -0.9
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00094 | 151.6 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 147.99 | 3.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00053 | 104.73 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 106.99 | -2.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.0009 | 100.09 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00033 | 117.54 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 120.05 | -2.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00076 | 125.7 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 132.15 | -6.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 100.86 | Base Case | External | 101.65 | -0.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 103.6 | Base Case | External | 104.93 | -1.33
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00041 | 100.05 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 101.35 | -1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00081 | 106.63 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External | 106.01 | 0.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07471 | 116.56 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 116.94 | -0.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00147 | 160.83 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 166.38 | -5.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00649 | 127.44 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 114.54 | 12.9
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00357 | 112.96 | P23:345:MEC:GDMEC 901 | External | 117.69 | -4.73
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01035 | 102.4 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 103.34 | -0.94
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00165 | 106.14 | P23:345:MEC:BLACK HAWK 901 | External | 108.21 | -2.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00014 | 108.64 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 113.26 | -4.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 2 | 500 | 500 | 0.00038 | 105.24 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 105.63 | -0.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00053 | 109.13 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 108.58 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00523 | 113.96 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 115.05 | -1.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00071 | 103.01 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 104.01 | -1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533429 MOUNDRG3 115 997898 MOUN TX-2 115 1 | 239 | 239 | 0.0685 | 136.12 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 139.24 | -3.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.0009 | 106 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 107.65 | -1.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00032 | 127.78 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 128.25 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00463 | 105.62 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 108.79 | -3.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00032 | 115.48 | 601014 AS KING3 345 601028 EAU CL 3 345 1: 601014 AS KING3 345 601028 EAU CL 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01148 | 121.23 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 122.72 | -1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 200.92 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 202.2 | -1.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00044 | 116.76 | P23:345:AMMO::MONTGOMERY:V43 | External | 117.55 | -0.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 113.28 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 112.49 | 0.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 139.74 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 141.95 | -2.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00029 | 109.89 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 109.96 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00092 | 140.77 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 137.2 | 3.57
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00098 | 123.68 | P23:345:MEC:OAK GROVE 901 | External | 126.22 | -2.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00032 | 115.66 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 117.97 | -2.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00124 | 179.52 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 182.57 | -3.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00672 | 109.33 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 111.82 | -2.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00167 | 103.58 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00092 | 140.77 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 137.2 | 3.57
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 117.98 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532796 WICHITA7 345 997933 WICH TX-12 138 1 | 400 | 430 | 0.03002 | 103.05 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 103.11 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00037 | 105.57 | P23:345:MEC:LOUISA 954 | External | 107.87 | -2.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00086 | 100.68 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 100.62 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00028 | 118.38 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 126.91 | -8.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01035 | 106.7 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 107.24 | -0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00355 | 116.02 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 120.22 | -4.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00276 | 103.92 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 105.87 | -1.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00122 | 103.01 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998347 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998346 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998355 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998354 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 103.47 | -0.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01167 | 131.87 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00228 | 127.36 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 129.81 | -2.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00099 | 119.3 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 121.74 | -2.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00289 | 111.53 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 115.21 | -3.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00431 | 100.88 | P23:345:MEC:SYCAMORE 901 | External | 103.33 | -2.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.48 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.51 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00112 | 109.91 | Base Case | External | 106.45 | 3.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00086 | 100.68 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 100.62 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 118.53 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 121.12 | -2.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 197.27 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00044 | 116.77 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 116.97 | -0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 179.27 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 183.81 | -4.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00023 | 102.7 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 102.71 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 2 | 500 | 500 | 0.00038 | 106.73 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 107.25 | -0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 997933 WICH TX-12 138 1 | 400 | 430 | 0.03002 | 102.95 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 102.85 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00103 | 113.49 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 115.79 | -2.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 107.28 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.98 | -0.7
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 110.43 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 111.68 | -1.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00015 | 141.59 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00332 | 112.32 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 114.71 | -2.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00074 | 122.09 | P23:345:XEL:8S23 WLM | External | 124.72 | -2.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636202 MIDPORT5 161 636203 LUNDQST5 161 1 | 231 | 231 | 1e-05 | 102.07 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 104.31 | -2.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00032 | 115.48 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 4e-05 | 133.52 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.39 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00672 | 109.33 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 111.82 | -2.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 109.86 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External | 112.52 | -2.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.41 | P12:138:GRDA:CLEVLND-COLLINS | External | 101.68 | -0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00288 | 101.21 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 101.61 | -0.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00218 | 101.57 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997726 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997726 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997733 RIVERTON 69.0 1 547469 RIV4525 161 997733 RIVERTON 69.0 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 | External | 101.79 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00837 | 123.4 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 125.9 | -2.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00044 | 116.64 | P23:345:AMMO::MONTGOMERY:V43 | External | 117.42 | -0.78
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08119 | 139.12 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 114.68 | P23:345-161:XEL:ADAMS_I:680_S | External | 110.67 | 4.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.0009 | 111.32 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 111 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 139.92 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 141.16 | -1.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533035 CHISHLM4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03685 | 107.9 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 107.6 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 6e-05 | 109.64 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 110.49 | -0.85
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 138.67 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 141.5 | -2.83
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00023 | 130.91 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.92 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00171 | 116.4 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 120.23 | -3.83
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00649 | 106.73 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 121.14 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 139.92 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 141.16 | -1.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00276 | 112.59 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00138 | 124.1 | Base Case | External | 127.72 | -3.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 3e-05 | 127.03 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 129.97 | -2.94
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 115.85 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 123.76 | -7.91
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00405 | 100.05 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 100.57 | -0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.0002 | 130.92 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 134.19 | -3.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0113 | 129.93 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 131.26 | -1.33
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 121.14 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01167 | 129.57 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.0009 | 106 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 107.65 | -1.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 117.37 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 119.07 | -1.7
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00355 | 116.02 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 120.22 | -4.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00163 | 119.75 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 120.33 | -0.58
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01035 | 107.47 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 107.71 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 149.52 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 151.82 | -2.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00103 | 113.49 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 115.79 | -2.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00052 | 108.73 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 108.09 | 0.64
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 103.83 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 103.79 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 149.26 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 151.62 | -2.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 235.41 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.86 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997578 345-161 161 1 | 500 | 500 | 0.00038 | 104.3 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 104.68 | -0.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00202 | 117.05 | P23:345:XEL:8S72 HNA | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00061 | 102.61 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 106.31 | 608633 FAIRMPK7 115 608683 STIN-MN7 115 1: 608633 FAIRMPK7 115 608683 STIN-MN7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 183.27 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 184.16 | -0.89
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00011 | 101.47 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 102.55 | -1.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00032 | 101.56 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 105.72 | -4.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00575 | 113.2 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 114.01 | -0.81
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 2 | 500 | 500 | 0.00038 | 106.73 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 107.25 | -0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636215 SHAULISRD5 161 636220 EL FARM5 161 1 | 215 | 215 | 0.00017 | 121.4 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 125.07 | -3.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06898 | 105.23 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 105.59 | P12:161:DPC:RCE-HAR5 | External | 102.3 | 3.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00011 | 101.47 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 102.55 | -1.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00166 | 112.64 | P23:345:MEC:GDMEC 901 | External | 117.25 | -4.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.0009 | 105.54 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 105.24 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997578 345-161 161 1 | 500 | 500 | 0.00038 | 105.79 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 106.3 | -0.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 997933 WICH TX-12 138 1 | 400 | 430 | 0.03002 | 102.95 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 102.85 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00109 | 104.45 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 107.96 | -3.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18236 | 146.75 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 148.8 | -2.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01035 | 122.01 | Base Case | External | 123.44 | -1.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533429 MOUNDRG3 115 997898 MOUN TX-2 115 1 | 239 | 239 | 0.0685 | 136.12 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 139.24 | -3.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0008 | 117.89 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 125.6 | -7.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00445 | 106.86 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 108.13 | -1.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997578 345-161 161 1 | 500 | 500 | 0.00038 | 104.3 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 104.68 | -0.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 7e-05 | 128.03 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 129.2 | -1.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15191 | 100.15 | 92669: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00086 | 122.93 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 121.98 | 0.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00076 | 136.52 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 139.83 | -3.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00102 | 111.54 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 113.86 | -2.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 139.74 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 141.95 | -2.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15191 | 100.73 | 92667: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00032 | 127.54 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 128.01 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00357 | 116.4 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 120.66 | -4.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 109.26 | 608633 FAIRMPK7 115 608680 WNTR ST7 115 1: 608633 FAIRMPK7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00028 | 102.31 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External | 104.69 | -2.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00031 | 104.18 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 112.58 | -8.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 117.23 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 119.89 | -2.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00113 | 116.81 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 118.55 | -1.74
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 122.73 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 122.73 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00227 | 127.73 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 129.53 | -1.8
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 314 | 314 | 0.00098 | 105.58 | P23:345:MEC:OAK GROVE 901 | External | 107.17 | -1.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00332 | 113.13 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 115.61 | -2.48
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.06867 | 121.59 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 129.75 | P23:345:MEC:GDMEC 901 | External | 133.74 | -3.99
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 197.27 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 2 | 500 | 500 | 0.00038 | 105.24 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 105.63 | -0.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.0002 | 100.63 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 105.35 | -4.72
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00081 | 106.63 | P12:161:DPC:AUTO-SINGLE:GENOA5:HARMONY5:1 | External | 106.01 | 0.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636203 LUNDQST5 161 636204 DR NE 5 161 1 | 272 | 272 | 0.00013 | 116.5 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 119.59 | -3.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00276 | 112.77 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00056 | 100 | 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1: 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.33 | -1.33
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 105.4 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 106.05 | -0.65
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00044 | 103.84 | P23:345:XEL:8S51 HMP | External | 105.69 | -1.85
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00112 | 106.72 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 112.39 | -5.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 100.73 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.95 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00332 | 109.62 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 110.31 | -0.69
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533013 MOUND 4 138 997898 MOUN TX-2 115 1 | 250 | 275 | 0.0685 | 118.91 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 121.58 | -2.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 107.65 | P23:345-161:XEL:ADAMS_I:680_S | External | 103.62 | 4.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00147 | 117.13 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 118.52 | -1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 113.38 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 112.58 | 0.8
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00015 | 147.36 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 101.67 | 81734: 337909 8ANO% 500 515305 FTSMITH8 500 1 515305 FTSMITH8 500 998252 FTSMITH3 161 3 515305 FTSMITH8 500 998251 FTSMTH6 161 6 515305 FTSMITH8 500 998250 FTSMITH4 161 4 515305 FTSMITH8 500 998248 FTSMITH1 345 1 515305 FTSMITH8 500 998260 FTSMITH3 161 3 515305 FTSMITH8 500 998259 FTSMTH6 161 6 515305 FTSMITH8 500 998258 FTSMITH4 161 4 515305 FTSMITH8 500 998256 FTSMITH1 345 1 515305 FTSMITH8 500 998257 FTSMITH3 161 3 515305 FTSMITH8 500 998256 FTSMTH6 161 6 515305 FTSMITH8 500 998255 FTSMITH4 161 4 515305 FTSMITH8 500 998253 FTSMITH1 345 1 | External | 101.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P23:345:MEC:MONTEZUMA 902 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.0002 | 126.88 | P23:500:EES-EAI:WH_BLF:B7914 | External | 126.88 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00023 | 104.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.66 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.25 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 103.25 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00145 | 100.39 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | External | 100.39 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00096 | 121.06 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 121.07 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00018 | 175.93 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 175.92 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.26 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 103.26 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.21 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 103.2 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 101.67 | P42:500:OKGE:SB_FTTH8581 | External | 101.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 107.63 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 107.63 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.14 | P12:161:ALTW:AUTO-SINGLE:OTTUMWA5:LUCAS5:1 | External | 105.14 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00045 | 112.91 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 112.9 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.77 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.77 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00463 | 100.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 100.76 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00045 | 112.91 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 112.9 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.94 | P23:345:MEC:MONTEZUMA 903 | External | 102.94 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 100.39 | Base Case | External | 100.38 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.7 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 216.69 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 7e-05 | 116.45 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 116.45 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.65 | P23:345:MEC:HILLS 974 | External | 102.65 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 105.31 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 105.3 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00018 | 175.93 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 175.92 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 105.01 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 105 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 107.63 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 107.63 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00142 | 109.67 | P23:500:EES-EAI:ARK_NU:B5106 | External | 109.68 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 123.85 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 123.69 | 0.16
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00023 | 105.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.9 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00033 | 102.17 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 102.19 | -0.02
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.12 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 102.12 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.47 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.46 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 106.91 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 106.91 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.0002 | 100.27 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 100.26 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.7 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 216.69 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 165.73 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 165.73 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00094 | 114.19 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 114.2 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00463 | 125.15 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 125.14 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00145 | 100.39 | P12:500:EES-EAI:ARK_NU:FTSMTH:1 | External | 100.39 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.14 | P13:69-161:ALTW:AUTO-SINGLE:LUCAS8:LUCAS5:1 | External | 105.14 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00086 | 105.57 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 105.56 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 105.67 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 105.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 105.67 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 105.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00145 | 100.39 | 104899: 337909 8ANO% 500 515305 FTSMITH8 500 1 | External | 100.39 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.97 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.97 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00146 | 100.52 | P42:500:OKGE:SB_FTTH8583 | External | 100.52 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00031 | 107.58 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 107.57 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 101.67 | P42:500:OKGE:SB_FTTH8585 | External | 101.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00096 | 121.06 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 121.07 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.47 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.46 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00094 | 114.19 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 114.2 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.0002 | 129.3 | P23:500:EES-EAI:WH_BLF:B7914 | External | 129.3 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.47 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.46 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.44 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.44 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.05 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 103.05 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 105.33 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 105.32 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.21 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 103.2 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.05 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 103.05 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 104.43 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 104.43 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.7 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 216.69 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 107.35 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 107.34 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 129.81 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 129.81 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 117.68 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.68 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 123.85 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 123.69 | 0.16
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 110.55 | P11:024:DPC:ALMA2:6 | External | 110.55 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.39 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 116.38 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 7e-05 | 116.29 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 116.29 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00031 | 107.65 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 107.64 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 117.25 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.24 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 127 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 126.95 | 0.05
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 108.58 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.58 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00249 | 108.68 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 108.63 | 0.05
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 110.55 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 110.55 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00086 | 105.57 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 105.56 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00051 | 110.76 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.76 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.0002 | 100.76 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 100.76 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.39 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 116.38 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00145 | 100.39 | 337909 8ANO% 500 515305 FTSMITH8 500 1: 337909 8ANO% 500 515305 FTSMITH8 500 1 | External | 100.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00018 | 136.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.97 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 104.96 | 67791: 336426 3CLAB8! 115 336458 3MICH N! 115 1 336462 6MICHO% 230 500360 FRONTST6 230 1 336412 3PATER! 115 336442 3SFORS 115 1 336442 3SFORS 115 336444 3MICH S! 115 1 | External | 104.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | 336462 6MICHO% 230 500360 FRONTST6 230 1: 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 120.96 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 120.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 112.93 | P23:500:EES:BF335618-1~3 | External | 112.9 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 115.61 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 115.61 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.68 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 107.65 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 128.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.38 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.3 | P12:500-230:EES:WILGLN:WATERF | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00073 | 104.49 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 104.48 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 103.68 | P23:500:EES:ABF_WG-A | External | 103.71 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.77 | P23:500:EES:ABF_WG-A | External | 107.8 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.39 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.37 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 104.47 | 336137 6SLIDEL! 230 500360 FRONTST6 230 1: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 | External | 104.47 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.29 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 103.27 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 103.48 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 103.48 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00034 | 101.91 | P12:230:EES:WATERF:VACHER:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 102.79 | P12:230:EES:PANAMA:DBAYOU:1 | External | 102.79 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.78 | P12:500-230:EES:WILGLN:WATERF | External | 103.76 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 115.61 | P12:230:EES:TEZCUC:WATERF:1 | External | 115.61 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 103.68 | P23:500:EES:ABF_WG-A | External | 103.71 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 103.73 | P23:500:EES:BF335618-1~3 | External | 103.71 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.68 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 107.65 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.94 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 108.93 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.46 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.43 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.39 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.79 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.76 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 111.66 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.78 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 116.7 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 116.73 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 119.4 | P12:230:EES:IRONMN:L_GPSY:1 | External | 119.4 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 113.49 | P12:230:EES:BELPNT:TEZCUC:L_GPSY:1 | External | 113.49 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.65 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.62 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.79 | P23:500:EES:BF335618-133 | External | 107.76 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 104.5 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.48 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.9 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.87 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 106.99 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 106.97 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 122.31 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 122.34 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 2e-05 | 130.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 130.1 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.35 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.32 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 114.91 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 114.91 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 111.95 | 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1: 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1 | External | 111.95 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 110.15 | P12:HV:EES::6TEZCUCO%:6IRONMAN%:1 | External | 110.14 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.45 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.41 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 114.91 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 114.91 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 103.73 | P23:500:EES:BF335618-1~3 | External | 103.71 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0003 | 100.4 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00014 | 142.87 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 142.89 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.3 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 102.79 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 102.79 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 109.48 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.44 | P23:500:EES:ABF_WG-E | External | 103.41 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.22 | 80163: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.22 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.83 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.82 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.34 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.31 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00014 | 160.91 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 160.93 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.3 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 109.48 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.47 | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 121.07 | 0.4
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 106.5 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 106.46 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 115.56 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 103.48 | P12:230:EES:TEZCUC:WATERF:1 | External | 103.48 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.22 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.19 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.51 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.48 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 118.75 | P23:500:EES:BF335618-1~3 | External | 118.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.3 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 117.56 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.7 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.67 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 2e-05 | 101.52 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.52 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.23 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.21 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.21 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 118.18 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.3 | P12:500-230:EES:WILGLN:WATERF | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.77 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.74 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.21 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 118.18 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.78 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.76 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.63 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 101.62 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 104.24 | P23:500:EES:ABF_WG-A | External | 104.25 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.22 | 64573: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.22 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 120.96 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 120.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 115.56 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.14 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.11 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 108.06 | P23:500:EES:BF335618-1~3 | External | 108.03 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.39 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.34 | P12:500-230:EES:WILGLN:WATERF | External | 112.31 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.39 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | P12:HV:EES::6MICHO%:FRONTST6:1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.35 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.32 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 108 | P23:500:EES:ABF_WG-A | External | 108.03 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00074 | 104.42 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 104.41 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.22 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.19 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.28 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 118.25 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00011 | 100.32 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 100.34 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.3 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.44 | P23:500:EES:ABF_WG-E | External | 103.41 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 9e-05 | 120.7 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 120.7 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0003 | 100.4 | P12:230:EES:TEZCUC:WATERF:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.56 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 112.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.44 | P23:500:EES:BF335618-133 | External | 103.41 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.94 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 108.93 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.89 | P23:500:EES:ABF_WG-E | External | 103.88 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.0001 | 112.54 | P23:500:EES:BF335618-133 | External | 112.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.39 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | P12:230:EES-CLEC::6MICHO%:FRONTST6:1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 115.61 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 115.61 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00028 | 101.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.74 | 0.05
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.75 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00017 | 130.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.83 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.83 | P23:500:EES:BF335618-1~3 | External | 107.8 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.7 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 107.67 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 103.48 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 103.48 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 112.87 | P23:500:EES:ABF_WG-A | External | 112.9 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.39 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 116.32 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 116.32 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.29 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 103.27 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06811 | 119.24 | P13:230-345:MIDW:POST ROCK | Internal | 118.64 | 0.6
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.59 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.56 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.7 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.67 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 111.11 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 111.13 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.34 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.31 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.71 | P23:500:EES:ABF_WG-E | External | 107.68 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 111.31 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 111.33 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 102.98 | P12:230:EES:STJAME:VACHER:1 | External | 102.98 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.39 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 112.36 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06947 | 120.91 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.12 | 0.79
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.39 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.37 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.29 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 103.27 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 116.32 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 116.32 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.54 | P12:500-230:EES:WILGLN:WATERF | External | 107.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.47 | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 121.07 | 0.4
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 114.91 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 114.91 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 2e-05 | 100.45 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 100.45 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.78 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.23 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.21 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.39 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 138.39 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.25 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.22 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 118.39 | P23:500:EES:BF335618-133 | External | 118.36 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.44 | P23:500:EES:BF335618-133 | External | 103.41 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.34 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 112.31 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.34 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.31 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.0001 | 112.54 | P23:500:EES:ABF_WG-E | External | 112.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00034 | 105.67 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 105.67 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 196.8 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 196.81 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 118.69 | P23:500:EES:ABF_WG-A | External | 118.72 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.74 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.51 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.48 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 102.76 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 102.74 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 120.96 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 120.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 111.11 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 111.13 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 119.4 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 119.4 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.7 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 107.67 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 102.76 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 102.74 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 118.39 | P23:500:EES:ABF_WG-E | External | 118.36 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 2e-05 | 129.92 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 129.92 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 110.15 | P12:230:EES:TEZCUC:IRONMN:1 | External | 110.14 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.86 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.85 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.22 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 118.19 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.3 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.37 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 112.33 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 106.91 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 106.89 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 112.37 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 112.33 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 127.74 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 127.77 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 9e-05 | 114.9 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 114.9 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.01 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.64 | 0.37
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.74 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00026 | 166.94 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 166.94 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.79 | P23:500:EES:ABF_WG-E | External | 107.76 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.98 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 103.97 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 107.7 | P12:500-230:EES:WILGLN:WATERF | External | 107.67 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 110.15 | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1: 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | External | 110.14 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.22 | P12:500-230:EES:WILGLN:WATERF | External | 118.19 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.47 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 103.88 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.3 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00011 | 148.12 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 148.14 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.3 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.27 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.01 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.64 | 0.37
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 107.71 | P23:500:EES:BF335618-133 | External | 107.68 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.48 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 118.45 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 112.4 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.41 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 119.4 | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1: 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | External | 119.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01171 | 125.39 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00139 | 121.46 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 122.7 | -1.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01254 | 114.21 | Base Case | External | 114.45 | -0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 203 | 203 | 0.00166 | 108.24 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0001 | 109.82 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 110.48 | -0.66
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 112 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 115.89 | -3.89
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 138.02 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.05 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00019 | 107.78 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.65 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0037 | 111.79 | Base Case | External | 111.44 | 0.35
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01008 | 107.09 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 106.98 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 106.85 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00064 | 107.91 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 112.36 | -4.45
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00733 | 102.11 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 102.4 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 115.13 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 118.45 | -3.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.00062 | 132.58 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00143 | 109.25 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00961 | 153.83 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00729 | 101.51 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 101.8 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 102.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.66 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 111.61 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 115.1 | -3.49
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00013 | 113.29 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 116.87 | -3.58
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 107.73 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.48 | -1.75
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 203 | 203 | 0.0022 | 100.89 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 173.59 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 177.8 | -4.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00053 | 110.06 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 109.66 | 0.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 151.23 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 152.42 | -1.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 104.97 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 104.19 | 0.78
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.45 | Base Case | External | 146.84 | -2.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 101.01 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 102.25 | -1.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0001 | 109.82 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 110.48 | -0.66
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 153.48 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 154.87 | -1.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00635 | 110.04 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 108.24 | 1.8
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01189 | 105.86 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 106.21 | -0.35
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997481 WEB AB 161 1 | 560 | 560 | 0.00205 | 100.53 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00036 | 109.2 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 110.71 | -1.51
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 112.08 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 114.52 | -2.44
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00143 | 109.25 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 106.16 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 105.53 | 0.63
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01008 | 107.06 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 103.57 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.54 | -0.97
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00789 | 116.71 | P23:345:MEC:GRIMES 901 | External | 116.93 | -0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 220.85 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 221.21 | -0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 104.03 | Base Case | External | 103.32 | 0.71
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300099 5MONTCT 161 300523 5WLMSBG 161 1 | 273 | 273 | 0.00705 | 101.35 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 220.85 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 221.21 | -0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01171 | 125.33 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 5e-05 | 106.85 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.84 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 997485 DGG9T1 161 1 | 560 | 700 | 0.00308 | 100.88 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03442 | 112.14 | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15189 | 101.82 | Base Case | Internal | 103.21 | -1.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 115.57 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 118.82 | -3.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 100.16 | Base Case | External | 100.12 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.08915 | 107.67 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 108.97 | -1.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 135.79 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 138.4 | -2.61
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337600 3REED% 115 337602 3DUMAS% 115 1 | 106 | 106 | 0.00018 | 107.16 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.35 | -0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00019 | 109.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.77 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.00062 | 132.58 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00729 | 101.51 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 101.8 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 103.57 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 104.54 | -0.97
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.19595 | 102.64 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 104.06 | -1.42
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 105.63 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 105.07 | 0.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00733 | 102.11 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 102.4 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300099 5MONTCT 161 300523 5WLMSBG 161 1 | 273 | 273 | 0.00705 | 101.35 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 108.52 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 109.13 | -0.61
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.00113 | 112.39 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 203 | 203 | 0.0022 | 100.89 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 211 | 211 | 0.00166 | 102 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 105.66 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 104.87 | 0.79
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 114.03 | P13:161-69:EES-EAI:HERGET:AT2 | External | 113.88 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 112.4 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 112.81 | -0.41
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00053 | 109.58 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 109.18 | 0.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 104.61 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 103.83 | 0.78
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997063 GLENHAM TR1 115 1 | 25 | 31 | 0.00031 | 103.54 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 103.54 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00094 | 108.31 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 108.68 | -0.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00104 | 112.5 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 110.66 | 1.84
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00093 | 106.82 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 107.08 | -0.26
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 156.29 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 160.05 | -3.76
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01171 | 106.29 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 106.46 | -0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00171 | 118.87 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00635 | 130.9 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 128.33 | 2.57
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01073 | 103.06 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 103.13 | -0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00064 | 101.65 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 101.86 | -0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 997485 DGG9T1 161 1 | 560 | 700 | 0.00308 | 103.12 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00036 | 115.1 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 118.8 | -3.7
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00139 | 121.46 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 122.7 | -1.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 152.4 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 153.39 | -0.99
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00143 | 109.25 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00013 | 113.29 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 116.87 | -3.58
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 335 | 335 | 0.00268 | 107.31 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.19595 | 100.78 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 101.96 | -1.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00106 | 102.47 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 101.07 | 1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 349 | 349 | 1e-05 | 100.68 | P23:345:MEC:BLACK HAWK 901 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00153 | 103.42 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00094 | 108.31 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 108.68 | -0.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 103.93 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 103.15 | 0.78
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00064 | 108.41 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 113.11 | -4.7
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 106.98 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 106.85 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 203 | 203 | 0.0022 | 100.89 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 107.89 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 109.45 | -1.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 173.59 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 177.8 | -4.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01213 | 120.12 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 203 | 203 | 0.00166 | 108.24 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 211 | 211 | 0.00166 | 102 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 152.42 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 153.62 | -1.2
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00031 | 115.93 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 114.53 | 1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 107.73 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.48 | -1.75
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00032 | 113.13 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External | 114.38 | -1.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 154.98 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 156.38 | -1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01073 | 123.16 | Base Case | External | 123.67 | -0.51
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18199 | 155.51 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 156.84 | -1.33
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 105.47 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 104.85 | 0.62
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01254 | 105.87 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 106.15 | -0.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 100.15 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 101.29 | -1.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00154 | 102.73 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 100.11 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.1 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 103.26 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 106.32 | -3.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01073 | 123.54 | Base Case | External | 123.62 | -0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.35 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 114.21 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 246 | 291 | 0.00144 | 115.5 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 140.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.69 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 211 | 211 | 0.00166 | 102 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00021 | 107.14 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 112.12 | -4.98
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00032 | 113.13 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External | 114.38 | -1.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 111.3 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.28 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15541 | 103.61 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 112 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 115.89 | -3.89
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 110.81 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 111.2 | -0.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01008 | 107.02 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00104 | 112.5 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 110.66 | 1.84
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 105.63 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 105.07 | 0.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.00113 | 112.39 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00064 | 101.65 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 101.86 | -0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00036 | 115.1 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 118.8 | -3.7
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15189 | 103.14 | Base Case | Internal | 104.78 | -1.64
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 107.89 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 109.45 | -1.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636204 DR NE 5 161 636210 WASHBRN5 161 1 | 272 | 272 | 0.00019 | 102.72 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 108.45 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 109.12 | -0.67
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01008 | 107.05 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03513 | 107.93 | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 110.81 | -2.88
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15541 | 105.7 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 106.98 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 106.85 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.0019 | 100.97 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 104.06 | -3.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00036 | 109.2 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 110.71 | -1.51
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.35 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 114.21 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 105.75 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.39 | -3.64
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.00062 | 132.58 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00961 | 153.83 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 335 | 335 | 0.00182 | 103.36 | P23:345:MEC:BLACK HAWK 901 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997621 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00061 | 120.46 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 118.22 | 2.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 6e-05 | 117.37 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 120.04 | -2.67
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 103.57 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.54 | -0.97
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 351 | 0.0309 | 141.18 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 108.45 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 109.12 | -0.67
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 114.03 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 113.88 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 113.54 | Base Case | External | 115.18 | -1.64
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 6e-05 | 117.37 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 120.04 | -2.67
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00041 | 110.6 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.62 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00106 | 102.47 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 101.07 | 1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 115.13 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 118.45 | -3.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 111.64 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.64 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 105.75 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 109.39 | -3.64
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01138 | 104.89 | P23:345:MEC:NORWALK 901 | External | 105.02 | -0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03513 | 107.93 | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 110.81 | -2.88
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 137.63 | P11:024:DPC:ALMA2:6 | External | 140.22 | -2.59
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.00113 | 112.39 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 127.17 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 128.14 | -0.97
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 126.9 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 128.58 | -1.68
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 5e-05 | 106.71 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.69 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.35 | P13:161-69:EES-EAI:HERGET:AT1 | External | 114.21 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00031 | 116.01 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 114.61 | 1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 114.03 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 113.88 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00085 | 107.79 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 109.19 | -1.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15345 | 102.14 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 102.96 | -0.82
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 101.01 | P11:024:DPC:ALMA2:6 | External | 102.25 | -1.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 220.85 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 221.21 | -0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01005 | 107.25 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 127.17 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 128.14 | -0.97
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 137.63 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 140.22 | -2.59
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 112.08 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 114.52 | -2.44
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00021 | 107.14 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 112.12 | -4.98
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00733 | 102.11 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 102.4 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 203 | 203 | 0.00166 | 108.24 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 112.4 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 112.81 | -0.41
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01005 | 107.29 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00064 | 108.41 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 113.11 | -4.7
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.10276 | 110.9 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 111.95 | -1.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15345 | 103.94 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 104.96 | -1.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00064 | 101.39 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 101.68 | -0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 105.75 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.39 | -3.64
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00217 | 115.96 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 119.85 | -3.89
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04972 | 104.34 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 105.68 | -1.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00171 | 118.25 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00018 | 128.06 | P23:500:EMI-EES:ABF_FRKLN-A | External | 128.07 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 107.73 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 109.48 | -1.75
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 335 | 335 | 0.00206 | 103.1 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 103.85 | -0.75
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04972 | 104.34 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 105.68 | -1.34
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 152.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 152.59 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 101.59 | P23:345:GRE:PVS 19JB4 | External | 101.59 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.23 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 127.23 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 109.18 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External | 109.16 | 0.02
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 102.84 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.71 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 116.71 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 139.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.14 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0002 | 110.43 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.43 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00026 | 114.19 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 114.19 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0002 | 105.62 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.62 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 149.56 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 149.55 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 108.42 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 108.41 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 127.47 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 127.46 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997614 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00054 | 127.25 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 127.25 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 113.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 113.88 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 127.47 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 127.46 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.55 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 117.55 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 234.57 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.56 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00396 | 100.6 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External | 100.57 | 0.03
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.23 | P13:161-69:EES-EAI:HERGET:AT2 | External | 127.23 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 149.56 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 149.55 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 6e-05 | 109.23 | Base Case | External | 109.23 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 109.3 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 109.29 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.55 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 117.55 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0002 | 112.58 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.58 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 117.89 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.89 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00058 | 111.61 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 111.61 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00048 | 113.22 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.29 | -0.07
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.59 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 127.6 | -0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 109.18 | 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22 1: 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 | External | 109.16 | 0.02
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 234.57 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.56 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00021 | 104.31 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 104.31 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00032 | 113.83 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 113.82 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 139.32 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 139.31 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 102.84 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.71 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 116.71 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 134.18 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 134.17 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.59 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 127.6 | -0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 102.05 | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1: 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | External | 102.05 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00058 | 112.08 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 112.07 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 657754 MAPLE R4 230 997110 MAPL RIV TR5 115 5 | 199.2 | 199.2 | 0.00026 | 100.68 | P13:115-13-230:XEL-XEL-OTP:AUTO-SINGLE:MAPLER7:MAPLERIV8:MAPLER4:6 | External | 100.68 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 103.02 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 103.01 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.23 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 127.23 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0029 | 103.3 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 103.27 | 0.03
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0013 | 103.88 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 103.87 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997053 GLENHAM TR1 115 1 | 25 | 31 | 0.00028 | 112.86 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.86 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 101.57 | P23:345:GRE:PVS 19JB1 | External | 101.57 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 102.84 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 108.42 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 108.41 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 113.15 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 113.14 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 657754 MAPLE R4 230 997110 MAPL RIV TR5 115 5 | 199.2 | 199.2 | 0.00026 | 100.68 | 657754 MAPLE R4 230 3WXFMR MAPL RIV TR6 6: 657754 MAPLE R4 230 997115 MAPL RIV TR6 115 6 603020 MAPLE R7 115 997115 MAPL RIV TR6 115 6 605713 MAPLERIV8 13.8 997115 MAPL RIV TR6 115 6 657754 MAPLE R4 230 997122 MAPL RIV TR6 115 6 603020 MAPLE R7 115 997122 MAPL RIV TR6 115 6 605713 MAPLERIV8 13.8 997122 MAPL RIV TR6 115 6 657754 MAPLE R4 230 997113 MAPL RIV TR6 115 6 603020 MAPLE R7 115 997113 MAPL RIV TR6 115 6 605713 MAPLERIV8 13.8 997113 MAPL RIV TR6 115 6 | External | 100.68 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 141.8 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.8 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 102.84 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.71 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 116.71 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00396 | 100.6 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External | 100.57 | 0.03
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 102.05 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1 | External | 102.05 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 102.84 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 102.84 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 102.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 132.7 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 132.77 | -0.07
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 109.3 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 109.29 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 3e-05 | 125.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 125.68 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 3e-05 | 125.86 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 125.85 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00032 | 113.91 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 113.89 | 0.02
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 108.71 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 108.71 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.0026 | 101.2 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 101.15 | 0.05
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00056 | 101 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 101 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 103.02 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 103.01 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.55 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 117.55 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.59 | P13:161-69:EES-EAI:HERGET:AT1 | External | 127.6 | -0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 100.47 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 100.47 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 234.57 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 234.56 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 117.28 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.28 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00022 | 103.98 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.97 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 103.88 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.88 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 5e-05 | 139.78 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.78 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.68 | 67791: 336426 3CLAB8! 115 336458 3MICH N! 115 1 336462 6MICHO% 230 500360 FRONTST6 230 1 336412 3PATER! 115 336442 3SFORS 115 1 336442 3SFORS 115 336444 3MICH S! 115 1 | External | 113.68 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | 336462 6MICHO% 230 500360 FRONTST6 230 1: 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 126.98 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 126.98 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 120.12 | P23:500:EES:BF335618-1~3 | External | 120.12 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 119.4 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 119.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00038 | 107.75 | P12:HV:EES::6FAIRVW!:6GYPSY%:1 | External | 107.75 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 144.4 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 113 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00015 | 128.64 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.64 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00058 | 100.99 | 500060 BVISTA 4 138 500065 BVISTA 6 230 1: 500060 BVISTA 4 138 500065 BVISTA 6 230 1 | External | 100.99 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | P12:500-230:EES:WILGLN:WATERF | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00022 | 101.06 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00073 | 103.91 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 103.9 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.06 | P23:500:EES:ABF_WG-E | External | 109.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 109.4 | P23:500:EES:ABF_WG-A | External | 109.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.14 | P23:500:EES:ABF_WG-A | External | 113.14 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.14 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.12 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.18 | 336137 6SLIDEL! 230 500360 FRONTST6 230 1: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 | External | 113.18 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 104.54 | 80254: 500050 BSALES 4 138 500820 TECHE 4 138 1 500460 JULTAP 4 138 500820 TECHE 4 138 1 500580 MORBHAN4 138 500820 TECHE 4 138 1 500660 PATOUT 4 138 500820 TECHE 4 138 1 501823 G3TECHE 24.0 500820 TECHE 4 138 1 501824 G4TECHE 13.8 500820 TECHE 4 138 1 | External | 104.53 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 104.77 | P12:138:CLEC::BSALES 4:TECHE 4:1 | External | 104.77 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 107.22 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 107.22 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00014 | 100.2 | 336065 6CONVNT! 230 336066 6FRISCO! 230 1: 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | External | 100.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 110.48 | P12:230:EES:PANAMA:DBAYOU:1 | External | 110.48 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.37 | P12:500-230:EES:WILGLN:WATERF | External | 108.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 119.4 | P12:230:EES:TEZCUC:WATERF:1 | External | 119.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 109.4 | P23:500:EES:ABF_WG-A | External | 109.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 109.4 | P23:500:EES:BF335618-1~3 | External | 109.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.8 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 119.8 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 113 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 103.83 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 103.83 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.18 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 114.18 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.13 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 113.1 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 118.94 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 118.95 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 0.00012 | 105.32 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 105.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.37 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 108.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00025 | 123.93 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 123.93 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 123.92 | P12:230:EES:IRONMN:L_GPSY:1 | External | 123.92 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.04 | P23:500:EES:BF335618-133 | External | 113.04 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 103.08 | P12:230:EES:RACELA:WATERF:1 | External | 103.08 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 117.67 | P12:230:EES:BELPNT:TEZCUC:L_GPSY:1 | External | 117.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.38 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 114.35 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 107.52 | P12:230:LAGN:FR_BRA_E:SLIDEL:LOGTOWNW:1 | External | 107.52 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | P12:230:EES-CLEC::6MICHO%:FRONTST6:1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 109.08 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.08 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.2 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 113.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 112.32 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 112.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 130.12 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 130.12 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 2e-05 | 133.49 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 133.49 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 116.92 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 116.92 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 121.19 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 121.18 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 116.13 | 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1: 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1 | External | 116.13 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 114.64 | P12:HV:EES::6TEZCUCO%:6IRONMAN%:1 | External | 114.64 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.74 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.71 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 109.4 | P23:500:EES:BF335618-1~3 | External | 109.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 107.2 | P12:HV:EES::6CONVNT!:6FRISCO!:1 | External | 107.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 107.67 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 107.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 150.1 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 150.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 114.25 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 110.48 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 110.48 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 115.77 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 115.76 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.94 | 80163: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.94 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.41 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 108.41 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00022 | 103.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 103.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.62 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.61 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 168.27 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 168.27 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 115.77 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 115.76 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 108.49 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 108.5 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 111.84 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 111.84 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 121.58 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 121.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0004 | 208.39 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 208.37 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 0.00012 | 106.56 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 106.55 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 107.22 | P12:230:EES:TEZCUC:WATERF:1 | External | 107.22 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.41 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | External | 102.4 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.21 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 109.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 125.66 | P23:500:EES:BF335618-1~3 | External | 125.66 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00055 | 108.95 | P12:230:EES:WATERF:VACHER:1 | External | 108.95 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 124.55 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 124.56 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.02 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 113.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 2e-05 | 105.79 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.78 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.88 | P12:230:EES:TEZCUC:WATERF:1 | External | 101.88 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 108.97 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.97 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.2 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 125.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | P12:500-230:EES:WILGLN:WATERF | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.2 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 125.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.37 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 108.77 | P23:500:EES:ABF_WG-A | External | 108.77 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.94 | 64573: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.94 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P12:230-21:EES:FCY:RVB | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 103.15 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 103.15 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 121.58 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 121.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.13 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.14 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00026 | 114.7 | P23:500:EES:BF335618-1~3 | External | 114.69 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 144.4 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | P12:HV:EES::6MICHO%:FRONTST6:1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.07 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 109.07 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 104.6 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 104.59 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00074 | 103.82 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 103.82 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 107.46 | 303223 6FR_BRANCH 230 336137 6SLIDEL! 230 1: 303223 6FR_BRANCH 230 336137 6SLIDEL! 230 1 | External | 107.46 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.21 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.25 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 125.25 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00017 | 105.33 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 105.32 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.06 | P23:500:EES:ABF_WG-E | External | 109.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.21 | P12:500-230:EES:WILGLN:WATERF | External | 125.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00013 | 127.08 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 127.08 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 107.67 | P12:230:EES:TEZCUC:WATERF:1 | External | 107.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 103.91 | P12:138:CLEC::BVISTA 4:ELPTAP 4:1 | External | 103.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.06 | P23:500:EES:BF335618-133 | External | 109.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.07 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 109.07 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0005 | 102.38 | P12:HV:EES::3BLPNT!:3LAPLAC:1 | External | 102.38 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 101 | P12:HV:EES::6LANDRY:6RACLND!:1 | External | 101 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 103.83 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 103.83 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.38 | P23:500:EES:ABF_WG-E | External | 108.37 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 114.64 | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1: 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | External | 114.64 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00054 | 113.58 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 113.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P11:21:EES:RVB:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 119.68 | P23:500:EES:BF335618-133 | External | 119.67 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00014 | 100.2 | P12:HV:EES::6CONVNT!:6FRISCO!:1 | External | 100.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 114.25 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 144.4 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 114.26 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 119.4 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 119.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 126.98 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 126.98 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.06 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 113.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00015 | 131.1 | P23:500:EES-EAI:WH_BLF:B7914 | External | 131.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.14 | P23:500:EES:BF335618-1~3 | External | 113.14 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.02 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 113.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 114.26 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 114.25 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 107.22 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 107.22 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 120.12 | P23:500:EES:ABF_WG-A | External | 120.12 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 144.4 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 120.51 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 120.51 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 114.29 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 114.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.02 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 113.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00021 | 117.29 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 117.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 114.3 | P23:500:EES:ABF_WG-E | External | 114.29 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 114.46 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 114.46 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 121.19 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 121.18 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 110.44 | P12:230:EES:STJAME:VACHER:1 | External | 110.44 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.03 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.65 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 119.65 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.14 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.12 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 144.4 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 106.78 | 303223 6FR_BRANCH 230 388425 6LOGTWN W6 230 1: 303223 6FR_BRANCH 230 388425 6LOGTWN W6 230 1 | External | 106.78 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 114.25 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 105.81 | P12:HV:EES::6ROMEVL!:6CONVNT!:1 | External | 105.81 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 120.51 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 120.51 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 114.26 | P12:500-230:EES:WILGLN:WATERF | External | 114.25 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 121.19 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 121.18 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 2e-05 | 104.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 104.43 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.02 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 113.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 108.97 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.97 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 144.4 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 144.4 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.53 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.53 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 100.35 | P12:230:EES:BELPNT:TEZCUC:L_GPSY:1 | External | 100.35 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 125.24 | P23:500:EES:BF335618-133 | External | 125.24 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.06 | P23:500:EES:BF335618-133 | External | 109.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.56 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 119.59 | -0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.62 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.61 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 119.68 | P23:500:EES:ABF_WG-E | External | 119.67 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 125.66 | P23:500:EES:ABF_WG-A | External | 125.66 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.34 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 108.33 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.21 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 109.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 108.49 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 108.5 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 126.98 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 126.98 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00021 | 117.29 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 117.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 123.92 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 123.92 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 125.25 | P23:500:EES:ABF_WG-E | External | 125.24 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 2e-05 | 133.3 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 133.3 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 114.64 | P12:230:EES:TEZCUC:IRONMN:1 | External | 114.64 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.46 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.45 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.21 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 125.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.88 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 101.88 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.03 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00026 | 114.7 | P23:500:EES:ABF_WG-A | External | 114.69 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.65 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 119.65 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 113.62 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 113.63 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.65 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 119.65 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 135.27 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 135.26 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00013 | 121.56 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 121.56 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P11:HV:EES::1RVR_BND_G1!:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.34 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 108.33 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.0004 | 176.42 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 176.41 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.04 | P23:500:EES:ABF_WG-E | External | 113.04 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.56 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 108.56 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 113.02 | P12:500-230:EES:WILGLN:WATERF | External | 113.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.06 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 108.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 110.07 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 110.06 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.88 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 101.88 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 106.05 | P13:230:115:EES:TRBONE:AT | External | 106.05 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00018 | 155.36 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 155.36 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 119.56 | P12:500-230:EES:WILGLN:WATERF | External | 119.59 | -0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.37 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 114.29 | P23:500:EES:BF335618-133 | External | 114.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.34 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.31 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 103.15 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 103.15 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.43 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 125.43 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.0002 | 117.49 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 117.49 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 123.92 | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1: 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | External | 123.92 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 125.21 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.21 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P23:345:MEC:MONTEZUMA 902 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 110.37 | P23:345:GRE:PVS 19JB4 | External | 110.37 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 3e-05 | 146.8 | P23:500:EES-EAI:WH_BLF:B7914 | External | 146.85 | -0.05
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00013 | 102.74 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 102.74 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00021 | 134.19 | P23:500:EES-EAI:WH_BLF:B7914 | External | 134.22 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00093 | 103.59 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 103.59 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.26 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 101.26 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00032 | 101.04 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 101.04 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.52 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.5 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.43 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 100.34 | 0.09
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 101 | 92386: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 100.98 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 100.77 | P23:345:MEC:MONTEZUMA 903 | External | 100.77 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 121.61 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 121.6 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00027 | 101.36 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.39 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.09 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.09 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.18 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998338 COLAUTO3 138 1 512705 COLLINS4 138 998346 COLAUTO3 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 | External | 100.16 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00153 | 102.04 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 102.02 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 171.13 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 171.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 101.03 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 101.93 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 101.92 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 108.88 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1 | External | 108.88 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 111.99 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 111.99 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 102.38 | Base Case | External | 102.37 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00046 | 122.43 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.42 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00592 | 102.38 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 102.37 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00046 | 122.43 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.42 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 235.32 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 235.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 111.07 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14 | External | 111.07 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00024 | 100.47 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 100.46 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.02 | 92398: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541163 DOGWDCT1 18.0 541225 PHILL 5 161 1 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 541164 DOGWDCT2 18.0 541225 PHILL 5 161 1 | External
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00027 | 109.24 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.27 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 171.13 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 171.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 105.04 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 105.03 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 118.13 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 118.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00027 | 110.52 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.56 | -0.04
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | 631115 OTTUMWA5 161 631118 LUCAS 5 161 1: 631115 OTTUMWA5 161 631118 LUCAS 5 161 1 | External | 102.99 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 103.87 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.87 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 106.37 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 106.36 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.8 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 100.79 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.82 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 100.8 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 235.32 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 235.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 161.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 161.66 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00088 | 110.26 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 110.26 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00032 | 110.23 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 110.21 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997053 GLENHAM TR1 115 1 | 25 | 31 | 0.00021 | 105 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 105 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00592 | 127.08 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 127.07 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.84 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 100.82 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.69 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 100.68 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 102.3 | 672540 QE 6 138 672541 CORY 6 138 1: 672540 QE 6 138 672541 CORY 6 138 1 | External | 102.3 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 101.97 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 101.97 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 110.81 | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1: 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | External | 110.81 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 106.34 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 106.34 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 100.68 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.68 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 106.34 | P12:161:AECI-INDN:ECKLES-5LEVASY:: | External | 106.33 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00081 | 100.49 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 100.49 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 108.88 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 108.88 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 105.04 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.03 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 344282 5CAPE GIR2 161 351006 5JOPPA SR 161 1 | 250 | 297 | 0.00039 | 101.47 | P23:345:AMIL::JOPPA:V5 | External | 101.47 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 103.68 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 103.68 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 103.68 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 103.68 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 100.22 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1: 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | External | 100.22 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 110.35 | P23:345:GRE:PVS 19JB1 | External | 110.35 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.52 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.5 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 109.65 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 109.64 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 103.87 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.87 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 101.27 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 101.26 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 108.22 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 108.21 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 103.87 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.87 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.0003 | 101.16 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 101.16 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00592 | 101.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 101.56 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00088 | 110.26 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 110.26 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00021 | 136.75 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.78 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0009 | 116.38 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 116.38 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 102.24 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 102.23 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 111.99 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 111.99 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.06 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 100.06 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.72 | 92409: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 100.7 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 100.9 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 100.9 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 118.13 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 118.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 101.93 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 101.92 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.06 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 100.06 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 235.32 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 235.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00059 | 113.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.53 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.17 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 100.16 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | P12:161:ALTW:AUTO-SINGLE:OTTUMWA5:LUCAS5:1 | External | 102.99 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 108.04 | P11:024:DPC:ALMA2:6 | External | 108.03 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 124.57 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.57 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00058 | 106.57 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 106.56 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0009 | 116.38 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.38 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 101 | 92463: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 100.98 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 124.74 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.74 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 111.08 | 106084: 656025 FRDRCKSB8 69.0 656039 LAWLERTP8 69.0 1 656039 LAWLERTP8 69.0 656061 PETERSON8 69.0 1 656039 LAWLERTP8 69.0 656041 LAWLR8 69.0 1 | External | 111.07 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 112.63 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 112.62 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 120.76 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 120.76 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00251 | 110.94 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 110.9 | 0.04
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 111.08 | P12:069:UMZ:# 5707 #: IN . PROPER N-1 (LINE) FOR 656025-656039-1 | External | 111.07 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.84 | 92461: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 | External | 100.82 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | P13:69-161:ALTW:AUTO-SINGLE:LUCAS8:LUCAS5:1 | External | 103 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 121.38 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 121.38 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 108.04 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 108.03 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00081 | 100.49 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 100.49 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 106.35 | 92154: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 106.35 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 106.35 | 104053: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 106.35 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 101.27 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 101.26 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 113.28 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 113.27 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 101.27 | P12:161:ITCM:AUTOSINGLE:LANSINGW:GENOA:1 | External | 101.26 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00032 | 110.3 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 110.29 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 113.28 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 113.27 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 103.27 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 103.26 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.37 | 93778: 659131 LARAMIE_-MB3 345 659135 STEGALL_-MB3 345 1 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 587874 G16-110-TAP 345 659131 LARAMIE_-MB3 345 1 | External | 110.35 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 101.64 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 101.24 | 0.4
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.7 | 104649: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.23 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.0002 | 101.4 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 101.4 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 103.08 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 103.09 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00015 | 110.19 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 110.19 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 102.69 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 102.67 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 119.02 | Base Case | External | 118.98 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.002 | 18414.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | External | 18414.8 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00056 | 109.55 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 109.49 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 239 | 239 | 0.00106 | 101.79 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 101.71 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01068 | 102.52 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 102.52 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.00054 | 18422.14 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 18422.19 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01049 | 100.37 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1 | External | 100.34 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.0021 | 18414.8 | 635200 RAUN 3 345 635214 NEAL 4G 24 1: 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | External | 18414.8 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.04 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | External | 107.64 | 0.4
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0002 | 105.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.45 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.53 | Base Case | External | 101.54 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.08466 | 18414.42 | 82335: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 18414.43 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 102.69 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 102.67 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.0003 | 110.14 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 110.08 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 102.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 102.63 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.05041 | 103.32 | 82356: 646258 S1258 5 161 646263 S1263 5 161 1 646258 S1258 5 161 646366 S1366 5 161 1 646258 S1258 5 161 645113 NBHST1 9 4.20 1 646258 S1258 5 161 645114 NBHST2 9 4.20 1 646258 S1258 5 161 645115 NBHST3 9 4.20 1 646258 S1258 5 161 645116 NBHST4 9 4.20 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103 | 0.32
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 7e-05 | 108.78 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.74 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661093 MERRCRT4 230 661982 MPT 34.5 KV 34.5 1 | 75 | 75 | 0.00033 | 100.4 | P23:345:XEL:8N22 SHC | External | 100.49 | -0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 111.27 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 110.81 | 0.46
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | External | 107.74 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 100.37 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 100.34 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661093 MERRCRT4 230 661982 MPT 34.5 KV 34.5 1 | 75 | 75 | 0.00016 | 100.53 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 100.44 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 110.44 | Base Case | External | 110.39 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00622 | 102.32 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 102.24 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 102.94 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | External | 103.01 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.3 | P23:345:XEL:8N22 SHC | External | 107.89 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00622 | 102.32 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 102.24 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00031 | 119.22 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 119.19 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00562 | 117.92 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 118.16 | -0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 102.29 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 102.29 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 3e-05 | 114.49 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.49 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 100.75 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 100.69 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 103.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 103.07 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 7e-05 | 108.78 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.74 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 102.98 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | External | 103.04 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 102.65 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 102.63 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0002 | 107.63 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.58 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15135 | 105.19 | Base Case | Internal | 104.15 | 1.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.37 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | External | 110.35 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 121.46 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 121.46 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00057 | 110.03 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 109.97 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.0003 | 111.27 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 111.26 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0042 | 103.11 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 103.04 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 100.11 | P11:345:OPPD:NEBCTY1G | External | 100.1 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 143.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.43 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00019 | 130.24 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.25 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.01958 | 18422.38 | 105024: 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 18422.51 | -0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01039 | 102.67 | P23:345:XEL:8N28 SHC | External | 102.66 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635431 J529J590COL1 34.5 1 | 1 | 1 | 0.00013 | 18414.42 | 82335: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 18414.43 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 100.24 | P11:345:OPPD:NEBCTY1G | External | 100.22 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 236.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 236.12 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 121.93 | Base Case | External | 121.92 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 102.02 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External | 101.95 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 103.27 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 103.26 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.96 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 131.65 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 137.19 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.12 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0025 | 106.37 | 635200 RAUN 3 345 635214 NEAL 4G 24 1: 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | External | 106.43 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 103.27 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 103.26 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00425 | 103.36 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.09 | 0.27
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01039 | 102.98 | P23:345:XEL:8N22 SHC | External | 103.06 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00041 | 118.58 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 118.53 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00131 | 101.33 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 101.34 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 100.41 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 100.37 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 111 | 105026: 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645022 N OMA 2G 13.8 645122 NO2 AUX9 2.40 1 646211 S1211 5 161 645022 N OMA 2G 13.8 1 645023 N OMA 3G 13.8 645123 NO3 AUX9 2.40 1 646211 S1211 5 161 645023 N OMA 3G 13.8 1 645021 N OMA 1G 13.8 645121 NO1 AUX9 2.40 1 647911 S911 8 69.0 645021 N OMA 1G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 110.56 | 0.44
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 102.93 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 102.85 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.3 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 107.89 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01039 | 103.01 | P23:345:XEL:8N22 SHC | External | 103.08 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 121.88 | Base Case | External | 121.88 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 103.08 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 103.09 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 131.99 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 131.87 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 3e-05 | 114.33 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.33 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 117.33 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.33 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 102.33 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 102.33 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01068 | 102.48 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 102.48 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997618 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00065 | 125.61 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 125.61 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 100.17 | P11:345:MEC-OPPD:NEBRASKA CITY 1 | External | 100.17 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00994 | 101.98 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External | 101.91 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.07 | 82335: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 107.89 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.3 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 107.89 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 102.93 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 102.85 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.37 | 105883: 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | External | 110.32 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 102.93 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 102.85 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00034 | 100.7 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 100.65 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 5e-05 | 108.04 | Base Case | External | 108.06 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00045 | 110.24 | 104853: 562711 G15_023_1 345 640510 HOLT.CO3 345 1 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | External | 110.21 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.47 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 106.43 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 131.99 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 131.87 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 117.95 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.93 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01039 | 102.63 | P23:345:XEL:8N28 SHC | External | 102.62 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 236.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 236.12 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.07 | 105018: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 107.89 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00031 | 119.22 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 119.19 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 100.03 | P11:345:MEC-OPPD:NEBRASKA CITY 1 | External | 100.03 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 139.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.74 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.88 | 105024: 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 110.55 | 0.33
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 236.08 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 236.12 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00028 | 113.33 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 113.12 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15135 | 107.05 | Base Case | Internal | 105.99 | 1.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.7 | 84408: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.23 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661093 MERRCRT4 230 661982 MPT 34.5 KV 34.5 1 | 75 | 75 | 7e-05 | 100.53 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 100.44 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00562 | 117.92 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 118.16 | -0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 100.7 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 100.65 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 103.07 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 103.07 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 110.09 | 105856: 648516 GRPR11 9 34.5 645065 GRPR11 W 0.69 1 648523 GRPR21 9 34.5 645067 GRPR21 W 0.69 1 648519 GRPR12 9 34.5 645066 GRPR12 W 0.69 1 648513 GRPR1 3 345 648520 GRPR2 3 345 1 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 648513 GRPR1 3 345 997246 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997245 GRPR1 TFMR 2 34.5 1 648526 GRPR22 9 34.5 645068 GRPR22 W 0.69 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z 652532 GR PRAIRIE 3 345 579457 G16-075XFMR1 34.5 1 648514 GRPR11X9 34.5 648516 GRPR11 9 34.5 Z1 648514 GRPR11X9 34.5 997246 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997246 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997244 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997245 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997244 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997243 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997243 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997253 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997252 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997253 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997253 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997251 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997252 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997251 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997250 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997250 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997244 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997243 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997244 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997244 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997242 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997243 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997242 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997241 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997241 GRPR2 TFMR 2 34.5 1 | External | 110.06 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337600 3REED% 115 337602 3DUMAS% 115 1 | 106 | 106 | 0.00018 | 103.87 | P23:500:EES-EAI:WH_BLF:B7914 | External | 103.84 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.0003 | 110.14 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 110.08 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 104.8 | Base Case | External | 104.74 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 105.75 | Base Case | External | 105.33 | 0.42
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 180.67 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 180.71 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.37 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 | External | 110.32 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0056 | 117.99 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External | 118.21 | -0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00131 | 104.25 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 104.14 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0002 | 100.69 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.64 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 100.41 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1 | External | 100.37 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 180.67 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 180.71 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 103.73 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.73 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00015 | 110.19 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 110.19 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00099 | 116.23 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 117.58 | -1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01326 | 123.33 | Base Case | External | 128.21 | -4.88
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 112.28 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 114.7 | -2.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00177 | 108.82 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 113.63 | -4.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 133.55 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.5 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01077 | 114.86 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 116.19 | -1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00046 | 116.48 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 115 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.0019 | 107.29 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00187 | 118.3 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 164.94 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 169.82 | -4.88
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 148.78 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 153.06 | -4.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 110.68 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 110.61 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00197 | 121.46 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 123.8 | -2.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00196 | 112.16 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01222 | 139.43 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00016 | 147.03 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00337 | 106.42 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 107.06 | -0.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00058 | 115.48 | P24:345:AMMO::LABADIE:15H | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 228.35 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 228.14 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.6 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.38 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.0006 | 102.46 | P23:345:ALTW:MITCHLCO:1160 | External | 106.52 | -4.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00131 | 117.41 | P23:345:MEC:BLACK HAWK 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 1 | 500 | 500 | 0.00041 | 107.86 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 108.41 | -0.55
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 120.19 | P23:345:MEC:LOUISA 954 | External | 123.92 | -3.73
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 112.3 | Base Case | External | 113.5 | -1.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00075 | 141.73 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 168.91 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 171.8 | -2.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 115.57 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00095 | 165.86 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 102.43 | P42:345:OKGE:SB_BOER7304 | Internal | 102.28 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 149.48 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.0019 | 110.42 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00199 | 116.98 | P23:345:XEL:8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00187 | 118.54 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00272 | 115.88 | P23:345:MEC:LOUISA 954 | External | 120.23 | -4.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00207 | 108.13 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 110.3 | -2.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.00323 | 122.78 | P23:345:MEC:SYCAMORE 905 | External | 125.11 | -2.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 1e-05 | 125.91 | P23:345:ITCM:HCKRYCK:FUT1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.0007 | 101.76 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.05 | -2.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0007 | 102.69 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 102.5 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00127 | 124.14 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 126.51 | -2.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00042 | 114.64 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532796 WICHITA7 345 997932 WICH TX-12 138 1 | 400 | 430 | 0.03018 | 113.39 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00038 | 131.78 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 132.23 | -0.45
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 119.93 | P23:345:ITCM:HCKRYCK:FUT1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00141 | 133.93 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00099 | 116.23 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 117.58 | -1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 1e-05 | 129.54 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 114.18 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 116.52 | -2.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00245 | 106.87 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0082 | 127.52 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 132.21 | -4.69
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00226 | 102.66 | P23:345:AMMO::ZACHARY:2 | External | 108.27 | -5.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00065 | 116.31 | 631083 TRAER 5 161 631086 DYSART 5 161 1: 631083 TRAER 5 161 631086 DYSART 5 161 1 | External | 117.56 | -1.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.74 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 101.65 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00033 | 133.59 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 132.75 | 0.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00184 | 107.13 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00031 | 101.76 | P23:345:ITCM:HCKRYCK:FUT1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00067 | 133.63 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 139.73 | -6.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.37 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 153.89 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 2e-05 | 147.86 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 148.67 | -0.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.6 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.38 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00283 | 115.03 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00032 | 115.95 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.0016 | 119.51 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 119.14 | 0.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00022 | 136.11 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.05 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00124 | 116.27 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 117.86 | -1.59
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07032 | 104.91 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0036 | 123.14 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00062 | 100.91 | P12:69:GRDA:PAWNEEGR-CLEVDSTK | External | 101.03 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636204 DR NE 5 161 636210 WASHBRN5 161 1 | 272 | 272 | 0.00021 | 116.99 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 102.54 | P23:345:MEC:LOUISA 954 | External | 105.84 | -3.3
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 997932 WICH TX-12 138 1 | 400 | 430 | 0.03018 | 112.79 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00033 | 116.54 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 118.66 | -2.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00043 | 103.37 | P23:345:XEL:8S51 HMP | External | 104.97 | -1.6
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620263 FORMN 7 115 997497 230/115 115 1 | 112 | 132 | 0.0006 | 102.03 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External | 100.99 | 1.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 102.71 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 105.37 | -2.66
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00161 | 116.98 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00019 | 110.51 | P23:345-161:XEL:ADAMS_I:680_S | External | 113.86 | -3.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.00221 | 102.87 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 105.29 | -2.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01229 | 127.34 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 129.85 | -2.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00322 | 100.81 | P12:500:EES:ND:8MT_OLIVE%:LAYFLD8:1 | External | 100.77 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 101.87 | Base Case | External | 105.97 | -4.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07023 | 102.77 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 103.28 | -0.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 109.5 | Base Case | External | 112.2 | -2.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00037 | 209.8 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 211.98 | -2.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0011 | 110.37 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 111.64 | -1.27
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 138.66 | Base Case | External | 140.71 | -2.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00099 | 103.47 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.75 | -4.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 107.79 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 107.79 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 111.31 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00197 | 121.46 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 123.8 | -2.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00203 | 104.87 | Base Case | External | 108.74 | -3.87
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00257 | 117.22 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 117.04 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 115.68 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 118.14 | -2.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 228.35 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 228.14 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 124.37 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 123.93 | 0.44
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 105.36 | Base Case | External | 106.3 | -0.94
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00231 | 131.38 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 133.29 | -1.91
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00031 | 110.89 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00084 | 104.32 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 137.18 | Base Case | External | 137.86 | -0.68
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 171.44 | P11:024:DPC:ALMA2:6 | External | 174.28 | -2.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00226 | 102.66 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 108.27 | -5.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 116.27 | 608676 HIBBARD7 115 608680 WNTR ST7 115 1: 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00012 | 101.79 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 102.89 | -1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 116.52 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 119.39 | -2.87
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00174 | 122.19 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997576 345-161 161 2 | 500 | 500 | 0.00041 | 108.85 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.41 | -0.56
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 106.28 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 106.28 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01186 | 140.38 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 106.54 | 105460: 525824 TUCO_TR1 1 13.2 998064 UPDATE LATER 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 525824 TUCO_TR1 1 13.2 998071 UPDATE LATER 230 1 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 | Internal | 106.67 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00097 | 111.93 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 111.64 | 0.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.0006 | 103.63 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0016 | 116.42 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 118.8 | -2.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 132.72 | Base Case | External | 136.34 | -3.62
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 112.43 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 114.36 | -1.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00034 | 101.7 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00031 | 111.42 | P23:345:ITCM:HCKRYCK:FUT1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00183 | 113.79 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.6 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.38 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.0019 | 110.41 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 184.39 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 185.86 | -1.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00033 | 140.68 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 149.92 | -9.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00045 | 121.03 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 119.3 | 1.73
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00199 | 145.28 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00051 | 102.77 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 111.11 | -8.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00016 | 136.71 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532796 WICHITA7 345 997932 WICH TX-12 138 1 | 400 | 430 | 0.03018 | 113.39 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 25 | 31 | 0.00021 | 111.35 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 111.32 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00064 | 152.86 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 157.33 | -4.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00206 | 112.31 | P23:345:XEL:8S25 WLM AS | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00133 | 108.23 | P23:345:AMIL::HERLEMAN:1 | External | 109.66 | -1.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00842 | 111.01 | P23:345:MEC:GRIMES 901 | External | 113.45 | -2.44
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.0029 | 115.39 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 118.86 | -3.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 104.42 | P11:345:MEC:GDMEC ST | External | 105.92 | -1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0015 | 127.41 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 134.49 | -7.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00194 | 140.28 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 111.83 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.82 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00299 | 100.79 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00024 | 101.34 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 102.15 | -0.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00023 | 147.7 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 106.28 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 106.28 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 118.94 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 120.87 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 123.65 | -2.78
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0053 | 115.36 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 114.54 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00124 | 116.27 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 117.86 | -1.59
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08909 | 130.22 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 131.66 | -1.44
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00177 | 108.82 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 113.63 | -4.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00186 | 106.34 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00036 | 181.73 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 184.12 | -2.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 1e-05 | 102.13 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 103.91 | -1.78
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 123.7 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 123.24 | 0.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 111.77 | Base Case | External | 117.19 | -5.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 227 | 227 | 0.002 | 101.3 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 102.62 | -1.32
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.74 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 101.65 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 121.73 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 121.27 | 0.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00111 | 112.51 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 113.83 | -1.32
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00235 | 100.55 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631098 MQOKETA5 161 631099 WYOMING5 161 1 | 167 | 167 | 0.00076 | 111.14 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00049 | 348.73 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 356.4 | -7.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 120.3 | Base Case | External | 123.51 | -3.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00903 | 123.3 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 128 | -4.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 257 | 257 | 0.0024 | 104.75 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 104.39 | 0.36
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 120.35 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 123.12 | -2.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00071 | 127.79 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 135.19 | -7.4
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 118.6 | P11:HV:EES::1WAT U3!:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | 197 | 197 | 0.00089 | 100.08 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997576 345-161 161 2 | 500 | 500 | 0.00041 | 111.03 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 111.92 | -0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00075 | 105 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 105.64 | -0.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00072 | 122.35 | P23:345:XEL:8S22 WLM | External | 127.04 | -4.69
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 134.93 | Base Case | External | 138.22 | -3.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.71 | P23:345:MEC:GDMEC 908 | External | 102.38 | -1.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00029 | 106.61 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.41 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.00193 | 103.96 | P23:345:MEC:SYCAMORE 905 | External | 106.53 | -2.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 102.69 | P23:345:MEC:LOUISA 964 | External | 105.94 | -3.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 111.55 | P23:345:MEC:LOUISA 954 | External | 115.13 | -3.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 73.1 | 73.1 | 0.20789 | 102.11 | 80545: 530686 RICE 6 230 530688 BUFLOCRK6 230 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 112.81 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 115.22 | -2.41
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00072 | 118.83 | P24:345:AMMO::LABADIE:15H | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00075 | 141.72 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 112.3 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 114.23 | -1.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07489 | 117.72 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 117.55 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00076 | 138.63 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00254 | 112.29 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00226 | 102.66 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 108.27 | -5.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00014 | 118.08 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 121.01 | -2.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00853 | 123.45 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 124.53 | -1.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 148.29 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 147.92 | 0.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.0007 | 101.76 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.05 | -2.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 112.3 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 114.23 | -1.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636210 WASHBRN5 161 636215 SHAULISRD5 161 1 | 261 | 261 | 0.00023 | 100.37 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00045 | 125.97 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 126.34 | -0.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 560 | 700 | 0.0033 | 104.59 | P23:345:MEC:SYCAMORE 905 | External | 106.28 | -1.69
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 164.94 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 169.82 | -4.88
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 102.43 | P43:345:SPS:TUCO:NR20_19L | Internal | 102.28 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 111.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00033 | 133.68 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 132.84 | 0.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 2e-05 | 101.11 | P12:HV:EES::6WILLOW_GL%:6PECUE:1 | External | 101.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 113.52 | P11:024:DPC:ALMA2:6 | External | 114.62 | -1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00152 | 103.02 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636200 BLACKHAWK 5 161 636202 MIDPORT5 161 1 | 272 | 272 | 6e-05 | 100.12 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 601055 SCOTTCO3 345 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00284 | 111.17 | P23:345:XEL:8M57 SCO | External | 110.58 | 0.59
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00162 | 120.23 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 119.73 | 0.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0006 | 133.8 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 141.04 | -7.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.002 | 114.44 | P23:345:XEL:SPS 8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01077 | 115.27 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 116.58 | -1.31
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00245 | 106.87 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00024 | 101.34 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 102.15 | -0.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 123.5 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 123.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 956 | 1152 | 0.00659 | 104.45 | P23:345:MEC:LOUISA 924 | External | 107.54 | -3.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00072 | 123.55 | P23:345:XEL:8S23 WLM | External | 126.95 | -3.4
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00033 | 116.63 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 118.58 | -1.95
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0006 | 133.8 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 141.04 | -7.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 108.16 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 107.54 | 0.62
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 111.37 | P23:345:XEL:SPS 8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 114.18 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 116.52 | -2.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00066 | 119.33 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 125 | -5.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15368 | 101.41 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 101.24 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | 327 | 327 | 0.00123 | 132.23 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00029 | 105.44 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.24 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 116.55 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 119.91 | -3.36
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 152.01 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 152.24 | -0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 104.92 | Base Case | External | 105.9 | -0.98
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00261 | 108.39 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00015 | 121.91 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 127.25 | -5.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00161 | 104 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.74 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 101.65 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00031 | 102.69 | P23:345:ITCM:HCKRYCK3 5267-5268-5269:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 102.43 | 105460: 525824 TUCO_TR1 1 13.2 998064 UPDATE LATER 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 525824 TUCO_TR1 1 13.2 998071 UPDATE LATER 230 1 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 | Internal | 102.28 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00032 | 106.48 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 122.89 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 122.44 | 0.45
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.0006 | 103.63 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1: 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0015 | 128.28 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00072 | 122.03 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.53 | -3.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00035 | 112.52 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 115.02 | -2.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00019 | 110.51 | P23:345-161:XEL:ADAMS_I:681_S | External | 113.86 | -3.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00196 | 115.76 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 135.26 | Base Case | External | 138.32 | -3.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00023 | 142.99 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00049 | 348.73 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 356.4 | -7.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00322 | 100.81 | P12:EHV:EES::8MT_OLIVE%:LAYFLD8%:1 | External | 100.77 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 101.52 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 102.1 | -0.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00074 | 106.01 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 104.4 | 1.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08909 | 130.22 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 131.66 | -1.44
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 100.09 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.29 | -0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01186 | 145.82 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 1e-05 | 102.13 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 103.91 | -1.78
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 102.71 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 105.37 | -2.66
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 115.29 | P11:25:EES:WATERF:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01229 | 133.32 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 137.66 | -4.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.0007 | 101.76 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 104.05 | -2.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 1e-05 | 134.03 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00056 | 104.14 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 106.5 | -2.36
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00322 | 100.81 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | External | 100.77 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 2e-05 | 101.11 | 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1: 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1 | External | 101.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00384 | 119.46 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00078 | 148.79 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 102.7 | Base Case | External | 102.95 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00073 | 132.59 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 139.53 | -6.94
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07489 | 117.72 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 117.55 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00045 | 125.97 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 126.34 | -0.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0016 | 156.36 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00031 | 110.89 | 601014 AS KING3 345 601028 EAU CL 3 345 1: 601014 AS KING3 345 601028 EAU CL 3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00384 | 119.46 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00084 | 104.34 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 112.63 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 114.83 | -2.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00075 | 156.94 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00165 | 120.61 | P23:345:MEC:BLACK HAWK 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00015 | 121.91 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 127.25 | -5.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00675 | 105.5 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 108 | -2.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 2e-05 | 136.88 | P23:345:MEC:BLACK HAWK 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0053 | 115.36 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 114.54 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00111 | 112.51 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 113.83 | -1.32
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00206 | 112.27 | P23:345:XEL:8S27 WLM AS | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 560 | 700 | 0.0033 | 107.01 | P23:345:MEC:SYCAMORE 905 | External | 108.92 | -1.91
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 122.52 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 122.06 | 0.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0122 | 123.12 | P24:345:AMMO::MCCREDIE:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.0006 | 102.01 | P23:345:ALTW:MITCHLCO:1150 | External | 106.07 | -4.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 184.39 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 185.86 | -1.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00045 | 121.16 | P23:345:AMMO::MONTGOMERY:V43 | External | 119.52 | 1.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 120.94 | P23:345:ITCM:HCKRYCK3 5267-5268-5269:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01229 | 127.14 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 130.52 | -3.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 106.54 | P43:345:SPS:TUCO:NR20_19L | Internal | 106.67 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.0019 | 107.29 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 123.57 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 123.12 | 0.45
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00031 | 100.89 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 100.94 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00043 | 103.34 | P23:345:XEL:8S51 HMP | External | 104.82 | -1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00103 | 118.09 | P23:345:MEC:OAK GROVE 901 | External | 122.98 | -4.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00035 | 112.52 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 115.02 | -2.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.0014 | 224.96 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 116.52 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 119.39 | -2.87
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 1 | 500 | 500 | 0.00041 | 107.86 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 108.41 | -0.55
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.00036 | 103.76 | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | External | 103.68 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00076 | 138.42 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00675 | 105.5 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 108 | -2.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 110.68 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 110.61 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00033 | 140.68 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 149.92 | -9.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.0006 | 103.63 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01077 | 114.86 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 116.19 | -1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00036 | 125.16 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 133.98 | -8.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0016 | 155.48 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 162.71 | -7.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 1 | 500 | 500 | 0.00041 | 110.05 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 110.93 | -0.88
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00296 | 128.73 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 133.08 | -4.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00119 | 105.6 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998347 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998346 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998355 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998354 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 105.99 | -0.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00202 | 107.63 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | 197 | 197 | 0.00089 | 100.01 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01222 | 147.63 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00231 | 131.38 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 133.29 | -1.91
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.0029 | 115.39 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 118.86 | -3.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 113.42 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 113.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 113.52 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 114.62 | -1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00036 | 181.73 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 184.12 | -2.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00045 | 121.16 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 119.43 | 1.73
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 2e-05 | 119.53 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 120.45 | -0.92
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00167 | 110.28 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 171.44 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 174.28 | -2.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00219 | 109.01 | P23:345:MEC:LOUISA 964 | External | 113.21 | -4.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00116 | 107.04 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.3 | -1.26
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00031 | 112.38 | P23:345:ITCM:HCKRYCK3 5267-5268-5269:IA-MVP | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00161 | 124.38 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 125.56 | -1.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 9e-05 | 144.18 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997576 345-161 161 2 | 500 | 500 | 0.00041 | 111.03 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 111.92 | -0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636202 MIDPORT5 161 636203 LUNDQST5 161 1 | 231 | 231 | 6e-05 | 110.77 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681543 ALMA 5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00031 | 110.89 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.00125 | 100.82 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 101.6 | -0.78
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 4e-05 | 137.23 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.06 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 116.52 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 119.39 | -2.87
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0007 | 102.69 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 102.5 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 124.75 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 100.09 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.29 | -0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00299 | 100.79 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00853 | 123.45 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 124.53 | -1.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00045 | 121.03 | P23:345:AMMO::MONTGOMERY:V43 | External | 119.39 | 1.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 115.91 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 118.38 | -2.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00067 | 133.63 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 139.73 | -6.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00097 | 118.26 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 117.97 | 0.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 142.7 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 144.27 | -1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 169.59 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 174.68 | -5.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00025 | 130.74 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.83 | -0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00178 | 126.96 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00608 | 103.81 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00046 | 116.48 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 115 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 142.7 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 144.27 | -1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00296 | 139.77 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00147 | 118.36 | Base Case | External | 122.68 | -4.32
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 136.21 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 143.72 | -7.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00014 | 118.08 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 121.01 | -2.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.00029 | 131.59 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01186 | 137.86 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00046 | 116.48 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 115 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01222 | 142.37 | P23:345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 117.17 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 120.49 | -3.32
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00299 | 100.62 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 100.82 | -0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00167 | 110.43 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00161 | 124.9 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 126.1 | -1.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00127 | 124.14 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 126.51 | -2.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.95 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 120.74 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 602023 LACROSS5 161 602025 MONROCO5 161 1 | 271.6 | 271.6 | 1e-05 | 102.13 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 103.91 | -1.78
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.95 | P13:161-69:EES-EAI:HERGET:AT1 | External | 120.74 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 120.35 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 123.12 | -2.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 997932 WICH TX-12 138 1 | 400 | 430 | 0.03018 | 112.79 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00116 | 107.04 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.3 | -1.26
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00381 | 107.26 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.3 | -5.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 228.35 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 228.14 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 106.06 | 608633 FAIRMPK7 115 608683 STIN-MN7 115 1: 608633 FAIRMPK7 115 608683 STIN-MN7 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0002 | 168.69 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 170.1 | -1.41
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 113.74 | Base Case | External | 121 | -7.26
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 2e-05 | 147.86 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 148.67 | -0.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00012 | 101.79 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 102.89 | -1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00226 | 105.37 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00074 | 106.47 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 106.28 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 1 | 500 | 500 | 0.00041 | 110.05 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 110.93 | -0.88
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00586 | 114.65 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 114.83 | -0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03318 | 106.54 | P42:345:OKGE:SB_BOER7304 | Internal | 106.67 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00296 | 140.01 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00221 | 118.01 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 120.5 | -2.49
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00072 | 122.03 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.53 | -3.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636215 SHAULISRD5 161 636220 EL FARM5 161 1 | 215 | 215 | 0.00023 | 132.72 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00125 | 116.87 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | 327 | 327 | 0.00139 | 117.32 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00174 | 122.22 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 118.3 | P23:345:XEL:SPS 8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 151.49 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 151.77 | -0.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 148.78 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 153.06 | -4.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997576 345-161 161 2 | 500 | 500 | 0.00041 | 108.85 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.41 | -0.56
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 103.4 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 106.01 | -2.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00172 | 108.84 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.00813 | 105.5 | P23:345:MEC:LOUISA 964 | External | 109.23 | -3.73
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01077 | 130.22 | Base Case | External | 132.06 | -1.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.95 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 120.74 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 112.29 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 113.47 | -1.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00141 | 132.95 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 140.09 | -7.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00476 | 101.87 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00067 | 118.16 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 123.65 | -5.49
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00183 | 113.76 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15187 | 101.66 | Base Case | Internal | 104.12 | -2.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00078 | 164.96 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00115 | 104.96 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.17 | -1.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 6e-05 | 102.81 | Base Case | External | 103.06 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00235 | 100.55 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 115.68 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 118.14 | -2.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 1e-05 | 109.31 | 608633 FAIRMPK7 115 608680 WNTR ST7 115 1: 608633 FAIRMPK7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 138.21 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 147.24 | -9.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00097 | 103.36 | P23:345:MEC:OAK GROVE 901 | External | 107.79 | -4.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00089 | 100.78 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.03074 | 128.9 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00276 | 110.77 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00194 | 140.25 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00071 | 157.07 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 165.7 | -8.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00244 | 105.58 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 116.55 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 119.91 | -3.36
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 127.99 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 128.02 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | 197 | 197 | 0.00089 | 100.84 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00103 | 134.81 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 110.68 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 110.61 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00023 | 147.7 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 148.59 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 148.16 | 0.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 131.13 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 132.97 | -1.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 314 | 314 | 0.00103 | 103.42 | P23:345:MEC:OAK GROVE 901 | External | 107.5 | -4.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00097 | 105.85 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 105.55 | 0.3
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00075 | 156.95 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00036 | 181.73 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 184.12 | -2.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636203 LUNDQST5 161 636204 DR NE 5 161 1 | 272 | 272 | 0.00021 | 127.42 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00123 | 110.86 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00177 | 108.82 | P23:345:AMMO::ZACHARY:2 | External | 113.63 | -4.81
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00067 | 133.63 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 139.73 | -6.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00065 | 116.31 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 117.56 | -1.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00023 | 150.63 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 101.52 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 102.1 | -0.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 4e-05 | 114.89 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 114.88 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603103 SCOTTCO7 115 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00284 | 113.91 | P23:345:XEL:8M57 SCO | External | 113.41 | 0.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00337 | 112.02 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 112.54 | -0.52
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00146 | 116.66 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 117.64 | -0.98
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00659 | 116.19 | P23:345:MEC:LOUISA 924 | External | 119.61 | -3.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 9e-05 | 151.62 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00012 | 165.68 | P23:500:EES-EAI:WH_BLF:B7914 | External | 165.68 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00032 | 117.12 | P23:500:EES-EAI:WH_BLF:B7914 | External | 117.12 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00032 | 112.12 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.12 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 140.38 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.38 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 111.11 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 111.11 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00032 | 114.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 114.29 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 110.66 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 110.66 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 130.68 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 130.67 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00032 | 112.71 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.71 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 130.68 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 130.67 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 127.4 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 127.39 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 127.4 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.39 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 121.39 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 121.39 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00023 | 143.06 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.06 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 2e-05 | 106.8 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.8 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 127.4 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.39 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 103.48 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External | 103.47 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 140.2 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.2 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00019 | 113.39 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.39 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00413 | 101.74 | 300043 7KINGDM 345 300044 7MCCRED 345 1: 300043 7KINGDM 345 300044 7MCCRED 345 1 | External | 101.71 | 0.03
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 108.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.37 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 608673 ARROWHD7 115 608688 COLBYVL7 115 1 | 126 | 126 | 0.00011 | 100.52 | 608673 ARROWHD7 115 608674 HANESRD7 115 1: 608673 ARROWHD7 115 608674 HANESRD7 115 1 | External | 100.53 | -0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 146.24 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 146.23 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 102.77 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 102.76 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 108 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 107.99 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 220.75 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 220.74 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 4e-05 | 103.81 | Base Case | External | 103.81 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 220.75 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 220.74 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997059 GLENHAM TR1 115 1 | 25 | 31 | 0.00028 | 105.01 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 105 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 146.24 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 146.23 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 106.92 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 106.92 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00019 | 115.51 | P23:500:EES-EAI:WH_BLF:B7914 | External | 115.51 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00028 | 110.56 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 110.56 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00056 | 111.09 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 111.08 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 220.75 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 220.74 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00031 | 108.95 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 108.93 | 0.02
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 136.17 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 136.17 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 127.76 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 127.76 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00056 | 111.55 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 111.55 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00423 | 106.74 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 106.71 | 0.03
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01498 | 100.07 | P24:345:AMMO::MCCREDIE:1 | External
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 102.77 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 102.76 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 107.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 107.29 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00017 | 142.88 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.88 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 101.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.5 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00043 | 142.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 142.44 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 111.4 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.4 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 106.92 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 106.92 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 111.06 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.06 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 6e-05 | 117.34 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 117.34 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 6e-05 | 117.5 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 117.5 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00031 | 109.02 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 109 | 0.02
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 103.48 | 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22 1: 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 | External | 103.47 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997617 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00052 | 120.8 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 120.79 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 106.6 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 106.59 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00043 | 121.49 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 121.48 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00023 | 100.4 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 100.4 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 100.73 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.73 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00413 | 101.76 | 300090 5KINGDM 161 300043 7KINGDM 345 1: 300090 5KINGDM 161 300043 7KINGDM 345 1 | External | 101.74 | 0.02
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | 21883: 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 104288: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09302 | NConv | P12:115:MIDW:RICE-LYONS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.1238 | NConv | P12:345:WERE:BENT-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 84582: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06129 | NConv | 104289: 532861 EMANHAT6 230 532865 NMANHT6 230 1 532865 NMANHT6 230 539639 ELMCREK6 230 1 532865 NMANHT6 230 997919 NMAN TX-1 115 1 532865 NMANHT6 230 997926 NMAN TX-1 115 1 532865 NMANHT6 230 997922 NMAN TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04887 | NConv | 81738: 514880 NORTWST7 345 514881 SPRNGCK7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514908 ARCADIA7 345 1 514880 NORTWST7 345 515497 MATHWSN7 345 1 514880 NORTWST7 345 998304 NORTWST2 138 1 514880 NORTWST7 345 998303 NORTWST3 138 1 514880 NORTWST7 345 998302 NORTWST4 138 1 514880 NORTWST7 345 998312 NORTWST2 138 1 514880 NORTWST7 345 998311 NORTWST3 138 1 514880 NORTWST7 345 998310 NORTWST4 138 1 514880 NORTWST7 345 998309 NORTWST2 138 1 514880 NORTWST7 345 998308 NORTWST3 138 1 514880 NORTWST7 345 998307 NORTWST4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06442 | NConv | P23:345:ITCGP:SV_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81385: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514929 PLVALLY4 138 514953 HOLLYWD4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 42750: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06129 | NConv | P12:230:WERE:NMAN-ELMC_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | P12:345:WERE:LATH-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08438 | NConv | P12:115:MKEC:SMITHCENTER-CONCORDIA(NORTH):: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104701: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.17245 | NConv | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 8622: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03914 | NConv | P42:345:OKGE:SB_CION7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 42991: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07763 | NConv | P42:345:OKGE:SB_REOW7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05426 | NConv | P23:345:WERE:SWIS_345-2:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03563 | NConv | 83836: 523093 HITCHLAND 3 115 523195 HANSFORD 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06442 | NConv | 38761: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.15184 | NConv | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04768 | NConv | P12:115:MKEC:BARBER-RIVERROAD:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P12:345:GRDA:T.NO.-CLEVLND | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P23:345:AEPW:TULSA NORTH CB 3413A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | P55:161-345:KCPL-GMO:STILWELL_BUS_11_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | P12:345:WERE:BENT-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104077: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | 84126: 509755 WEKIWA-7 345 509852 T.NO.--7 345 1 509852 T.NO.--7 345 510406 N.E.S.-7 345 1 509852 T.NO.--7 345 512694 CLEVLND7 345 1 509852 T.NO.--7 345 512865 GREC TAP5 345 1 509852 T.NO.--7 345 998407 TULSA N 2 138 1 509852 T.NO.--7 345 998415 TULSA N 2 138 1 509852 T.NO.--7 345 998412 TULSA N 2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | P42:345:OKGE:SB_CION7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104250: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08875 | NConv | P23:345:WERE:JEC_345-17:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P12:345:WERE:N345-PSO_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.17245 | NConv | P12:230:WERE:CIRC-MWE_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04849 | NConv | 852790: 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 560062 G15088_T 345 640277 MOORE 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03586 | NConv | P12:345:WERE:EMPR-MORR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03438 | NConv | 813780: 514707 PERRY 4 138 514802 SOONER 4 138 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | 105000: 515576 RANCHRD7 345 515621 OPENSKY7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04272 | NConv | P12:345:OKGE:BKRBKR336 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03563 | NConv | 105088: 523352 HERRING_TP 3 115 523377 RIVERVIEW 3 115 1 523304 MOORE_W 3 115 523366 RB-SNEED 3 115 1 523352 HERRING_TP 3 115 523366 RB-SNEED 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 523352 HERRING_TP 3 115 523359 HERRING 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03879 | NConv | P12:115:WERE:RENO-WMCP_115:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104978: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07781 | NConv | 7842: 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06048 | NConv | P12:345:OKGE:BKRBKR502 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03879 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | P42:345:OKGE:SB_RARD7393 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 42990: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.13589 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | P12:345:OKGE-ITC:BKRBKR503_1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03438 | NConv | 812230: 514880 NORTWST7 345 514881 SPRNGCK7 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84500: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P23:345:AEPW:DELAWARE CB 3401A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | P12:345:OKGE:BKBK442NEW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | P23:345:WERE:ROSE_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07228 | NConv | P23:345:WERE:WICH_345-116:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04281 | NConv | P12:345:OKGE:BKRBKR336_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | 84834: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.26547 | NConv | P12:115:MKEC:ELLSWORTHTAP-ELLSWORTH:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | P12:345:OKGE-ITC:BKRBKR502_1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81387: 514902 MCCLAIN4 138 514929 PLVALLY4 138 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | P23:345:WERE:HOYT_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03879 | NConv | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03087 | NConv | 8632: 533011 HALSTD 4 138 533013 MOUND 4 138 1 533013 MOUND 4 138 997895 MOUN TX-2 115 1 533013 MOUND 4 138 997851 MOUN TX-1 69.0 1 533013 MOUND 4 138 997902 MOUN TX-2 115 1 533013 MOUND 4 138 997858 MOUN TX-1 69.0 1 533013 MOUND 4 138 997898 MOUN TX-2 115 1 533013 MOUND 4 138 997854 MOUN TX-1 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06278 | NConv | P12:230:WERE:CIRC-GRTBND_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | P23:161-345:KCPL:STILWELL_R12-22::STILWELL-WGARD-STILT22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | 104811: 650247 40&BENNET 7 115 650276 76&ROKEBY 7 115 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P12:345:WERE:RENO-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08339 | NConv | P12:230:WERE:CIRC-EMCP_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04281 | NConv | 81730: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | 84377: 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03925 | NConv | 81377: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09302 | NConv | 7856: 533416 RENO 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06278 | NConv | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 8612: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04275 | NConv | P12:345:OKGE:BKBK443NEW2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | P42:345:OKGE:SB_RARD7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 82850: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | P12:345:WERE:N345-AECI_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 105014: 514902 MCCLAIN4 138 515481 STHLAKE4 138 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | P42:345:OKGE:SB_SOER7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 82851: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:RENO_345-150:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84501: 543044 MOONLT 5 161 543132 BNSF 5 161 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04272 | NConv | P42:345:OKGE:SB_WWHV7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.26547 | NConv | P12:115:MKEC:ELLSWORTH-BUSHTON:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05426 | NConv | P23:345:WERE:SWIS_345-1:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0827 | NConv | 8656: 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533415 DAVIS 3 115 533416 RENO 3 115 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09302 | NConv | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04849 | NConv | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 640277 MOORE 3 345 997373 MOORE T1 115 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | 104889: 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | 92511: 650247 40&BENNET 7 115 650276 76&ROKEBY 7 115 1 650576 761TERTIARY 7.20 997198 T761 12.5 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 650274 91&HWY2 7 115 650276 76&ROKEBY 7 115 1 650276 76&ROKEBY 7 115 997198 T761 12.5 1 650376 76&ROKEBY 9 12.5 997198 T761 12.5 1 650576 761TERTIARY 7.20 997205 T761 12.5 1 650276 76&ROKEBY 7 115 997205 T761 12.5 1 650376 76&ROKEBY 9 12.5 997205 T761 12.5 1 650576 761TERTIARY 7.20 997196 T761 12.5 1 650276 76&ROKEBY 7 115 997196 T761 12.5 1 650376 76&ROKEBY 9 12.5 997196 T761 12.5 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 105015: 514895 SARA 4 138 515481 STHLAKE4 138 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07228 | NConv | 47130010: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81386: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514946 MIDWEST4 138 514953 HOLLYWD4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03563 | NConv | 83937: 523309 MOORE_CNTY 6 230 523959 POTTER_CO 6 230 1 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1 523959 POTTER_CO 6 230 998120 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998120 WAUK 90343-A 230 1 523959 POTTER_CO 6 230 998126 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998126 WAUK 90343-A 230 1 523323 MCDOWELL 6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998123 WAUK 90343-A 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | P12:345:WERE:CANR-LATH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | P42:345:NPPD:BKR-MOR-3306 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P42:345:GRDA:CLEVLND CB13280 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104160: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | P12:345:WERE:WAVS-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 84583: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08339 | NConv | 104291: 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 997917 EMCP TX-1 115 1 532872 EMCPHER6 230 997924 EMCP TX-1 115 1 532872 EMCPHER6 230 997920 EMCP TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08493 | NConv | P12:345:OKGE-WERE:BKRBKR422 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | P23:345:WERE:ROSE_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03177 | NConv | 81731: 514880 NORTWST7 345 514908 ARCADIA7 345 1 514908 ARCADIA7 345 514909 REDBUD 7 345 1 514908 ARCADIA7 345 514909 REDBUD 7 345 2 514908 ARCADIA7 345 514909 REDBUD 7 345 3 514908 ARCADIA7 345 515045 SEMINOL7 345 1 514908 ARCADIA7 345 587804 G16-119-TAP 345 1 514908 ARCADIA7 345 998295 ARCADIA2 138 1 514908 ARCADIA7 345 998294 ARCADIA3 138 1 514908 ARCADIA7 345 998293 ARCADIA4 138 1 514908 ARCADIA7 345 587804 G16-100-TAP 345 1 514908 ARCADIA7 345 998303 ARCADIA2 138 1 514908 ARCADIA7 345 998302 ARCADIA3 138 1 514908 ARCADIA7 345 998301 ARCADIA4 138 1 514908 ARCADIA7 345 998300 ARCADIA2 138 1 514908 ARCADIA7 345 998299 ARCADIA3 138 1 514908 ARCADIA7 345 998298 ARCADIA4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03586 | NConv | 7821: 533305 MORRIS 3 115 533309 WEMPORI3 115 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06048 | NConv | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03879 | NConv | 7829: 533416 RENO 3 115 533438 WMCPHER3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04278 | NConv | P12:345:OKGE:BKBK443NEW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | P12:345:OKGE:BKBK442NEW2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04887 | NConv | P12:345:OKGE:BKBK443NEW3 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07763 | NConv | P12:345:OKGE:BKRBKR421 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03586 | NConv | P23:345:WERE:MORR_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104159: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104979: 515852 DGRASSE7 345 539801 THISTLE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04849 | NConv | 852750: 560062 G15088_T 345 640277 MOORE 3 345 1 640278 SHELDON7 115 997366 MOORE T1 115 1 640277 MOORE 3 345 997366 MOORE T1 115 1 640280 MOORE 9 13.8 997366 MOORE T1 115 1 640278 SHELDON7 115 997373 MOORE T1 115 1 640277 MOORE 3 345 997373 MOORE T1 115 1 640280 MOORE 9 13.8 997373 MOORE T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P12:345:WERE:N345-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81372: 514895 SARA 4 138 514898 CIMARON4 138 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | P42:345:OKGE:SB_WONG7315 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | 106389: 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | 21881: 514715 WOODRNG7 345 560084 G16-061-TAP 345 1 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P42:345:NPPD:BKR-SW-3306 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 1044511: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03925 | NConv | 104895: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | P12:345:WERE:WAVS-WOLF_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.17245 | NConv | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07763 | NConv | P12:345:OKGE:BKRBKR400 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07763 | NConv | P42:345:OKGE:SB_WONG7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104221: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104225: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | P12:345:OKGE:BKRBKR357_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | 21880: 514715 WOODRNG7 345 560084 G16-061-TAP 345 1 515497 MATHWSN7 345 515875 REDNGTN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 1044561: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03914 | NConv | P12:345:OKGE:BKBK441NEW2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | 84128: 510380 DELWARE7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 998406 DELAWARE 138 1 510380 DELWARE7 345 998414 DELAWARE 138 1 510380 DELWARE7 345 998411 DELAWARE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P42:345:NPPD:BKR-SW-3308 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104226: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | 8585: 532765 HOYT 7 345 532772 STRANGR7 345 1 533211 ARNOLD 3 115 533268 STRANGR3 115 1 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.17245 | NConv | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.26547 | NConv | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P23:345:AEPW:DELAWARE CB 3405A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P23:345:WERE:N345_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | 103794: 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P12:345:AEPW-WERE:DELWARE7:NEOSHO7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | 104219: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04842 | NConv | P13:138-115:MKEC:BARBER_XFR:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03869 | NConv | 8654: 533380 SPRGCRK3 115 533429 MOUNDRG3 115 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533429 MOUNDRG3 115 997895 MOUN TX-2 115 1 533429 MOUNDRG3 115 997902 MOUN TX-2 115 1 533429 MOUNDRG3 115 997898 MOUN TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | P23:161-345:KCPL:STILWELL_R11-12::STILWELL-WGARD-STILT11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P23:345:WERE:N345_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07228 | NConv | 47130011: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P23:345:GRDA:CLEVLND CB13280 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104222: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | P12:345:PWT:THIS-DGRS_345_2::FUTURE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04278 | NConv | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | P12:345:OKGE:BKRBKR150 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81388: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514933 DRAPER 4 138 514946 MIDWEST4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P43:345:GRDA:CLEVLND CB10180 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03879 | NConv | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03925 | NConv | P42:345:OKGE:SB_CION7381 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03282 | NConv | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P23:345:GRDA:CLEVLND CB10180 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | 104257: 532765 HOYT 7 345 532766 JEC N 7 345 1 532765 HOYT 7 345 532772 STRANGR7 345 1 532765 HOYT 7 345 997954 HOYT TX-1 115 1 532765 HOYT 7 345 997960 HOYT TX-1 115 1 532765 HOYT 7 345 997956 HOYT TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84504: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08875 | NConv | P12:345:WERE:HOYT-JEC_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07781 | NConv | P12:115:WERE:CIRC-RENO_115_1:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08493 | NConv | P12:345:WERE:VIOL-OGE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 77951: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | P12:345:WERE:SWIS-WGAR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:RENO_345-160:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07763 | NConv | P42:345:OKGE:SB_WONG7313 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104161: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0827 | NConv | 104477: 533415 DAVIS 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | 81733: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514934 DRAPER 7 345 515045 SEMINOL7 345 1 514934 DRAPER 7 345 515045 SEMINOL7 345 2 514934 DRAPER 7 345 515045 SEMINOL7 345 3 514934 DRAPER 7 345 998290 DRAPER2 138 1 514934 DRAPER 7 345 998289 DRAPER3 138 1 514934 DRAPER 7 345 998288 DRAPER4 138 1 514934 DRAPER 7 345 998298 DRAPER2 138 1 514934 DRAPER 7 345 998297 DRAPER3 138 1 514934 DRAPER 7 345 998296 DRAPER4 138 1 514934 DRAPER 7 345 998295 DRAPER2 138 1 514934 DRAPER 7 345 998294 DRAPER3 138 1 514934 DRAPER 7 345 998293 DRAPER4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0827 | NConv | P12:115:WERE:CIRC-RENO_115_2:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104266: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.13589 | NConv | P13:345-230:MKEC:SPEARVILLE_XFR2:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06129 | NConv | P12:230:MKEC:ELMCREEK-NORTHMANHATTAN:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04842 | NConv | P12:138:MKEC:BARBER-FLATRIDGE:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.13589 | NConv | P23:345:SUNC:SV_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | P12:230:WERE:SUMM-UNIO_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03925 | NConv | P12:345:OKGE:BKBK441NEW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06048 | NConv | P12:345:OKGE:BKRBKR503 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | 92068: 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06905 | NConv | P12:115:MKEC:PRICHARD-SEMCRUDE:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.26547 | NConv | P12:115:MIDW-MKEC:ELLSWORTH-BUSHTON:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104703: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08493 | NConv | P42:345:OKGE:SB_REOW7389 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04122 | NConv | P42:345:OKGE:SB_DRER7384 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03586 | NConv | 104262: 532766 JEC N 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532770 MORRIS 7 345 997949 MORR TX-1 230 1 532770 MORRIS 7 345 997955 MORR TX-1 230 1 532770 MORRIS 7 345 997951 MORR TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | 104218: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | P42:345:OKGE:SB_WONG7385 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | P12:230:WERE:MORR-UNIO_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | P23:345:WERE:N345_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 84584: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84499: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | P12:345:PWT:THIS-DGRS_345_1::FUTURE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04173 | NConv | 21882: 514803 SOONER 7 345 560084 G16-061-TAP 345 1 515497 MATHWSN7 345 515875 REDNGTN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04768 | NConv | P12:115:MKEC:RIVERROAD-SAINTJOHN:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | P23:345:WERE:SWIS_345-5:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06583 | NConv | P12:345:OKGE:BKRBKR357_1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03596 | NConv | 104810: 650274 91&HWY2 7 115 650276 76&ROKEBY 7 115 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | P23:345:WERE:WOLF_345-120:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04887 | NConv | P42:345:OKGE:SB_NOST7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06048 | NConv | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 42751: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07228 | NConv | P12:345:WERE:VIOL-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | P23:345:WERE:BENT_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04849 | NConv | 854540: 560062 G15088_T 345 640277 MOORE 3 345 1 640215 HASTING7 115 640313 PAULINE7 115 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.0332 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03438 | NConv | 906800: 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09302 | NConv | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03698 | NConv | 81776: 509852 T.NO.--7 345 512694 CLEVLND7 345 1 512694 CLEVLND7 345 560056 G15066_T 345 1 512694 CLEVLND7 345 998333 CLVAUTO1 138 1 512694 CLEVLND7 345 998341 CLVAUTO1 138 1 512694 CLEVLND7 345 998338 CLVAUTO1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | 7801: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532991 WEAVER 4 138 533062 ROSEHIL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09302 | NConv | P12:115:MIDW:LYONS-WHEATLANDS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06442 | NConv | 38760: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06048 | NConv | 104976: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | P55:161-345:KCPL:STILWELL_BUS_22_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | P12:345:WERE:HOYT-STRA_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03869 | NConv | 104371: 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05426 | NConv | P12:345:WERE:EMPR-SWIS_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | 104702: 542966 WGARDNR5 161 543132 BNSF 5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.26547 | NConv | P12:115:MIDW:BUSHTON-RICE COUNTY | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.17245 | NConv | P12:230:MIDW-WERE:RICE6-CIRCLE6 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03143 | NConv | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 104251: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.09807 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06442 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.1238 | NConv | P23:345:WERE:BENT_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04281 | NConv | P42:345:OKGE:SB_WWHV7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08515 | NConv | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | P23:345:WERE:STRA_345-95:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04253 | NConv | 84346: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04887 | NConv | 81721: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514880 NORTWST7 345 514881 SPRNGCK7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.07156 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.04848 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.04711 | NConv | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 640277 MOORE 3 345 997373 MOORE T1 115 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.03549 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.06374 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.04848 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.04869 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.04869 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06403 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06052 | NConv | 104288: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | P12:345:WERE:BENT-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84582: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:161-345:KCPL:STILWELL_R11-12::STILWELL-WGARD-STILT11 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 42750: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P12:345:WERE:LATH-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104701: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06052 | NConv | 8622: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 42991: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 83836: 523093 HITCHLAND 3 115 523195 HANSFORD 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38761: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.15135 | NConv | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05006 | NConv | 20632: 640065 AXTELL 3 345 640312 PAULINE3 345 1 560062 G15088_T 345 640277 MOORE 3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.74281 | NConv | P12:115:MKEC:ELLSWORTHTAP-SMITHCENTER:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 84377: 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P55:161-345:KCPL-GMO:STILWELL_BUS_11_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04171 | NConv | P42:345:OKGE:SB_TAGA7381 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104225: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:PWT:THIS-DGRS_345_1::FUTURE | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P12:345:WERE:BENT-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | 81742: 514715 WOODRNG7 345 515476 HUNTERS7 345 1 514715 WOODRNG7 345 515875 REDNGTN7 345 1 514715 WOODRNG7 345 560084 G16-061-TAP 345 1 514715 WOODRNG7 345 587460 G16-028_128 345 1 514715 WOODRNG7 345 998321 WOODRNG2 138 1 514715 WOODRNG7 345 998329 WOODRNG2 138 1 514715 WOODRNG7 345 998326 WOODRNG2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104077: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | P42:345:SPS:POTTERCO:2R05_19L | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044561: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104250: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | P23:345:WERE:JEC_345-17:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P12:345:WERE:N345-PSO_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | 105000: 515576 RANCHRD7 345 515621 OPENSKY7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04165 | NConv | P12:345:OKGE:BKRBKR336 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 105088: 523352 HERRING_TP 3 115 523377 RIVERVIEW 3 115 1 523304 MOORE_W 3 115 523366 RB-SNEED 3 115 1 523352 HERRING_TP 3 115 523366 RB-SNEED 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 523352 HERRING_TP 3 115 523359 HERRING 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104978: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 830510: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7393 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 42990: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.13556 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 82850: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84500: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P23:345:AEPW:DELAWARE CB 3401A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P23:345:WERE:ROSE_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | P23:345:WERE:WICH_345-116:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P12:345:OKGE:BKRBKR336_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 84834: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P42:345:OKGE:SB_TAGA7386 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P12:345:OKGE:BKRBKR357_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P12:345:AEPW:DELWARE7:N.E.S.-7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | 47130011: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P23:345:WERE:EMPR_345-330:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06249 | NConv | P12:230:WERE:CIRC-GRTBND_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7311 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:WERE:WOLF_345-120:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_REOW7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P12:345:WERE:RENO-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044511: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P12:345:OKGE:BKRBKR421 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_HURS7309 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104979: 515852 DGRASSE7 345 539801 THISTLE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 81730: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.14926 | NConv | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_REOW7312 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 8612: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04168 | NConv | P12:345:OKGE:BKBK443NEW2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P42:345:SPS:FINNEY_OR70_19L | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | P12:345:WERE:N345-AECI_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:161-345:KCPL:STILWELL_R12-22::STILWELL-WGARD-STILT22 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_SOER7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 82851: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | 104258: 532765 HOYT 7 345 532766 JEC N 7 345 1 532766 JEC N 7 345 532767 GEARY 7 345 1 532766 JEC N 7 345 532770 MORRIS 7 345 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 997953 JEC TX-13 230 1 532766 JEC N 7 345 997952 JEC TX-26 230 1 532766 JEC N 7 345 997959 JEC TX-13 230 1 532766 JEC N 7 345 997958 JEC TX-26 230 1 532766 JEC N 7 345 997955 JEC TX-13 230 1 532766 JEC N 7 345 997954 JEC TX-26 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84501: 543044 MOONLT 5 161 543132 BNSF 5 161 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04165 | NConv | P42:345:OKGE:SB_WWHV7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:NES CB 3441A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:WERE:WAVS_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P12:345:WERE:WAVS-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08356 | NConv | 104291: 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 997917 EMCP TX-1 115 1 532872 EMCPHER6 230 997924 EMCP TX-1 115 1 532872 EMCPHER6 230 997920 EMCP TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | P23:345:WERE:JEC_345-16:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03062 | NConv | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P12:345:WERE:WAVS-WOLF_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | 47130010: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 83937: 523309 MOORE_CNTY 6 230 523959 POTTER_CO 6 230 1 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1 523959 POTTER_CO 6 230 998120 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998120 WAUK 90343-A 230 1 523959 POTTER_CO 6 230 998126 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998126 WAUK 90343-A 230 1 523323 MCDOWELL 6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998123 WAUK 90343-A 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P12:345:WERE:CANR-LATH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.14926 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P12:345:AEPW-WERE:DELWARE7:NEOSHO7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104160: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:NES CB 3445A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_HURS7319 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.13556 | NConv | P23:345:SUNC:SV_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:DELAWARE CB 3409A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:HOYT_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P12:345:OKGE-WERE:BKRBKR422 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104187: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 532802 WAVERTX7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:ROSE_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | 7821: 533305 MORRIS 3 115 533309 WEMPORI3 115 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 8656: 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533415 DAVIS 3 115 533416 RENO 3 115 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04171 | NConv | P12:345:OKGE:BKBK443NEW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7313 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P12:345:WERE:N345-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06897 | NConv | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104268: 532780 CANEYRV7 345 532781 CANEYWF7 345 1 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P12:345:OKGE:BKRBKR400 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_WONG7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:LATH_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03741 | NConv | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998300 CIMARON1 138 1 514901 CIMARON7 345 998299 CIMARON2 138 1 514901 CIMARON7 345 998308 CIMARON1 138 1 514901 CIMARON7 345 998307 CIMARON2 138 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05006 | NConv | 852690: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 560062 G15088_T 345 640277 MOORE 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104221: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 105457: 523126 NBLWND-CB3 1 34.5 523123 NBLWND-WTG31 0.69 1 523126 NBLWND-CB3 1 34.5 523129 NBLWND-LV3 1 34.5 1 523131 NBLWND-HV3 3 115 523129 NBLWND-LV3 1 34.5 1 523103 NOBLE_WND 3 115 523131 NBLWND-HV3 3 115 1 523103 NOBLE_WND 3 115 523130 NBLWND-HV2 3 115 1 523130 NBLWND-HV2 3 115 523127 NBLWND-LV1 1 34.5 1 523124 NBLWND-CB1 1 34.5 523127 NBLWND-LV1 1 34.5 1 523124 NBLWND-CB1 1 34.5 523121 NBLWND-WTG11 0.69 1 523102 NOBLE_TR 1 13.8 998149 PRO G2218-01 115 1 523103 NOBLE_WND 3 115 998149 PRO G2218-01 115 1 523103 NOBLE_WND 3 115 523128 NBLWND-LV2 1 34.5 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 523102 NOBLE_TR 1 13.8 998155 PRO G2218-01 115 1 523103 NOBLE_WND 3 115 998155 PRO G2218-01 115 1 523102 NOBLE_TR 1 13.8 998153 PRO G2218-01 115 1 523103 NOBLE_WND 3 115 998153 PRO G2218-01 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | 84128: 510380 DELWARE7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 998406 DELAWARE 138 1 510380 DELWARE7 345 998414 DELAWARE 138 1 510380 DELWARE7 345 998411 DELAWARE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104226: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 8585: 532765 HOYT 7 345 532772 STRANGR7 345 1 533211 ARNOLD 3 115 533268 STRANGR3 115 1 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_HURS7389 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P42:345:OKGE:SB_REOW7319 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:DELAWARE CB 3405A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:WERE:N345_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104219: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06052 | NConv | 104293: 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532874 UNIONRG6 230 532875 DVISTA 6 230 1 532874 UNIONRG6 230 997914 UNIO TX-1 115 1 532874 UNIONRG6 230 997921 UNIO TX-1 115 1 532874 UNIONRG6 230 997917 UNIO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:WERE:SWIS_345-5:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P23:345:WERE:N345_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104222: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:PWT:THIS-DGRS_345_2::FUTURE | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04171 | NConv | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | P23:345:WERE:EMPR_345-210:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P12:345:WERE:HOYT-STRA_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | P23:345:ITCGP:SV_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:OKGE-ITC:BKRBKR502_1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 104257: 532765 HOYT 7 345 532766 JEC N 7 345 1 532765 HOYT 7 345 532772 STRANGR7 345 1 532765 HOYT 7 345 997954 HOYT TX-1 115 1 532765 HOYT 7 345 997960 HOYT TX-1 115 1 532765 HOYT 7 345 997956 HOYT TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84504: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | P12:345:WERE:HOYT-JEC_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P12:345:WERE:VIOL-OGE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 77951: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:RENO_345-160:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_WONG7313 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104161: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84583: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82900: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104266: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | 84129: 509807 ONETA--7 345 510406 N.E.S.-7 345 1 509852 T.NO.--7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 510406 N.E.S.-7 345 1 511840 NES3-1 22.0 510406 N.E.S.-7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04779 | NConv | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:CANR_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104703: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P42:345:OKGE:SB_REOW7389 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | 104262: 532766 JEC N 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532770 MORRIS 7 345 997949 MORR TX-1 230 1 532770 MORRIS 7 345 997955 MORR TX-1 230 1 532770 MORRIS 7 345 997951 MORR TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104278: 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532800 LATHAMS7 345 532801 ELKRVR17 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104218: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P23:345:WERE:MORR_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03912 | NConv | P42:345:OKGE:SB_RETN7303 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84584: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P12:345:WERE:EMPR-MORR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P12:345:OKGE:BKRBKR357_1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:OKGE-ITC:BKRBKR503_1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 42751: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | P12:345:WERE:VIOL-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P23:345:WERE:BENT_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:RENO_345-150:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | P23:345:WERE:SWIS_345-1:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104277: 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532799 WAVERLY7 345 532802 WAVERTX7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P12:345:WERE:SWIS-WGAR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03505 | NConv | 81776: 509852 T.NO.--7 345 512694 CLEVLND7 345 1 512694 CLEVLND7 345 560056 G15066_T 345 1 512694 CLEVLND7 345 998333 CLVAUTO1 138 1 512694 CLEVLND7 345 998341 CLVAUTO1 138 1 512694 CLEVLND7 345 998338 CLVAUTO1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 7801: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532991 WEAVER 4 138 533062 ROSEHIL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07425 | NConv | P12:115:MKEC:SMITHCENTER-CONCORDIA(SOUTH):: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38760: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | 8604: 532765 HOYT 7 345 532766 JEC N 7 345 1 532766 JEC N 7 345 532767 GEARY 7 345 1 532766 JEC N 7 345 532770 MORRIS 7 345 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 997953 JEC TX-13 230 1 532766 JEC N 7 345 997952 JEC TX-26 230 1 532766 JEC N 7 345 997959 JEC TX-13 230 1 532766 JEC N 7 345 997958 JEC TX-26 230 1 532766 JEC N 7 345 997955 JEC TX-13 230 1 532766 JEC N 7 345 997954 JEC TX-26 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 104976: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P55:161-345:KCPL:STILWELL_BUS_22_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_OPKY7388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 105458: 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 524295 SPNSPUR_WND1 0.69 560357 SPNSPUR_WND 34.5 1 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1 560357 SPNSPUR_WND 34.5 524296 SPNSPUR_WND7 345 1 523957 POTTER_TR 1 13.2 998120 WAUK 90343-A 230 1 523961 POTTER_CO 7 345 998120 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998126 WAUK 90343-A 230 1 523961 POTTER_CO 7 345 998126 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998123 WAUK 90343-A 230 1 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | P12:345:WERE:EMPR-SWIS_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104702: 542966 WGARDNR5 161 543132 BNSF 5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 80545: 530686 RICE 6 230 530688 BUFLOCRK6 230 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | P23:345:WERE:N345_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104251: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03912 | NConv | P42:345:OKGE:SB_RETN7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | P23:345:WERE:BENT_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P42:345:OKGE:SB_WWHV7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03912 | NConv | P42:345:OKGE:SB_RETN7311 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:STRA_345-95:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84346: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05741 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03342 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06289 | NConv | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | P23:345:WERE:HOYT_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09922 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06427 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 104257: 532765 HOYT 7 345 532766 JEC N 7 345 1 532765 HOYT 7 345 532772 STRANGR7 345 1 532765 HOYT 7 345 997954 HOYT TX-1 115 1 532765 HOYT 7 345 997960 HOYT TX-1 115 1 532765 HOYT 7 345 997956 HOYT TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09922 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA | non-Converged in the BC | N/A
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.8 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 106.63 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 108.57 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 108.61 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00197 | 105.69 | 104518: 541201 SIBLEY 7 345 997774 SIBLEY11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 997781 SIBLEY11 161 11 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | External | 105.65 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 100.48 | 346004 7GOSCK 345 3WXFMR GSK1 GSU 1: 346004 7GOSCK 345 998845 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998845 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998845 GSK1 GSU 13.8 1 346004 7GOSCK 345 998848 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998848 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998848 GSK1 GSU 13.8 1 346004 7GOSCK 345 998852 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998852 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998852 GSK1 GSU 13.8 1 | External | 100.37 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00119 | 137.61 | P23:345:GRE:PVS 19JB2 | External | 137.78 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00036 | 106.4 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 106.65 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 108.42 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.95 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 103.84 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 104.05 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 104.32 | -0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 100.87 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 100.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00052 | 113.96 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 113.88 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00535 | 125.61 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 125.56 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 116.7 | P12:345:AMIL-MEC::OAKGROVE:SANDBURG:1 | External | 116.8 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00309 | 110.88 | 300043 7KINGDM 345 300044 7MCCRED 345 1: 300043 7KINGDM 345 300044 7MCCRED 345 1 | External | 110.8 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 102.73 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 102.75 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.39 | P11:24:AEPW:PIRKEY 1 | External | 111.29 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00119 | 115.42 | P12:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | External | 115.56 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 107.59 | P23:345:MEC:CBEC 905 | External | 107.06 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 118.43 | P23:345:XEL:8P5 KING | External | 118.47 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 112.32 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 112.3 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.91 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.9 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 103.43 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 103.42 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 146.77 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | External | 146.9 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01241 | 128.46 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00027 | 120.25 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 120.14 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.74 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18 1: 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0003 | 103.87 | P12:161:ALTW:AUTO-SINGLE:MTVERN5:WYOMING5:1 | External | 103.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 105.87 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 105.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 103.94 | 105813: 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 652509 FTRANDL4 230 652526 UTICAJC4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 652509 FTRANDL4 230 652510 FTRANDL7 115 1 652509 FTRANDL4 230 652510 FTRANDL7 115 2 652509 FTRANDL4 230 652547 FTRDL34G 13.8 1 652509 FTRANDL4 230 652548 FTRDL56G 13.8 1 652509 FTRANDL4 230 652549 FTRDL78G 13.8 1 652501 ARMOUR 7 115 652510 FTRANDL7 115 1 652501 ARMOUR 7 115 652518 MTVERN 7 115 1 652246 ARMOUR 9 34.5 652501 ARMOUR 7 115 1 652249 ARMOUR 8 69.0 652501 ARMOUR 7 115 1 640349 SPENCER7 115 652510 FTRANDL7 115 1 652475 BONESTL7 115 652510 FTRANDL7 115 1 652510 FTRANDL7 115 655490 WHTSWAN-ER7 115 1 652510 FTRANDL7 115 652546 FTRDL12G 13.8 1 652475 BONESTL7 115 652478 GREGORY7 115 1 652525 TYNDALL7 115 655490 WHTSWAN-ER7 115 1 652525 TYNDALL7 115 660006 YKNTJCT7 115 1 652525 TYNDALL7 115 652286 TYNDALL8 69.0 1 | External | 103.89 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 123.95 | P23:345:MEC:BLACK HAWK 901 | External | 124.34 | -0.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.4 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 100.3 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00027 | 115.76 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 115.67 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.5 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | Internal | 105.09 | 1.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.35 | P24:345:XEL:8E7 ECL BS SPS | External | 118.33 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00447 | 107.03 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1: 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | External | 106.96 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 108.09 | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | External | 108.4 | -0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06899 | 106.89 | P23:345:MEC:MONTEZUMA 901 | Internal | 105.54 | 1.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01025 | 107.32 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 107.48 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00122 | 101.09 | P12:161:MEC:AUTO-SINGLE:POCHNTC5:POMEROY5:1 | External | 101.03 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 107.72 | 620314 BIGSTON4 230 3WXFMR BSP 230 1: 620314 BIGSTON4 230 997504 BSP 230 115 1 620316 BIGSTON9 13.8 997504 BSP 230 115 1 620314 BIGSTON4 230 997512 BSP 230 115 1 620316 BIGSTON9 13.8 997512 BSP 230 115 1 620314 BIGSTON4 230 997505 BSP 230 115 1 620316 BIGSTON9 13.8 997505 BSP 230 115 1 | External | 107.2 | 0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00118 | 114.97 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 114.78 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00458 | 106.52 | 104570: 301342 5BUTLER 161 541208 NEVADA 5 161 1 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 106.42 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00033 | 109.02 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 109.27 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 6e-05 | 114.48 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 114.95 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 106.6 | P23:345:MEC:OAK GROVE 901 | External | 106.54 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.15 | P11:13:GRE:AUTO-SINGLE:GRE-PVS53G:3 | External | 142.23 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 111.49 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 111.42 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 147.97 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 148.15 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.25 | P11:345:AMMO::CALLAWAY:1 | External | 110.17 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 105.82 | 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2: 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2 | External | 105.69 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 101.25 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 100.98 | 0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 114.44 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 114.31 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 104.03 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 103.99 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 107.22 | P24:345:AMMO::LABADIE:20H | External | 106.98 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 105.66 | P23:345:MEC:CBEC 905 | External | 105.13 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01075 | 118.38 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 118.23 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00015 | 102.59 | 93779: 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 588210 GEN-2016-130 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659105 LELAND_O-BE3 345 659111 LELAND_2-BEG 20.0 1 659105 LELAND_O-BE3 345 997099 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997098 LOS KV2A 230 1 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 997106 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997105 LOS KV2A 230 1 659105 LELAND_O-BE3 345 997097 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997096 LOS KV2A 230 1 | External | 102.28 | 0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00176 | 125.37 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 125.61 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00309 | 110.88 | 300090 5KINGDM 161 300043 7KINGDM 345 1: 300090 5KINGDM 161 300043 7KINGDM 345 1 | External | 110.82 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0012 | 111.9 | P23:345:AMIL::SANDBURG:3 | External | 111.74 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00132 | 114 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1 | External | 114.29 | -0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 149.94 | P23:345:MEC:SYCAMORE 901 | External | 150.06 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 129.78 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 129.76 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.63 | P24:345:XEL:8E7 ECL BS SPS | External | 118.18 | 0.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533416 RENO 3 115 533429 MOUNDRG3 115 1 | 218 | 262 | 0.07812 | 129.03 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 128.32 | 0.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00423 | 105.06 | 345408 7OVERTON 345 345409 5OVERTON 161 1: 345408 7OVERTON 345 345409 5OVERTON 161 1 | External | 104.95 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.08 | P24:345:XEL:8E7 ECL BS SPS | External | 126.17 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 133.57 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 133.42 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00152 | 111 | P12:345:XEL:SPS HNA-SSL | External | 111.14 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00126 | 114.9 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00219 | 101.92 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | External | 101.84 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00114 | 111.26 | P23:345:XEL:8N28 SHC | External | 111.41 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00186 | 151.8 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 151.76 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.0021 | 102.09 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 102.13 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.85 | P23:345:ITCM:HCKRYCK:FUT1 | External | 153.02 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.98 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 100.97 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 100.05 | 672540 QE 6 138 672541 CORY 6 138 1: 672540 QE 6 138 672541 CORY 6 138 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.2 | P13:161-22:AEPW:FLINTCR5 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00472 | 110.22 | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | External | 110.07 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01243 | 124.98 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 124.71 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 124.71 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 104.47 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | External | 104.66 | -0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 115.25 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External | 115.01 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 100.98 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 100.7 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 118.31 | P24:345:XEL:8E7 ECL BS SPS | External | 117.93 | 0.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 155.31 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 155.28 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15956 | 130.75 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 129.46 | 1.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.53 | P11:HV:EES::TURKCOAL:1 | External | 111.43 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.34 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 104.14 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.94 | P11:HV:EES::1WAT U3!:1 | External | 100.75 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00985 | 109.17 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 110.39 | -1.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00134 | 119.69 | 636235 WALL LK5 161 636236 WALL LK8 69 1: 636235 WALL LK5 161 636236 WALL LK8 69.0 1 | External | 119.48 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00417 | 104.18 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 104.06 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 100.76 | 71593: 603065 CHISAGO7 115 603172 WYOMING7 115 1 603136 HUGO 7 115 603172 WYOMING7 115 1 603065 CHISAGO7 115 605269 LINDSTM7 115 1 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 100.69 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01142 | 136.37 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 136.31 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00033 | 101.06 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 101 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 113.1 | 300001 1THLG1 20 300120 5THMHILB1 161 1: 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 113 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00152 | 107.81 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 107.78 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.62 | P11:24:AEPW:PIRKEY 1 | External | 111.52 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00135 | 113.99 | P23:345:XEL:SPS 8S81 SSL | External | 114.13 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 6e-05 | 114.39 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 114.9 | -0.51
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05277 | 101.52 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 101.3 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00173 | 113.72 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 114.35 | -0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.7 | 104894: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00534 | 115.41 | P22:345:AMMO::OVERTON:1 | External | 115.3 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 107.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External | 106.86 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15529 | 103.98 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal | 102.8 | 1.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.47 | 92432: 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.42 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 114.1 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 114.19 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.49 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 100.48 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01263 | 120.11 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 120.02 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.1733 | 101.83 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 100.64 | 1.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.82 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | External | 111.77 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00209 | 103.28 | P23:345:MEC:NORWALK 901 | External | 103.14 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00417 | 103.52 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 103.45 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.66 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00031 | 134.28 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 134.2 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00018 | 106.57 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 106.27 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 112.95 | P23:345:XEL:SPS 8S81 SSL | External | 112.91 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01038 | 111.37 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 111.27 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 105.04 | P23:345:ALTW:MITCHLCO:1140 | External | 104.99 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.19 | 84486: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.95 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 110.88 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 997481 DGG9T1 161 1 | 560 | 700 | 0.00295 | 105.88 | P23:345:MEC:SYCAMORE 905 | External | 105.89 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.25 | P12:115:OTP:AUTO-SINGLE:GRE-GRACEV7:DUMONT7:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.36 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 110.42 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 115.87 | P12:161:DPC:RCE-HAR5 | External | 115.93 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00424 | 120.87 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External | 120.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00161 | 103.46 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.4 | 346004 7GOSCK 345 3WXFMR GSK3 GSU 1: 346004 7GOSCK 345 998843 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998843 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998843 GSK3 GSU 13.8 1 346004 7GOSCK 345 998846 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998846 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998846 GSK3 GSU 13.8 1 346004 7GOSCK 345 998850 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998850 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998850 GSK3 GSU 13.8 1 | External | 110.3 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07005 | 112.71 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 111.24 | 1.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.23 | P11:HV:EES::PIRKEY 1:1 | External | 100.11 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 105.61 | Base Case | External | 105.5 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.0702 | 113.79 | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 112.13 | 1.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00084 | 121.72 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 121.54 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 116.7 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 116.8 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01038 | 102.62 | P23:345-161:XEL:ADAMS_I:681_S | External | 102.54 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01142 | 136.37 | P23:345:MEC:MONTEZUMA 902 | External | 136.31 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00207 | 113.12 | P12:345:XEL:SPS HNA-SSL | External | 113.25 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00094 | 122.26 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 122.05 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00113 | 113.3 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 113.46 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 113.58 | 300070 5CLARK 161 541208 NEVADA 5 161 1: 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 113.5 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00535 | 126.73 | P22:345:AMMO::OVERTON:1 | External | 126.71 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 112.86 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | External | 112.86 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00135 | 113.88 | P12:345:XEL:SPS HNA-SSL | External | 114.02 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 140.11 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 140.3 | -0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00107 | 109.64 | P23:345:GRE:PVS 19JB2 | External | 109.7 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00053 | 103.27 | 631084 VIELE 5 161 630013 VIELE 8 69 1: 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | External | 103.62 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 681528 HARMONY5 161 1 | 240 | 264 | 0.00059 | 106.56 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 106.54 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.91 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 152.79 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00257 | 117.39 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 117.54 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.08612 | 119.93 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 117.79 | 2.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.43 | P13:161-69:ITCM:LIME CK5 T1:IA-NW | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 104.82 | 672621 SHAND 4 230 672321 SHAND 1G 18 1: 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | External | 104.77 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0011 | 107.71 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 107.69 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00221 | 146.63 | P23:345:MEC:KOSSUTH 904 | External | 146.77 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01112 | 125.73 | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | External | 125.29 | 0.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.45 | P12:HV:EES::PIRKEY 4:1 | External | 111.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00012 | 115.97 | P23:345:XEL:8S27 WLM AS | External | 116.04 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00228 | 129.92 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 129.81 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00985 | 107.28 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01176 | 125.96 | P23:345:AMMO::ZACHARY:2 | External | 125.91 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00648 | 106.81 | P12:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 106.71 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00066 | 111.97 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External | 111.79 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00164 | 117.93 | P23:345:MEC:GDMEC 902 | External | 117.88 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.25 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 142.29 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00083 | 120.13 | 105985: 656191 HAMPTON5 161 656207 HAMPTONTAP5 161 1 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 636230 FRANKLN5 161 656207 HAMPTONTAP5 161 1 | External | 119.95 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.42 | P23:345:ALTW:MITCHLCO:1130 | External | 106.51 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00083 | 120.85 | P12:161:CBPC-MEC:SHEFFIELD-HAMPTONTAP-FRANKLIN:1 | External | 120.66 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00278 | 102.1 | P12:138:AMMO::BLAND:OSAGE:6030 | External | 102.05 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01069 | 113.09 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 113.03 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05965 | 102.27 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal | 100.74 | 1.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.65 | P12:EHV:EES::8ANO%:1 | External | 103.56 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00472 | 110.26 | P23:345:WERE:N345_345-80:: | External | 110.11 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00038 | 105.41 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 105.3 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 109.59 | 92672: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00409 | 117.95 | 104105: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External | 117.9 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00418 | 104.1 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 104 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00464 | 103.41 | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | External | 103.36 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 113.92 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 113.56 | 0.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00062 | 126.17 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 125.99 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 119.53 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 119.48 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00055 | 110.24 | P12:345:XEL:SPS WLM-SSL | External | 110.19 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.81 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 112.93 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00032 | 118 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 117.97 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.4 | 346004 7GOSCK 345 3WXFMR GSK2 GSU 1: 346004 7GOSCK 345 998844 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998844 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998844 GSK2 GSU 13.8 1 346004 7GOSCK 345 998847 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998847 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998847 GSK2 GSU 13.8 1 346004 7GOSCK 345 998851 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998851 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998851 GSK2 GSU 13.8 1 | External | 110.3 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 101.49 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 101.36 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00034 | 115.48 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 115.46 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 118.19 | P23:345:AMIL::HERLEMAN:1 | External | 118.19 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00168 | 122.1 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 122.12 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 123.07 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 123.07 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00648 | 106.81 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 106.71 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00147 | 107.19 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 107.22 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00123 | 112.1 | P23:345:AMIL::HERLEMAN:3 | External | 112.05 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.89 | P11:21:EES:RVB:1 | External | 103.81 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00133 | 107.03 | P12:345:XEL:SPS HNA-SSL | External | 107.14 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 154.61 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 154.62 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 202.17 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 202.2 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 4e-05 | 106.2 | P23:345:MEC:GDMEC 902 | External | 106.24 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 113.76 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External | 113.27 | 0.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0014 | 100.2 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | External | 100.05 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00044 | 116.73 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 116.84 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00983 | 119.16 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 119.1 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00186 | 150.19 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 150.47 | -0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 100.89 | 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1: 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 100.81 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.003 | 100.69 | P22:345:AMMO::LABADIE:3 | External | 100.65 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00123 | 108.6 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | External | 108.76 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 142.49 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 142.58 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 7e-05 | 116.72 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 116.74 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00012 | 153.92 | P12:161:DPC:AUTO-SINGLE:WABACO5:ALMA5:1 | External | 153.98 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | 717.1 | 717.1 | 0.07187 | 109.45 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 109.23 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00062 | 110.49 | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | External | 110.47 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 112.86 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 113.23 | -0.37
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 123.68 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 123.55 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 105.98 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 106.3 | -0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.05 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 101.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00205 | 121.19 | P23:345:MEC:KOSSUTH 904 | External | 121.31 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 105.15 | 620238 WINGER 7 115 3WXFMR WINGER 1: 620238 WINGER 7 115 997512 WINGER 69.0 1 657805 WINGER 8 69.0 997512 WINGER 69.0 1 620138 WINGER 9 41.6 997512 WINGER 69.0 1 620238 WINGER 7 115 997519 WINGER 69.0 1 657805 WINGER 8 69.0 997519 WINGER 69.0 1 620138 WINGER 9 41.6 997519 WINGER 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00417 | 103.37 | 84122: 509782 R.S.S.-7 345 509807 ONETA--7 345 1 509782 R.S.S.-7 345 509834 COGENT 7 345 1 509782 R.S.S.-7 345 509870 SAPLPRD7 345 1 509782 R.S.S.-7 345 514909 REDBUD 7 345 1 509782 R.S.S.-7 345 515235 PECANCK7 345 1 509782 R.S.S.-7 345 588040 G16133G16146 345 1 509782 R.S.S.-7 345 998422 RSS 2 138 1 509782 R.S.S.-7 345 998408 RSS 1 138 1 509782 R.S.S.-7 345 998430 RSS 2 138 1 509782 R.S.S.-7 345 998416 RSS 1 138 1 509782 R.S.S.-7 345 998427 RSS 2 138 1 509782 R.S.S.-7 345 998413 RSS 1 138 1 | External | 103.28 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00123 | 104.59 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 104.61 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 108.81 | P23:345:ALTW:MITCHLCO:1160 | External | 108.65 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 106.4 | P11:345:AMMO::CALLAWAY:1 | External | 106.3 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.0002 | 102.62 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 102.56 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 115.65 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 115.68 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00052 | 100.03 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.87 | P23:345:MEC:OAK GROVE 901 | External | 116.87 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 107.37 | 8670: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | Internal | 105.93 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00014 | 114.08 | 1061260: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00119 | 115.42 | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1: 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | External | 115.56 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 118.44 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 118.48 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14606 | 125.89 | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 124.95 | 0.94
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00072 | 153.43 | P23:345:ITCM:SALEM 3 2735:IA-NE | External | 153.15 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 113.44 | P23:345:ALTW:MITCHLCO:1130 | External | 113.58 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.79 | 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26 1: 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26.0 1 | Internal | 104.5 | 1.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 122.68 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 122.65 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15094 | 100.98 | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 100.17 | 0.81
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00732 | 111.38 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 111.29 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 113.56 | 84404: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 | External | 113.49 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 108.36 | P23:345:ALTW:MITCHLCO:1130 | External | 108.55 | -0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 111.56 | 631017 PRAR CK7 115 629066 PR CRK4G 18 1: 631017 PRAR CK7 115 629066 PR CRK4G 18.0 1 | External | 111.46 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 107.09 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 107 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00123 | 104.66 | P12:345:XEL:ASK-ECL SPS | External | 104.66 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00152 | 111.19 | P23:345:XEL:8S25 WLM AS | External | 111.54 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.99 | P11:HV:EES::1RVR_BND_G1!:1 | External | 106.79 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03682 | 114.8 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 114.63 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.23 | P11:23:EES-EAI:PLUM17:1 | External | 110.12 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00056 | 101.73 | P23:345:XEL:8S50 HMP | External | 101.78 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01113 | 126.15 | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | External | 125.89 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00133 | 107.12 | P23:345:XEL:SPS 8S81 SSL | External | 107.23 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01045 | 116.24 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 116.16 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0002 | 156.22 | P23:345:GRE:PVS 19JB2 | External | 156.22 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.25 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External | 120.12 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 116.06 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 115.38 | 0.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 107.81 | P23:345:MEC:CBEC 908 | External | 107.26 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 142.16 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 142.04 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01025 | 107.29 | P12:345:XEL:ASAK-ECL SPS | External | 107.44 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 107.84 | P23:345:ITCM:SALEM 3 2835:IA-NE | External | 107.67 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00985 | 109 | P12:345:MEC:TIFFIN-ARNOLD | External | 108.94 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 128.07 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 128.06 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 110.91 | P24:345:XEL:8E7 ECL BS | External | 111.19 | -0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00132 | 106.15 | P12:161:MEC:AUTO-SINGLE:HAYES5:POMEROY5:1 | External | 106.14 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.09 | 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26 1: 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26.0 1 | External | 101.03 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 111.86 | P13:161-69:ITCM:CARBIDE5 T1:IA-EC | External | 111.67 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 107.04 | 84365: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00058 | 111.59 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 112.04 | -0.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00025 | 127.1 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 127.14 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00094 | 162.03 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 162.05 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 104.61 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 104.56 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 140.46 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 142.04 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 141.95 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00067 | 118.66 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 117.88 | 0.78
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00137 | 131.4 | P23:345:GRE:CHL 304JB22 | External | 131.56 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 104.96 | 105823: 652515 HURON 7 115 660009 BTAP WP7 115 1 660003 HURONWP7 115 660009 BTAP WP7 115 1 660009 BTAP WP7 115 660040 DAKOTACCESS7 115 1 652515 HURON 7 115 652528 WOONSKT7 115 1 652515 HURON 7 115 655481 REDFELD-ER7 115 1 652515 HURON 7 115 660003 HURONWP7 115 1 652284 HURON 8 69.0 652515 HURON 7 115 1 652515 HURON 7 115 997158 HU KV1A 115 1 652515 HURON 7 115 997157 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 1 652507 FTTHOMP4 230 652514 HURON 4 230 2 652514 HURON 4 230 652530 WATERTN4 230 2 652514 HURON 4 230 652614 CARPENTER 4 230 1 652514 HURON 4 230 659205 BROADLND-BE4 230 1 652514 HURON 4 230 997158 HU KV1A 115 1 652514 HURON 4 230 997157 HU KV1B 115 2 652528 WOONSKT7 115 659123 STORLA__-BE7 115 1 652528 WOONSKT7 115 655355 WOONSKT-ER8 69.0 2 652284 HURON 8 69.0 655063 SW341-ER8 69.0 1 652284 HURON 8 69.0 655066 SW352-ER8 69.0 1 652284 HURON 8 69.0 655067 SW353-ER8 69.0 1 652282 HURON429 13.3 997157 HU KV1B 115 2 652281 HURON419 13.3 997158 HU KV1A 115 1 652515 HURON 7 115 997165 HU KV1A 115 1 652515 HURON 7 115 997164 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 2 652514 HURON 4 230 997165 HU KV1A 115 1 652514 HURON 4 230 997164 HU KV1B 115 2 652282 HURON429 13.3 997164 HU KV1B 115 2 652281 HURON419 13.3 997165 HU KV1A 115 1 652515 HURON 7 115 997156 HU KV1A 115 1 652515 HURON 7 115 997155 HU KV1B 115 2 652514 HURON 4 230 997156 HU KV1A 115 1 652514 HURON 4 230 997155 HU KV1B 115 2 652282 HURON429 13.3 997155 HU KV1B 115 2 652281 HURON419 13.3 997156 HU KV1A 115 1 | External | 104.73 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 113.89 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 113.83 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00037 | 101.3 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 101.21 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00113 | 113.36 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 113.31 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 110.9 | P24:345:XEL:8E7 ECL BS SPS | External | 110.6 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.52 | P22:345:AMMO::RUSHISLAND:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00119 | 112.17 | P23:345:MEC:OAK GROVE 903 | External | 111.3 | 0.87
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01039 | 106.32 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01305 | 121.17 | P12:345:XEL:SPS WLM-SSL | External | 121.09 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 101.74 | Base Case | External | 101.61 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00983 | 115.93 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 115.95 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 111.02 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 110.97 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 112.57 | P23:345:MEC:LOUISA 924 | External | 112.35 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00294 | 100.81 | 104710: 541225 PHILL 5 161 541239 HSNVL 5 161 1 541225 PHILL 5 161 541243 LKWINGB5 161 1 541225 PHILL 5 161 541313 HARRIS 161 1 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 541163 DOGWDCT1 18.0 541225 PHILL 5 161 1 541164 DOGWDCT2 18.0 541225 PHILL 5 161 1 541225 PHILL 5 161 997775 P HILL 11 161 11 541280 PHILL 2 69.0 541225 PHILL 5 161 1 541225 PHILL 5 161 997782 P HILL 11 161 11 541225 PHILL 5 161 997778 P HILL 11 161 11 | External | 100.72 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.24 | P23:345:OPPD:S3458 NEBCTY1G | External | 103.21 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 110.68 | 344011 7HUGHES 345 344012 7HPW-N 345 1: 344011 7HUGHES 345 344012 7HPW-N 345 1 | External | 110.69 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.1 | P12:EHV:EES::8ANO%:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0029 | 100.91 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 100.87 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 133.78 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 133.8 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.1 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 104.03 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.87 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.87 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 4e-05 | 130.69 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 130.56 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00282 | 102.91 | 104212: 542972 HAWTH 7 345 997748 HAWTHORN22 161 22 542972 HAWTH 7 345 997749 HAWTHORN20 161 20 542972 HAWTH 7 345 997755 HAWTHORN22 161 22 542972 HAWTH 7 345 997756 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | External | 102.86 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 136.31 | P23:345:ALTW:MITCHLCO:1130 | External | 136.51 | -0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 156.42 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 156.47 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00834 | 135.76 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 135.48 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 100.87 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0013 | 106.96 | P23:345:GRE:CHL 304JB22 | External | 107.09 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.97 | 92478: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 135.01 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 131.9 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 131.9 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.38 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 118.51 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.28 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 118.15 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00041 | 101.27 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 101.35 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 120.02 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 119.67 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.26 | P12:HV:EES::TURK 4%:1(1) | External | 104.13 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00021 | 151.07 | P23:345:MEC:GDMEC 902 | External | 151.06 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 138.16 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 138.02 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0006 | 107.1 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 107.15 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00123 | 104.64 | P24:345:XEL:8E7 ECL BS SPS | External | 104.65 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01248 | 124.21 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00381 | 112.71 | P22:345:AMMO::LABADIE:4 | External | 112.59 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00046 | 103.67 | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | External | 103.38 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00012 | 105.01 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 104.76 | 0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00381 | 116.77 | P24:345:AMMO::LABADIE:8H | External | 116.68 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00111 | 106.32 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 106.29 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.39 | P11:HV:EES::PIRKEY 1:1 | External | 111.29 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 145.71 | 71568: 601024 TERMINL3 345 997652 90198-B 115 10 603110 TERMINL7 115 997652 90198-B 115 10 605516 TERTER19 34.5 997652 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997659 C0512551 115 9 603084 KOLMNLK7 115 997659 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997659 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 601024 TERMINL3 345 997659 90198-B 115 10 603110 TERMINL7 115 997659 90198-B 115 10 605516 TERTER19 34.5 997659 90198-B 115 10 601021 KOLMNLK3 345 997666 C0512551 115 9 603084 KOLMNLK7 115 997666 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997666 C0512551 115 9 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 | External | 145.69 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00981 | 116.15 | P23:345:GRE:PVS 19JB2 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 121.25 | P11:345:AMMO::CALLAWAY:1 | External | 121.14 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 135.33 | P12:069:UMZ:# 5707 #: IN . PROPER N-1 (LINE) FOR 656025-656039-1 | External | 134.28 | 1.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00061 | 107.69 | P23:345:AMIL::SANDBURG:3 | External | 107.73 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00289 | 101.07 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 101 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00409 | 104.83 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 104.74 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 120.02 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 119.67 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00176 | 114.86 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 115.09 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18231 | 152.92 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 151.62 | 1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 122.35 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 122.22 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.04 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.41 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2 | External | 141.47 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 101.25 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 100.98 | 0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05887 | 101.76 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6 | Internal | 100.36 | 1.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00011 | 116.69 | P12:345:XEL:SPS WLM-SSL | External | 116.79 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.32 | 631206 QUINN3 345 631207 J416_WF3 345 1: 631206 QUINN3 345 631207 J416_WF3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06932 | 112.71 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 111.22 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.19 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 101.12 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 165.12 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 165.15 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 119.04 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 119.02 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.75 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External | 112.21 | 0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06961 | 111.9 | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 110.48 | 1.42
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00111 | 115 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 114.77 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 103.43 | P23:345:MEC:MONTEZUMA 902 | External | 103.42 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 6e-05 | 110.54 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 110.49 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 106.52 | P22:345:AMMO::LABADIE:3 | External | 106.47 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 116.02 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 115.95 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 100.48 | 346004 7GOSCK 345 3WXFMR GSK3 GSU 1: 346004 7GOSCK 345 998843 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998843 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998843 GSK3 GSU 13.8 1 346004 7GOSCK 345 998846 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998846 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998846 GSK3 GSU 13.8 1 346004 7GOSCK 345 998850 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998850 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998850 GSK3 GSU 13.8 1 | External | 100.37 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 115.74 | P23:345:ALTW:MITCHLCO:1150 | External | 115.63 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00424 | 118.98 | P12:161:AECI:M:HUNTSDL:C_PERCH:1 | External | 118.9 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 6e-05 | 125.91 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 125.9 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00022 | 108.19 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 108.1 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00209 | 109.49 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 109.63 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00025 | 102.93 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 103.03 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 139.6 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 139.47 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01038 | 112.22 | P23:345-161:XEL:ADAMS_I:680_S | External | 112.14 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00974 | 115.79 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.53 | 636410 SUB P IC 5 161 636411 SUB P IC 8 69 1: 636410 SUB P IC 5 161 636411 SUB P IC 8 69.0 1 | External | 110.41 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.63 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 101.86 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 169.66 | P24:345:XEL:8E7 ECL BS | External | 169.73 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 112.94 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01164 | 126.97 | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | External | 127.01 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0001 | 121.98 | 620363 FORMAN 4 230 3WXFMR 230/115 1: 620363 FORMAN 4 230 997498 230/115 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 620363 FORMAN 4 230 997505 230/115 115 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 | External | 121.45 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00014 | 114.08 | 106126: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.29 | P13:230:EES:WATERF:T6:T7 | External | 112.16 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 107.84 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 107.82 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01199 | 124.64 | P12:345:MEC:TIFFIN 9T1 SPS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00981 | 116.36 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 116.36 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.04 | P12:345:XEL:ASAK-ECL SPS | External | 125.99 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0007 | 109.24 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 109.17 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 169.7 | P12:345:XEL:ASK-ECL SPS | External | 169.91 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.34 | 631048 EMERY 5 161 629067 EMERYGT1 18 1: 631048 EMERY 5 161 629067 EMERYGT1 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 144.49 | Base Case | External | 144.51 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.85 | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1: 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | External | 153.02 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 142.49 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 142.58 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 102.73 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 102.68 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 102.81 | P23:345:GRE:CHL 304JB22 | External | 102.94 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00117 | 116.12 | 69840: 270700 CORDOVA ; B 345 270867 QUAD 8-10 345 1 270867 QUAD 8-10 345 636605 MECCORD3 345 1 | External | 115.98 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00981 | 116.36 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 116.36 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.36 | P12:345:XEL:ASK-ECL SPS | External | 118.34 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 111.61 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 111.77 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 140.55 | P13:13-13-161:XEL:AUTO-SINGLE:WHT55G:WHT56G:WHT565:1 | External | 140.49 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.61 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 106.85 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00116 | 140.86 | P12:161:ALTW-MEC:AUTO-SINGLE:BNEJCT5:FT.DODG5:1 | External | 140.57 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 101.55 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 101.5 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.34 | P23:500:EES-EAI:WH_BLF:B7932 | External | 100.31 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00984 | 117.96 | P23:345:MEC:TIFFIN 954 | External | 117.91 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01176 | 133.81 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 133.77 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00012 | 115.99 | P23:345:XEL:8S25 WLM AS | External | 116.02 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0106 | 103.77 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00081 | 107.7 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 107.64 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00032 | 102.21 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 102.14 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 102.78 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 102.85 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00052 | 105.97 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 105.94 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01052 | 111.68 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 111.61 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00012 | 107.05 | 105835: 652520 OAHE 7 115 652559 OAHE 1G 13.8 1 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652489 PIERRE 7 115 652600 ASH TAP 115 1 652520 OAHE 7 115 652600 ASH TAP 115 1 652600 ASH TAP 115 658120 GARFLD 7 115 1 652476 EAGLEBT7 115 652520 OAHE 7 115 1 652491 IRVSIMM7 115 652520 OAHE 7 115 1 652520 OAHE 7 115 997156 OA NO. 5 115 1 652520 OAHE 7 115 997155 OA NO. 6 115 1 652589 OAHE 9 13.8 997156 OA NO. 5 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652520 OAHE 7 115 997163 OA NO. 5 115 1 652520 OAHE 7 115 997162 OA NO. 6 115 1 652589 OAHE 9 13.8 997163 OA NO. 5 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 652520 OAHE 7 115 997154 OA NO. 5 115 1 652520 OAHE 7 115 997153 OA NO. 6 115 1 652589 OAHE 9 13.8 997154 OA NO. 5 115 1 | External | 106.51 | 0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.34 | P11:HV:EES::1NM G1:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01038 | 101.36 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 101.23 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.35 | P13:500:EES-EAI:WH_BLF:ST2 | External | 100.3 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111 | P12:EHV:EES::WELSH 7:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0013 | 133.23 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | External | 133.45 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05962 | 101.16 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01208 | 121 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 120.94 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.55 | P13:138-24:AEPW:TURK 4 | External | 111.45 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 120.24 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 120.24 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.004 | 117.95 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | External | 117.87 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00144 | 110.39 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 110.42 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00041 | 101.27 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 101.35 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01149 | 112.59 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00145 | 166.19 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 166.4 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.0065 | 114.32 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 113.2 | 1.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00354 | 126.35 | P23:345:MEC:GDMEC 901 | External | 126.22 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.72 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 100.7 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.15 | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 112.89 | 631059 8TH ST.5 161 681520 GALENA 5 161 1: 631059 8TH ST.5 161 681520 GALENA 5 161 1 | External | 112.88 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00387 | 125.94 | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | External | 125.87 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00648 | 106.81 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 106.71 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00053 | 108.66 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 108.58 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00071 | 104.14 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 104.01 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00098 | 123.15 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 123.03 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00985 | 118.9 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 120.2 | -1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.8 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 153.82 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00025 | 125.34 | P12:230:OTP::BIGSTON4:HANKSON4 | External | 125.4 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 102.77 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 102.74 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0303 | 136.27 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 136.09 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.005 | 125.76 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 126.11 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00329 | 103.05 | P23:161-345:GMO:BLUESPRINGSE_R4-12::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 102.98 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 156.57 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 156.47 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00059 | 140.35 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 140.28 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00034 | 115.6 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 115.58 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00463 | 105.28 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.17 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 113.88 | 92666: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 113.81 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00413 | 124.58 | P23:345:MEC:GDMEC 901 | External | 124.45 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00472 | 110.28 | P12:345:WERE:N345-LACY_345:: | External | 110.13 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.25 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 112.1 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 105.69 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 105.44 | 0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 105.33 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External | 105.26 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.86 | P23:345:ALTW:MITCHLCO:1160 | External | 106.74 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00092 | 150.37 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 150.36 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 123.46 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 123.01 | 0.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 107.6 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 107.5 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00096 | 133.4 | P23:345:MEC:OAK GROVE 901 | External | 133.33 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.81 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 112.93 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.74 | P21:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.78 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 117.79 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 117.73 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 117.91 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 118.07 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00062 | 109.98 | 301422 2LEE 69 631216 WEVER5 161 1: 301422 2LEE 69.0 631216 WEVER5 161 1 | External | 109.76 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 111.97 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 111.99 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 110.77 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | External | 110.84 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00109 | 105.89 | P23:345:MEC:TIFFIN 944 | External | 105.2 | 0.69
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00424 | 118.98 | 300500 5HUNTSDL 161 343004 5PERCHE 161 1: 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | External | 118.9 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 133.4 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 133.44 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00112 | 104.19 | 85493: 635200 RAUN 3 345 640226 HOSKINS3 345 1 640226 HOSKINS3 345 640342 SHELCRK3 345 1 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 640226 HOSKINS3 345 997391 HOSKINS T2 230 1 640226 HOSKINS3 345 997389 HOSKN T4 115 1 640226 HOSKINS3 345 997398 HOSKINS T2 230 1 640226 HOSKINS3 345 997396 HOSKN T4 115 1 | External | 104.08 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 110.14 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | Internal | 108.77 | 1.37
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0012 | 116.86 | P12:69:ATC:N-36:MIN69:SHU69 | External | 116.82 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 114.52 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 114.47 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01037 | 110.2 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 108.69 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.06 | P23:500:EAI:NBF_WHITE ~1 | External | 101 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 105.81 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 105.8 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15517 | 106.46 | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | Internal | 105.29 | 1.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.45 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 111.36 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 105.87 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06079 | 112.32 | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | Internal | 110.97 | 1.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00142 | 130.47 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 130.44 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 116.7 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 116.8 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.08 | P13:500:EES-EAI:INDEP2:MT2 | External | 105.91 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.76 | 344884 7LABADIE1 345 344894 1LAB G1 20 1: 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.57 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.51 | P12:EHV:EES::8WHT BLUFF%:1 | External | 103.42 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00642 | 102.03 | P23:345:MEC:OAK GROVE 901 | External | 101.99 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.62 | P11:24:AEPW:TURKCOAL | External | 101.53 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00367 | 120.62 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | External | 122.25 | -1.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 115.48 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 115.36 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 | 70 | 70 | 1e-05 | 102.91 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 102.91 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 110.87 | 271543 GARDEN PL; 138 631033 ALBANY 6 138 1: 271543 GARDEN PL; 138 631033 ALBANY 6 138 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00202 | 100 | P13:345-161:MEC:AUTO-SINGLE:NORWLK3:NORWLK5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00143 | 109.2 | P12:161:MEC-WAPA:AUTO-SINGLE:WEBSTER5:HOPE5:1 | External | 108.88 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 109.07 | P23:345:MEC:OAK GROVE 904 | External | 109.41 | -0.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 2e-05 | 159.88 | P42:345:NPPD:BKR-C-3322-2 | External | 159.86 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.55 | P13:138-24:AEPW:PIRKEY 4 | External | 101.47 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00065 | 130.48 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 130.41 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.21 | P13:138-24:AEPW:TURK 4 | External | 100.09 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 158.67 | 630139 ADAMS 8 69 631046 ADAMS 5 161 1: 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | External | 158.61 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 107.69 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External | 107.63 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00067 | 102.21 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 102.19 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00066 | 107.95 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 107.8 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00597 | 108.77 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | External | 108.65 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16673 | 124 | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 123 | 1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 141.01 | P23:345:MEC:OAK GROVE 904 | External | 141.06 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00066 | 109.41 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 109.4 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00101 | 117.07 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 116.95 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.45 | P11:23:EES-EAI:PLUM17:1 | External | 110.34 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00012 | 103.52 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 103.46 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00166 | 100.07 | P23:345:MEC:SYCAMORE 901 | External | 100.11 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00109 | 105.31 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 105.29 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.16 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 101.09 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00152 | 111.06 | P12:345:XEL:SPS WLM-SSL | External | 111.12 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01032 | 101.02 | P23:500:EAI:NBF_SAN SOUC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.09302 | 101.94 | P13:115-230:MIDW:RICE COUNTY | Internal | 101.28 | 0.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01028 | 115.3 | P23:345:XEL:8E5 ECL BS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 102.75 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00152 | 106.9 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 106.86 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00163 | 123 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 122.95 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 116.61 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 116.61 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00107 | 109.8 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 109.94 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 104.15 | 104501: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 104.05 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.77 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 122.08 | P23:345:XEL:8S23 WLM | External | 122.01 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06983 | 124.04 | 78002: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 122.59 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.65 | 631017 PRAR CK7 115 629066 PR CRK4G 18 1: 631017 PRAR CK7 115 629066 PR CRK4G 18.0 1 | External | 106.57 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00472 | 105.08 | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External | 104.96 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0124 | 126.33 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 126.28 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 125.61 | 300003 1THLG3 24 300049 7THOMHL 345 1: 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 125.48 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 118.86 | P22:345:XEL:ADAMS 3 N1:MN | External | 118.84 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.74 | P12:138:GRDA:CLEVLND-COLLINS | External | 101.68 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01049 | 112.68 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00089 | 112.79 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 112.6 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 601050 HELENA 3 345 615649 GRE-CHUBLAK3 345 1 | 1792.6 | 1792.6 | 0.00443 | 100.08 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External | 100.03 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 135.14 | 603271 FARIBALT GEN 115 600050 FEP CT G 18 1: 603271 FARIBALT GEN 115 600050 FEP CT G 18.0 1 | External | 135.19 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 114.06 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 113.96 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 107.76 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00045 | 110 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 110.93 | -0.93
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 108.23 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 108.13 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 111.02 | P23:345:XEL:8P5 KING | External | 111.03 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00092 | 150.37 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 150.36 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 123.59 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 123.65 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 101.8 | P12:161:DPC:RCE-HAR5 | External | 101.72 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.11 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 100.06 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 146.78 | P11:21:EES:RVB:1 | External | 146.84 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 123.39 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 123.36 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 108.24 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 108.14 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 141.23 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 141.16 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.87 | P11:20:AMMO:1LAB G1:1 | External | 112.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00113 | 138.09 | P12:161:MEC-WAPA:AUTO-SINGLE:FRANKLN5:HAMPTONTAP5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01038 | 111.11 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 111.01 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 603103 SCOTTCO7 115 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00294 | 111.79 | P23:345:XEL:8M57 SCO | External | 111.89 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14606 | 128.24 | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 127.31 | 0.93
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00144 | 110.39 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 110.42 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.5 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Internal | 105.09 | 1.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 117.13 | P12:161:AMMO-AECI::SOUTHRIVER:ADAIR:1 | External | 117.13 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00011 | 115.76 | P12:345:XEL:SPS WLM-SSL | External | 115.75 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.21 | P13:230:EES:WATERF:T6:T7 | External | 104.17 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.12 | P23:345:MEC:LOUISA 954 | External | 100.99 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 100.48 | 346004 7GOSCK 345 3WXFMR GSK2 GSU 1: 346004 7GOSCK 345 998844 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998844 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998844 GSK2 GSU 13.8 1 346004 7GOSCK 345 998847 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998847 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998847 GSK2 GSU 13.8 1 346004 7GOSCK 345 998851 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998851 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998851 GSK2 GSU 13.8 1 | External | 100.36 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 108.78 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 108.77 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 104.09 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 104.32 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0007 | 109.24 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 109.17 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.00018 | 144.67 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 144.6 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00424 | 120.87 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External | 120.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01032 | 101.02 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 100.93 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00573 | 106.41 | P23:345:MEC:HILLS 9114 | External | 106.33 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.34 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 111.4 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 111.4 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01026 | 115.52 | P12:345:XEL:ASAK-ECL | External | 115.72 | -0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00732 | 111.38 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 111.29 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 136.85 | P23:345:ALTW:MITCHLCO:1160 | External | 136.63 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 105.56 | P23:345:ALTW:MITCHLCO:1150 | External | 105.51 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00073 | 119.14 | P23:345:MEC:OAK GROVE 904 | External | 119.2 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 122.37 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External | 122.28 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00157 | 108.15 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 108.12 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00219 | 102.34 | P13:161-69:CIPCO:ANITA T1:IA-SW | External | 102.16 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0055 | 113.66 | 104177: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 113.54 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16051 | 100.52 | P12:115:MKEC:SAINTJOHN-SAINTJOHN(MIDWEST):: | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.12 | P11:HV:EES::1NM G1:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 101.91 | 631024 E CALMS7 115 631095 E CALMS5 161 1: 631024 E CALMS7 115 631095 E CALMS5 161 1 | External | 101.8 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0001 | 106.03 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596) | External | 105.53 | 0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07059 | 120.83 | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | Internal | 119.53 | 1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 211 | 211 | 0.00168 | 101.27 | P23:345:AMMO::ZACHARY:2 | External | 101.24 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00094 | 127.59 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 127.36 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 114.16 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 114 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07588 | 111.5 | P23:345:SUNC:SV_BRK188 | Internal | 109.97 | 1.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 108.78 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 108.64 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00063 | 104.77 | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1: 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | External | 104.8 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0091 | 102.73 | P23:345:MEC:ATCHISON CO 903 | External | 102.61 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00097 | 119.48 | 105985: 656191 HAMPTON5 161 656207 HAMPTONTAP5 161 1 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 636230 FRANKLN5 161 656207 HAMPTONTAP5 161 1 | External | 119.29 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0013 | 106.9 | P23:345:GRE:CHL 304JB21 | External | 107.03 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 245.29 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 245.28 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 141.02 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 141.01 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00135 | 113.86 | P12:345:XEL:SPS WLM-SSL | External | 114.01 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.38 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 142.39 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 184.12 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 184.16 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15956 | 131.21 | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 130.01 | 1.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07494 | 111.36 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 109.57 | 1.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.74 | P23:345:GRE:CHL 304JB20 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00327 | 106.17 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 106.1 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.5 | 344001 5ADAIR2 161 631112 APANOSE5 161 1: 344001 5ADAIR2 161 631112 APANOSE5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 114.89 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07706 | 128.32 | P12:230:WERE:CIRC-GRTBND_230:: | Internal | 126.75 | 1.57
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00169 | 102.44 | P23:345-161:XEL:ADAMS_I:681_S | External | 102.42 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08229 | 112.76 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal | 111.15 | 1.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.67 | P12:161:DPC:RCE-HAR5 | External | 108.71 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 115.77 | P23:345:ALTW:MITCHLCO:1160 | External | 115.65 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00164 | 117.95 | P23:345:MEC:GDMEC 901 | External | 117.9 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 105.73 | P23:500:EAI:NBF_WHITE ~1 | External | 105.53 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00367 | 119.95 | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 119.93 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00294 | 100.81 | 84318: 541225 PHILL 5 161 541239 HSNVL 5 161 1 541225 PHILL 5 161 541243 LKWINGB5 161 1 541225 PHILL 5 161 541313 HARRIS 161 1 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 541163 DOGWDCT1 18.0 541225 PHILL 5 161 1 541164 DOGWDCT2 18.0 541225 PHILL 5 161 1 541225 PHILL 5 161 997775 P HILL 11 161 11 541280 PHILL 2 69.0 541225 PHILL 5 161 1 541225 PHILL 5 161 997782 P HILL 11 161 11 541225 PHILL 5 161 997778 P HILL 11 161 11 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 121.07 | P23:345:ITCM:SALEM 3 215:IA-NE | External | 120.91 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.88 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 112.76 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.11 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 106.23 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06947 | 112.46 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 110.99 | 1.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14558 | 101.28 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 100.29 | 0.99
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 115.35 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 115.82 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00108 | 114.9 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 114.75 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14644 | 127.93 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 126.98 | 0.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 6e-05 | 113.43 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 113.96 | -0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.4 | P12:HV:EES::JTEC 5:1 | External | 103.34 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0027 | 128.85 | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 128.76 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.91 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 152.79 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.69 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1: 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1 | External | 106.62 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.77 | P11:26:EES-EAI:WH_BLF:1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 114.01 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 135.21 | 85478: 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 | External | 135.2 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.88 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | External | 103.81 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 132.12 | Base Case | External | 132 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01045 | 106.73 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 106.67 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.43 | 631206 QUINN3 345 631207 J416_WF3 345 1: 631206 QUINN3 345 631207 J416_WF3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0053 | 128.44 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 128.36 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00079 | 124.73 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 124.69 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 131.92 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 131.95 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05916 | 106.66 | 78000: 532771 RENO 7 345 587884 G16-111-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 105.22 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.51 | P11:345:AMMO::CALLAWAY:1 | External | 110.43 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05962 | 101.16 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00076 | 142.12 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 141.72 | 0.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.11 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 106.23 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 4e-05 | 106.19 | P23:345:MEC:GDMEC 901 | External | 106.24 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00124 | 124.2 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 124.06 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05717 | 106.23 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 104.98 | 1.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07059 | 115.2 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 113.76 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 135.56 | 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1: 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1 | External | 135.55 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 124.99 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 124.53 | 0.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00982 | 118.89 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 118.88 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 103.43 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 103.42 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 111.89 | 657747 ASH1 9 34.5 657701 BARNES 4 230 1: 657747 ASH1 9 34.5 657701 BARNES 4 230 1 | External | 111.43 | 0.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01043 | 111.96 | P23:345:MEC:BLACK HAWK 901 | External | 111.81 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 7e-05 | 117.43 | P23:345:XEL:8M53 SCO | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 139.6 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 139.47 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.74 | 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1: 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.78 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00385 | 111.5 | 300249 2FAIRPT 69 300076 5FAIRPT 161 1: 300249 2FAIRPT 69.0 300076 5FAIRPT 161 1 | External | 111.41 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00385 | 111.5 | 300249 2FAIRPT 69 300076 5FAIRPT 161 2: 300249 2FAIRPT 69.0 300076 5FAIRPT 161 2 | External | 111.41 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.7 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 114.24 | P23:345:MEC:LOUISA 924 | External | 114.49 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.93 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External | 103.9 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 104.83 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK | External | 104.24 | 0.59
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.76 | P11:EHV:EES::1ISES U2:1 | Internal | 104.35 | 1.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00065 | 128.28 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 128.26 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 113.15 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | External | 113.18 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.94 | P13:230:EES:WATERF:T6:T7 | External | 100.75 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00061 | 166.61 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 166.74 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00355 | 106.12 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 106.1 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 113.24 | P12:345:XEL:SPS HNA-SSL | External | 113.18 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 114.24 | P24:345:XEL:8E7 ECL BS | External | 114.41 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00052 | 100.12 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00227 | 129.61 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 129.53 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.69 | 92463: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 100.68 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0006 | 107.1 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 107.15 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 134.5 | P23:345:MEC:SYCAMORE 901 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0016 | 138.6 | P12:161:MEC-WAPA:AUTO-SINGLE:WEBSTER5:HOPE5:1 | External | 138.3 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 103.82 | 105850: 652529 WATERTN3 345 652829 WATERTN-LNX3 345 Z 652537 WHITE 3 345 652829 WATERTN-LNX3 345 1 652293 WHITE 9 13.8 997148 WHT KU1A 115 1 652504 BROOKNG7 115 652538 WHITE 7 115 1 652538 WHITE 7 115 655472 IVANHOE-ER7 115 1 652538 WHITE 7 115 997148 WHT KU1A 115 1 601006 SPLT RK3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 2 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 652537 WHITE 3 345 997148 WHT KU1A 115 1 652293 WHITE 9 13.8 997155 WHT KU1A 115 1 652538 WHITE 7 115 997155 WHT KU1A 115 1 652537 WHITE 3 345 997155 WHT KU1A 115 1 652293 WHITE 9 13.8 997146 WHT KU1A 115 1 652538 WHITE 7 115 997146 WHT KU1A 115 1 652537 WHITE 3 345 997146 WHT KU1A 115 1 | External | 103.79 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01126 | 132.2 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 132.1 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 160.73 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4 | External | 160.68 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00671 | 110.73 | P12:345:MEC:WALCOTT-SUB 56 + SUB 56 9T1 | External | 110.65 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.96 | P11:HV:EES::1WAT U3!:1 | Internal | 105.46 | 1.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00408 | 118.19 | 92256: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 118.11 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.29 | 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1: 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.33 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 112.07 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 111.98 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00123 | 108.71 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | External | 108.92 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00045 | 110 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 110.93 | -0.93
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 104.28 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 104.27 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00042 | 105.71 | P23:345:XEL:8S51 HMP | External | 105.69 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05798 | 100.56 | P12:69:MIDW:WALNUT CREEK-HANSTON | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.74 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1 | External | 111.13 | 0.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.77 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 150.79 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00215 | 102.38 | 631069 ANTA TP5 161 631070 ANITA 5 161 1: 631069 ANTA TP5 161 631070 ANITA 5 161 1 | External | 102.26 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01019 | 122.14 | P23:345:MEC:ATCHISON CO 903 | External | 122.02 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 106.07 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 105.52 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00121 | 118.79 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 118.59 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 113 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 112.9 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14644 | 125.82 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 124.85 | 0.97
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 120.53 | P12:345:XEL:ASAK-ECL | External | 120.37 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00031 | 100.34 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 101.1 | -0.76
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01087 | 112.99 | P23:345:XEL:8S27 WLM AS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.58 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 109.34 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 109.43 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 118.47 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 118.41 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00115 | 108.93 | 69840: 270700 CORDOVA ; B 345 270867 QUAD 8-10 345 1 270867 QUAD 8-10 345 636605 MECCORD3 345 1 | External | 108.81 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15515 | 106.05 | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | Internal | 104.9 | 1.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00168 | 120.96 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 120.92 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00064 | 113.52 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 113.44 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 118.93 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 119.03 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 227 | 227 | 0.00196 | 101.91 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 101.87 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00388 | 113.41 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 113.36 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06946 | 117.6 | 7800: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 116.21 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 105.66 | P23:500:EAI:NBF_SAN SO~2 | External | 105.44 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 114.16 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External | 113.69 | 0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 111.47 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 111.41 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00073 | 154.1 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 153.86 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 114.16 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 114 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 110.87 | P23:345:XEL:8P1 KING | External | 110.94 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00085 | 120.89 | 631048 EMERY 5 161 656201 SHEFFLD5 161 1: 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 120.69 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 107.48 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 107.61 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 113.34 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 113.14 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.57 | P11:HV:EES::1ISES U1:1 | External | 101.52 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 133.46 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 132.42 | 1.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.24 | P11:HV:EES::TURKCOAL:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00094 | 162.03 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 162.05 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00282 | 102.91 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 | External | 102.86 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.98 | P12:345:XEL:ASK-ECL SPS | External | 104.98 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 107.36 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 107.42 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 110.81 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 110.97 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.42 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1 | External | 141.48 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 100.98 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.82 | 337909 8ANO% 500 337911 1ANO U2 22 1: 337909 8ANO% 500 337911 1ANO U2 22.0 1 | Internal | 105.43 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 108.57 | P22:345:XEL:ADAMS 3 N1:MN | External | 108.48 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00176 | 126.65 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 126.61 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.06506 | 111.59 | P12:230:WERE:CIRC-GRTBND_230:: | Internal | 110.2 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 127.87 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 128.03 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00117 | 108.13 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | External | 108.21 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 116.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 116.75 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00099 | 147.15 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 146.95 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.46 | 92405: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 102.42 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01037 | 108.41 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 108.36 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 102.42 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 102.52 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 3e-05 | 163.52 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 163.32 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00409 | 118.13 | 104080: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 118.06 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00129 | 116.69 | P23:345:MEC:BLACK HAWK 901 | External | 116.71 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 119.69 | P23:345:MEC:LOUISA 954 | External | 119.54 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.27 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 101.21 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 109.88 | Base Case | External | 109.3 | 0.58
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00255 | 130.8 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | External | 130.76 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.62 | P11:HV:EES::PIRKEY 1:1 | External | 111.52 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00565 | 105.22 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 105.18 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00974 | 106.21 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00191 | 115.44 | P23:345:MEC:KOSSUTH 904 | External | 115.54 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00073 | 154.1 | P23:345:ITCM:HCKRYCK:FUT2 | External | 153.86 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00011 | 117.86 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 117.71 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 149.92 | P12:115:XEL:AUTO-SINGLE:LINDSTM7:GRE-SHAFER7:1 | External | 149.86 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 124.2 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 124.2 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.49 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 101.48 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 102.78 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 102.85 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.77 | 344012 7HPW-N 345 344013 7HPW-S 345 1: 344012 7HPW-N 345 344013 7HPW-S 345 1 | External | 120.62 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 118.32 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 118.21 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 112.96 | P55:345:ATC:ARPIN | External | 112.89 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 105.15 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 100.89 | P12:115:XEL:AUTO-SINGLE:LAWCRK7:GRE-SHAFER7:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533013 MOUND 4 138 997898 MOUN TX-2 115 1 | 250 | 275 | 0.06846 | 121.87 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 121.58 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00329 | 102.32 | 84399: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 102.25 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 124.58 | P13:115-161:ALTW:AUTO-SINGLE:STONPT7:STONPT5:1 | External | 124.48 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 119.91 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 119.88 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.74 | P12:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.78 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15517 | 103.95 | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | Internal | 102.89 | 1.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.01 | P12:HV:EES::PIRKEY 4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 121.91 | P23:345:MEC:SYCAMORE 901 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 104.72 | P23:345:XEL:8N28 SHC | External | 104.84 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00414 | 105.33 | P24:345:AMMO::LABADIE:20H | External | 105.24 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00035 | 107.27 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 107.31 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 113.89 | P23:345:ITCM:HCKRYCK:FUT1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 107.13 | P24:345:XEL:8E7 ECL BS SPS | External | 106.78 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00111 | 111.66 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00202 | 100 | 635640 NORWLK3 345 635641 NORWLK5 161 1: 635640 NORWLK3 345 635641 NORWLK5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 108.48 | 83956: 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 107.02 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 108.09 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 108.4 | -0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.67 | 337909 8ANO% 500 337910 1ANO U1 22 1: 337909 8ANO% 500 337910 1ANO U1 22.0 1 | External | 101.61 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 111.47 | P12:230:GRE:AUTO-SINGLE:GRE-RAMSEY4:GRE-BALTA4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 105.38 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 105.3 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01307 | 121.47 | P23:345:XEL:8S25 WLM AS | External | 121.47 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00053 | 104.19 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00026 | 101.89 | P12:161:ALTW:AUTO-SINGLE:GRMND5:MQOKETA5:1 | External | 101.81 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.2 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.74 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 148.26 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:GLENMONT:1 | External | 148.17 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.78 | 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2: 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2 | External | 120.64 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00386 | 115.92 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 115.86 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 163.73 | P24:345:XEL:8E7 ECL BS | External | 163.66 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 148.18 | P11:345:AMMO::CALLAWAY:1 | External | 148.06 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.04 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 136.46 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 136.53 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 113.04 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 112.99 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 103.46 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 103.41 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00018 | 154.83 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 154.88 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14644 | 127.93 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 126.98 | 0.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00073 | 120.08 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 119.99 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.34 | 631166 NUTHTCH5 161 631171 WHISWIL5 161 1: 631166 NUTHTCH5 161 631171 WHISWIL5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00055 | 100.37 | P23:345:XEL:8S25 WLM AS | External | 100.35 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00648 | 106.81 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 106.71 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 4e-05 | 104.56 | P23:345:MEC:MONTEZUMA 901 | External | 104.47 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00255 | 130.8 | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 130.76 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 116.13 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | External | 116.23 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00232 | 108.95 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | External | 108.99 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00223 | 114.15 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 113.83 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 116.02 | P22:345:MEC:SUB 92 | External | 115.95 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 111.79 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 111.8 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 110.93 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 110.86 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01032 | 110.88 | P23:500:EAI:NBF_SAN SOUC | External | 110.79 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07063 | 118.75 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal | 117.23 | 1.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03485 | 106.48 | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 105.92 | 0.56
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 108.13 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External | 107.7 | 0.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00055 | 103.21 | P12:115:ITCM:STON PT7-PRAR CK7:IA-EC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 105.37 | P22:345:AMMO::LABADIE:3 | External | 105.2 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01264 | 125.43 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997743 NASHUA11 161 11 542980 NASHUA 7 345 997750 NASHUA11 161 11 542980 NASHUA 7 345 997746 NASHUA11 161 11 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07017 | 115.51 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal | 113.96 | 1.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 106.87 | 620245 WILTON 7 115 3WXFMR WILTON 1: 620245 WILTON 7 115 997511 WILTON 69.0 1 657968 WILTON 8 69.0 997511 WILTON 69.0 1 620145 WILTON 9 41.6 997511 WILTON 69.0 1 620245 WILTON 7 115 997518 WILTON 69.0 1 657968 WILTON 8 69.0 997518 WILTON 69.0 1 620145 WILTON 9 41.6 997518 WILTON 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00053 | 108.2 | P23:345:MEC:LOUISA 924 | External | 108.23 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 7e-05 | 147.45 | 105802: 300097 5MARYVL 161 652560 CRESTON5 161 1 631069 ANTA TP5 161 652560 CRESTON5 161 1 635056 ADAMS 5 161 652560 CRESTON5 161 1 635645 MCKSBRG 5 161 652560 CRESTON5 161 1 652560 CRESTON5 161 997144 CS KY3A 69.0 1 652560 CRESTON5 161 997143 CS KY6A 69.0 1 631069 ANTA TP5 161 631070 ANITA 5 161 1 631069 ANTA TP5 161 652603 EXIRA 5 161 1 630381 SLAKEN 8 69.0 652569 CRESTON8 69.0 1 630385 SLAKES 8 69.0 652569 CRESTON8 69.0 1 630419 ECRESTN8 69.0 652569 CRESTON8 69.0 1 652569 CRESTON8 69.0 997144 CS KY3A 69.0 1 652569 CRESTON8 69.0 997143 CS KY6A 69.0 1 652615 CRESTON29 13.8 997143 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997144 CS KY3A 69.0 1 652560 CRESTON5 161 997151 CS KY3A 69.0 1 652560 CRESTON5 161 997150 CS KY6A 69.0 1 652569 CRESTON8 69.0 997151 CS KY3A 69.0 1 652569 CRESTON8 69.0 997150 CS KY6A 69.0 1 652615 CRESTON29 13.8 997150 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997151 CS KY3A 69.0 1 652560 CRESTON5 161 997142 CS KY3A 69.0 1 652560 CRESTON5 161 997141 CS KY6A 69.0 1 652569 CRESTON8 69.0 997142 CS KY3A 69.0 1 652569 CRESTON8 69.0 997141 CS KY6A 69.0 1 652615 CRESTON29 13.8 997141 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997142 CS KY3A 69.0 1 | External | 147.45 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 114 | P23:345:XEL:8N8 MNN | External | 113.96 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 104.67 | P23:345:MEC:GDMEC 902 | External | 104.58 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 104.28 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 104.27 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 121.03 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 121.03 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.28 | P11:24:AEPW:PIRKEY 1 | External | 104.15 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 105.92 | P23:345:ALTW:MITCHLCO:1160 | External | 105.86 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 116.02 | P23:345:MEC:HILLS 934 | External | 115.95 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.11 | 338145 8ISES% 500 338146 1ISES U2 26 1: 338145 8ISES% 500 338146 1ISES U2 26.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.11 | P12:345:XEL:ASK-ECL SPS | External | 126.17 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00108 | 114.14 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 113.96 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01149 | 112.35 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00055 | 106.22 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 106.17 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.9 | P13:500:EES-EAI:INDEP2:MT2 | External | 103.81 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.68 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 108.74 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01134 | 101.13 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | External | 101.03 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0056 | 115.34 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External | 115.24 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 110.15 | P23:345-161:XEL:ADAMS_I:680_S | External | 110.06 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01196 | 125.72 | P23:345:MEC:MORGANV FUT2:IA-EC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 115 | 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1: 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1 | External | 114.37 | 0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00215 | 102.38 | P12:161:WAPA-ALTW:AUTO-SINGLE:ANTATP5:ANITA5:1 | External | 102.26 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 116.41 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 116.4 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00165 | 119.1 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 119.31 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533416 RENO 3 115 533429 MOUNDRG3 115 1 | 218 | 262 | 0.07812 | 129.03 | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 128.32 | 0.71
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 108.41 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 108.39 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.35 | P23:500:EES-EAI:WH_BLF:B7942 | External | 100.3 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.19 | 84371: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 118.12 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 104.15 | 92230: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 104.05 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 110.83 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | Internal | 109.39 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.51 | P11:HV:EES::1RVR_BND_G1!:1 | Internal | 105.07 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00409 | 117.95 | 92252: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External | 117.89 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.54 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | External | 100.36 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 110.73 | P21:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 110.66 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 602029 TREMVAL5 161 681543 ALMA 5 161 1 | 223.1 | 223.1 | 4e-05 | 103.67 | 681543 ALMA 5 161 681545 LUFKIN 161 1: 681543 ALMA 5 161 681545 LUFKIN 161 1 | External | 103.48 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 116.35 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 118.52 | P12:345:XEL:ASAK-ECL SPS | External | 118.52 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00017 | 122.74 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 122.7 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.1733 | 100.16 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.82 | P13:500:EES-EAI:ARK_NU:T2 | Internal | 105.43 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 7e-05 | 129.94 | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1: 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | External | 130.09 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18231 | 153.87 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 152.38 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 108.3 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 108.27 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 107.13 | P12:345:XEL:ASAK-ECL | External | 107.26 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00414 | 127.13 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 126.88 | 0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 121.1 | P23:345:ITCM:SALEM 3 2870:IA-NE | External | 120.94 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 129.63 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 129.45 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 126.95 | P23:345:AMMO::ZACHARY:2 | External | 126.96 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 113.02 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 113.14 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01126 | 142.92 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 142.84 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00193 | 100.47 | P23:345:MEC:SYCAMORE 901 | External | 100.42 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00354 | 126.34 | P23:345:MEC:GDMEC 902 | External | 126.2 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 147.93 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 147.93 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 110.81 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External | 110.97 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.34 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 101.15 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01235 | 121.53 | P24:345:AMMO::LABADIE:20H | External | 121.42 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.98 | P12:345:XEL:ASK-ECL SPS | External | 118.06 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01052 | 111.45 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 111.38 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00012 | 107.02 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 106.82 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00981 | 116.44 | P23:345:GRE:PVS 19JB2 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 7e-05 | 117.42 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 117.46 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 100.67 | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1: 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | External | 100.45 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00156 | 107.2 | 104712: 541253 ST JOE 5 161 541257 COOK 5 161 1 541253 ST JOE 5 161 541258 WOODBIN5 161 1 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 541253 ST JOE 5 161 997777 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997776 ST. JOSEPH33 161 33 541253 ST JOE 5 161 997784 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997783 ST. JOSEPH33 161 33 541253 ST JOE 5 161 997780 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997779 ST. JOSEPH33 161 33 | External | 107.1 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.08 | P13:500:EES-EAI:ARK_NU:T2 | External | 102.05 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.58 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 110.71 | P12:345:XEL:ASAK-ECL SPS | External | 111 | -0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00055 | 113.35 | P12:115:ALTW:AUTO-SINGLE:STONPT7:SQUARED7:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00113 | 114.22 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 114.19 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 105.05 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 105.05 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00985 | 117.58 | P12:345:MEC:TIFFIN-ARNOLD | External | 117.51 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 121.04 | 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1: 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1 | External | 120.94 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00986 | 118.1 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 118.03 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 104.71 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 104.84 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.83 | P23:345:ALTW:MITCHLCO:1150 | External | 106.72 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00998 | 115.01 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03682 | 114.8 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 114.63 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.38 | P12:161:ITCM:AUTOSINGLE:8THST.:GALENA:1 | External | 108.36 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00413 | 124.57 | P23:345:MEC:GDMEC 902 | External | 124.38 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.48 | P11:345:AMMO::RUSHISLAND:U1 | External | 112.36 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.0004 | 107.25 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 107.33 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.15 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 112.08 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.89 | P11:345:AMMO::CALLAWAY:1 | External | 100.95 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01142 | 128.95 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 128.89 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.98 | P24:345:XEL:8E7 ECL BS | External | 104.98 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00123 | 104.56 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 104.59 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 139.04 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 139.07 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.23 | P12:EHV:EES::8SANS SOUCI%:1 | External | 110.12 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00463 | 104.97 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 111.25 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 111.41 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03461 | 106.47 | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | Internal | 106.01 | 0.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 112.29 | P23:345:MEC:BLACK HAWK 901 | External | 112.61 | -0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01049 | 103.1 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 102.79 | 0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06652 | 117.77 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 116.31 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00107 | 109.8 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 109.94 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00981 | 116.07 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 116.07 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 113.28 | P23:345:MEC:LOUISA 954 | External | 113.17 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00998 | 116.57 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 116.51 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00172 | 123.17 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 123.35 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06894 | 106.31 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 104.89 | 1.42
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.47 | 92479: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.26 | P23:345:AEPW:WELSH CB 10630 NBTB | External | 101.2 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 140.92 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 140.97 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 108.13 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 107.99 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 163.48 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 163.56 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01142 | 136.05 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 135.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.7 | 92478: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 7e-05 | 116.72 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 116.74 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00133 | 107.22 | P23:345:XEL:8S27 WLM AS | External | 107.23 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00111 | 115.96 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 115.75 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 117.25 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 116.95 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08885 | 140.68 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 138.89 | 1.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 114.18 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 114.15 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00168 | 120.96 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 120.92 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 105.35 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.27 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 123.72 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 123.47 | 0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 142.01 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 141.89 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00135 | 106.09 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 106.04 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 110.75 | 657747 ASH1 9 34.5 657701 BARNES 4 230 1: 657747 ASH1 9 34.5 657701 BARNES 4 230 1 | External | 110.2 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 118.28 | 84406: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 118.2 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01176 | 133.81 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 133.77 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00098 | 123.15 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 123.03 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 117.98 | P23:345:XEL:8P5 KING | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 113.34 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 113.14 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00329 | 103.05 | 104529: 541205 BLSPE 5 161 541211 BLSPS 5 161 1 541206 PRALEE 5 161 541211 BLSPS 5 161 1 541205 BLSPE 5 161 541226 GRAINVL5 161 1 | External | 102.98 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 109.9 | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1: 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | External | 109.83 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00409 | 104.83 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 104.74 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 123.33 | 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1: 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1 | External | 123.2 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00415 | 103.96 | 81775: 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 512650 GRDA1 7 345 512750 TONECE7 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512688 GRDA17-1 22.8 512650 GRDA1 7 345 1 512650 GRDA1 7 345 998343 GRDAUTO1 161 1 512650 GRDA1 7 345 998351 GRDAUTO1 161 1 512650 GRDA1 7 345 998348 GRDAUTO1 161 1 | External | 103.87 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00409 | 104.83 | P23:345:MEC:MONTEZUMA 901 | External | 104.74 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 110.16 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 106.94 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK | External | 106.32 | 0.62
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01248 | 120.6 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 120.45 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00064 | 108.48 | P23:345:AMMO::ZACHARY:2 | External | 108.54 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 104.52 | P23:345:GRE:PVS 19JB2 | External | 104.46 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00106 | 108 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 108.47 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.76 | P12:345:XEL:ASK-ECL SPS | External | 108.8 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.13 | 85478: 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 | External | 142.23 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00011 | 100.88 | P23:345:ATC:ARPIN:424-S_GD | External | 100.77 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00042 | 169.26 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 169.13 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 126.95 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 126.96 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.32 | 81750: 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | External | 104.34 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00122 | 102.17 | P12:161:MEC:AUTO-SINGLE:POCHNTC5:POMEROY5:1 | External | 102.11 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 102.17 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.22 | P11:EHV:EES::1ANO U2:1 | External | 100.04 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00126 | 115.11 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 115.02 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 106.35 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 106.24 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00412 | 104.04 | P23:500:EES-EAI:INDEP2:B6126 | External | 103.94 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.89 | 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1: 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1 | External | 120.75 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 106.51 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 106.71 | -0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01028 | 114.11 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 114.25 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00295 | 104.65 | P23:345:AMMO::BLAND:V15 | External | 104.58 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 105.35 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.27 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01087 | 112.98 | P23:345:XEL:8S25 WLM AS | External | 112.97 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00074 | 120.66 | P23:345:XEL:8S22 WLM | External | 120.54 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00379 | 114.28 | P22:345:XEL:ADAMS 3 N1:MN | External | 112.62 | 1.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.45 | P12:EHV:EES::8SANS SOUCI%:1 | External | 110.34 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 185.47 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 185.4 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00129 | 102.03 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 101.97 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0019 | 136.74 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 136.66 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 104.59 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 104.71 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15801 | 126.54 | 78001: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 125.35 | 1.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 119.18 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 119.06 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 4e-05 | 157.36 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 157.47 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 129.37 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 129.24 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.6 | P11:HV:EES::1RVR_BND_G1!:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 104.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 104.84 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01087 | 113.22 | P23:345:XEL:8S25 WLM AS | External | 113.22 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 132.38 | Base Case | External | 132.25 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.87 | P11:345:AMMO::LABADIE:3 | External | 112.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00224 | 100.36 | P21:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 100.25 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 112.74 | P12:345:XEL:ASAK-ECL | External | 112.62 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.83 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.84 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00209 | 109.49 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 109.63 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00093 | 122.81 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 122.62 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 105.68 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 105.98 | -0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00191 | 115.44 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 115.54 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00289 | 101.32 | 300088 5HUBEN 161 300042 7HUBEN 345 1: 300088 5HUBEN 161 300042 7HUBEN 345 1 | External | 101.26 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 133.72 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 133.76 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 109.76 | P23:345:MEC:LOUISA 954 | External | 109.63 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00029 | 155.64 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 155.56 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 109.87 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 109.94 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 119.71 | P23:345:MEC:GDMEC 902 | External | 119.6 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 122.98 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 122.98 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.79 | P11:26:EES-EAI:WH_BLF:1:D388 | Internal | 104.5 | 1.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0055 | 113.53 | 104653: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 | External | 113.41 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.87 | P11:20:AMMO:1LAB G2:2 | External | 112.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.02 | 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1: 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1 | External | 100.91 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.0702 | 113.79 | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 112.13 | 1.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.47 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 100.57 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00167 | 100.6 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 100.64 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.47 | 92382: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.42 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 118.67 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 118.68 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00732 | 101.67 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 101.59 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00011 | 115.76 | P12:345:XEL:SPS HNA-SSL | External | 115.75 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 136.85 | P23:345:ALTW:MITCHLCO:1150 | External | 136.62 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00012 | 159.08 | P12:161:DPC:ALM-ROC | External | 159.18 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 110.48 | 608626 BOSWELL4 230 608774 BOSWE43G 20.9 1: 608626 BOSWELL4 230 608774 BOSWE43G 20.9 1 | External | 110.25 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 118.23 | P12:345:XEL:ASK-ECL SPS | External | 118.3 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.08 | 338145 8ISES% 500 338146 1ISES U2 26 1: 338145 8ISES% 500 338146 1ISES U2 26.0 1 | External | 105.91 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.88 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | Internal | 104.5 | 1.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681539 ELK MND5 161 681545 LUFKIN 161 1 | 201 | 221 | 0.00031 | 102.63 | P12:345:XEL:ASAK-ECL | External | 102.8 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 105.05 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 105.05 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.51 | P11:EHV:EES::1ANO U2:1 | External | 106.32 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 7e-05 | 129.24 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 129.2 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 100.99 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 100.71 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.001 | 146.81 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 146.6 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00054 | 103.33 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 116.62 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 116.67 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.93 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 103.9 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00381 | 112.66 | P22:345:AMMO::LABADIE:2 | External | 112.54 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01038 | 112.45 | P23:345-161:XEL:ADAMS_I:680_S | External | 112.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 112.55 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 112.55 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00411 | 104.99 | P24:345:AMMO::LABADIE:15H | External | 104.97 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0002 | 152.42 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9: 601002 ADAMS 3 345 997679 ADAMS 3 161 9 631046 ADAMS 5 161 997679 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997679 ADAMS 3 161 9 601002 ADAMS 3 345 997686 ADAMS 3 161 9 631046 ADAMS 5 161 997686 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997686 ADAMS 3 161 9 601002 ADAMS 3 345 997682 ADAMS 3 161 9 631046 ADAMS 5 161 997682 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997682 ADAMS 3 161 9 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 112.8 | P23:345:MEC:LOUISA 954 | External | 112.28 | 0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 118.03 | P12:EHV:EES::7CALAWY 1:1 | External | 118.03 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 124.58 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 124.48 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 116.62 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 116.57 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00057 | 110.69 | P23:345:MEC:MONTEZUMA 901 | External | 110.67 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00034 | 115.9 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 115.89 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00121 | 118.79 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 118.59 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.47 | 92350: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 113.3 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 113.22 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01028 | 113.9 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 155.5 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 155.56 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00457 | 103.58 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | External | 103.47 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 956 | 1152 | 0.00622 | 111.96 | P23:345:MEC:LOUISA 924 | External | 111.68 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.96 | P11:25:EES:WATERF:1 | Internal | 105.46 | 1.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00408 | 118.01 | 92272: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External | 117.97 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 103.84 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 103.79 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 109.22 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 109.38 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 107.33 | P23:345:MEC:LOUISA 924 | External | 107.48 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0028 | 103.97 | P13:161-345:AMMO::MONTGOMERY:1 | External | 103.91 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 148.52 | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | External | 148.42 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 112.32 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 112.43 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 116.61 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 116.61 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00459 | 108.33 | P23:345:MEC:GDMEC 902 | External | 108.23 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 106.72 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00097 | 119.48 | P12:161:MEC-CBPC:FRANKLIN-HAMPTON-SHEFFIELD | External | 119.29 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00026 | 104.61 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 103.86 | 0.75
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 344001 5ADAIR2 161 631112 APANOSE5 161 1 | 223 | 223 | 0.0004 | 110.44 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 110.38 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 105.5 | 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1: 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1 | External | 105.39 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01087 | 113.23 | P23:345:XEL:8S27 WLM AS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 110.3 | 658109 FERGSFL4 230 3WXFMR 230/115 1: 658109 FERGSFL4 230 997100 230/115 115 1 658110 FERGSFL7 115 997100 230/115 115 1 658111 FERGSFL9 13.2 997100 230/115 115 1 658109 FERGSFL4 230 997107 230/115 115 1 658110 FERGSFL7 115 997107 230/115 115 1 658111 FERGSFL9 13.2 997107 230/115 115 1 658109 FERGSFL4 230 997098 230/115 115 1 658110 FERGSFL7 115 997098 230/115 115 1 658111 FERGSFL9 13.2 997098 230/115 115 1 | External | 110.28 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00012 | 153.92 | 681532 WABACO 5 161 681543 ALMA 5 161 1: 681532 WABACO 5 161 681543 ALMA 5 161 1 | External | 153.98 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00298 | 104.39 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 104.31 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.53 | P11:24:AEPW:TURKCOAL | External | 111.43 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0028 | 103.97 | 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1: 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1 | External | 103.91 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0119 | 125.17 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 125.14 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 122.08 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.05 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.45 | P13:138-24:AEPW:PIRKEY 4 | External | 111.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06947 | 112.48 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 111.01 | 1.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.88 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 104.76 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00014 | 113.89 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 113.26 | 0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.87 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 110.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00172 | 124.91 | P23:345:MEC:SYCAMORE 901 | External | 125.04 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.74 | P24:345:XEL:8E7 ECL BS SPS | External | 108.79 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00986 | 118.1 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 118.03 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0116 | 128.11 | P23:345:AMMO::MONTGOMERY:V43 | External | 127.7 | 0.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 110.25 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 112 | -1.75
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 106.52 | P23:345:MEC:SYCAMORE 901 | External | 106.49 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.68 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 108.74 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.69 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.72 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07059 | 115.26 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 113.77 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 107.12 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 106.57 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 119.57 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 119.53 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00145 | 106.74 | P23:345:XEL:SPS 8S81 SSL | External | 106.79 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 116.68 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00014 | 105.14 | P23:345-161:XEL:ADAMS_I:681_S | External | 105.08 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 111.67 | P12:115:OTP-GRE::BIGSTON7:TORONTO7 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00834 | 135.76 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 135.48 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 114.01 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 114 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01142 | 136.37 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 136.31 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 115.12 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External | 115.01 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 147.4 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 147.32 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.43 | P11:HV:EES::1GYP_U4 G1:1 | External | 100.39 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.15 | P11:345:OPPD:NEBCTY1G:LT | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 103.94 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 104.27 | -0.33
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.79 | P23:345:XEL:8N8 MNN | External | 112.58 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01126 | 149.55 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 149.47 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.07 | 84372: 541261 STALEY 2 69.0 541262 LIBERTY2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 118.01 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.95 | 92386: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 103.84 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00022 | 108.19 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 108.1 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.94 | P11:25:EES:WATERF:1 | External | 100.75 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 114.77 | P11:024:DPC:ALMA2:6 | External | 114.95 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.05 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External | 101.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.91 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 108.96 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 115.2 | P23:345:ALTW:MITCHLCO:1130 | External | 115.3 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05229 | 101.57 | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | Internal | 100.41 | 1.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00135 | 114.1 | P23:345:XEL:8S27 WLM AS | External | 114.12 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00027 | 104.49 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 104.43 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00034 | 108.99 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | External | 108.9 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 110.5 | P11:345:AMMO::CALLAWAY:1 | External | 110.41 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 113.66 | P12:345:XEL:ASAK-ECL | External | 114.32 | -0.66
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.67 | P12:345:XEL:ASAK-ECL SPS | External | 117.83 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 115.11 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 114.85 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 135.2 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 135.16 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00067 | 102.21 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 102.19 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.41 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 118.56 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.8 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 108.68 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00076 | 128.54 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 128.22 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 111.82 | P23:345:ALTW:MITCHLCO:1130 | External | 112 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00067 | 130.97 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 131.02 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.45 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 108.29 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | Internal | 106.8 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.7 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07057 | 120.37 | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | Internal | 118.89 | 1.48
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01134 | 110.82 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | External | 110.72 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01248 | 124.21 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 124.15 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 118.21 | P24:345:XEL:8E7 ECL BS | External | 118.29 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01247 | 129.8 | P23:345:MEC:BLACK HAWK 901 | External | 129.96 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 2 | 500 | 500 | 0.00037 | 105.66 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 105.63 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 100.32 | 631075 CARBIDE5 161 630006 CARBIDE8 69 1: 631075 CARBIDE5 161 630006 CARBIDE8 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00521 | 117.37 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 117.28 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 107 | P11:EHV:EES::1ANO U2:1 | Internal | 105.55 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 133.18 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 133.2 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 117.88 | P12:345:XEL:ASK-ECL SPS | External | 117.9 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 185.47 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 185.4 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00066 | 103.08 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 103 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 107.67 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.65 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00018 | 100.34 | P23:345:MEC:LOUISA 954 | External | 100.27 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01038 | 112.22 | P23:345-161:XEL:ADAMS_I:681_S | External | 112.14 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.11 | 601014 AS KING3 345 600006 KING 31G 20 1: 601014 AS KING3 345 600006 KING 31G 20.0 1 | External | 142.16 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00044 | 116.87 | P23:345:AMMO::MONTGOMERY:V43 | External | 117.55 | -0.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 117.89 | P23:345:XEL:8P6 KING | External | 118.53 | -0.64
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 110.2 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 110.13 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.88 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 103.81 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00146 | 104.26 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | External | 104.1 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00151 | 113.91 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 113.85 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00042 | 103.98 | P42:345:NPPD:BKR-CPR-3304 | External | 104.89 | -0.91
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.65 | P12:345:XEL:ASK-ECL SPS | External | 118.19 | 0.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00985 | 117.81 | P12:345:MEC:TIFFIN 9T1 SPS | External | 117.73 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.67 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 108.71 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00042 | 169.26 | P23:345:XEL:8P6 KING | External | 169.13 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01263 | 120.11 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 120.02 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 117.79 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 117.73 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00732 | 111.61 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 111.52 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.05 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 123.29 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 123.03 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 114.09 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00029 | 101.36 | P23:345:MEC:OAK GROVE 904 | External | 101.33 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 106.08 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 106.03 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.74 | P24:345:XEL:8E7 ECL BS | External | 108.79 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.09 | 631048 EMERY 5 161 629069 EMERYST1 18 1: 631048 EMERY 5 161 629069 EMERYST1 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00167 | 100.6 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 100.64 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00031 | 103.15 | P23:345:MEC:LOUISA 924 | External | 102.95 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 121.74 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 121.68 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00118 | 110.98 | P23:345:MEC:OAK GROVE 904 | External | 111.04 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00111 | 104.65 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00073 | 154.1 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 153.86 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 158.9 | 681532 WABACO 5 161 681537 ROCHSTR5 161 1: 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | External | 158.92 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.52 | P22:345:AMMO::LABADIE:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00998 | 116.57 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 116.51 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.64 | P12:HV:EES::TURK 4%:1(1) | External | 101.54 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01049 | 112.89 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00113 | 113.3 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 113.46 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.51 | 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z: 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z | External | 110.39 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 9e-05 | 119.01 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 118.97 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.28 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 104.16 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06877 | 109.57 | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 108.18 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00029 | 155.64 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 155.56 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 111.3 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 108.26 | P11:21:EES:RVB:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.74 | P23:500:AEPW-EES:ABF_HTBG-A | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00986 | 117.8 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 117.73 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.17 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 142.2 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 105.95 | 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26 1: 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26.0 1 | External | 105.72 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00288 | 117.17 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 117.14 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 123.48 | 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1: 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1 | External | 123.36 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00378 | 116.07 | P24:345:AMMO::RUSHISLAND:V6 | External | 115.99 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00384 | 103.9 | 300226 2HICKRY 69 300087 5HICKCK 161 1: 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | External | 103.79 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00471 | 121.75 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 121.63 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.58 | 92461: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 | External | 100.68 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.24 | P11:22:EES-EAI:ARK_NU:1 | External | 102.18 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00011 | 115.8 | P23:345:XEL:SPS 8S81 SSL | External | 115.78 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01001 | 114.65 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | External | 114.69 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00064 | 108.48 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 108.54 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.08 | P24:345:XEL:8E7 ECL BS | External | 126.17 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 105.89 | P23:345:MEC:CBEC 908 | External | 105.35 | 0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.22 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z: 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | External | 111.11 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01142 | 128.95 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 128.89 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00153 | 104.15 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | External | 104.03 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00114 | 108.38 | 631059 8TH ST.5 161 681520 GALENA 5 161 1: 631059 8TH ST.5 161 681520 GALENA 5 161 1 | External | 108.36 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00985 | 117.87 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 117.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00224 | 100.36 | P12:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 100.25 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00023 | 142.74 | P23:500:EMI-EES:ABF_FRKLN-A | External | 142.73 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 119.67 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 119.63 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.77 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 150.79 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00331 | 114.69 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 114.71 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 112.99 | P12:345:XEL:SPS HNA-SSL | External | 112.93 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 158.9 | P12:161:DPC:AUTO-SINGLE:WABACO5:ROCHSTR5:1 | External | 158.92 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 111.59 | P12:230:GRE:AUTO-SINGLE:GRE-RAMSEY4:GRE-RMSYCB14:Z | External | 111.91 | -0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00565 | 105.22 | P22:345:MEC:SUB 92 | External | 105.18 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 122.09 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 121.97 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.24 | P11:EHV:EES::1ANO U2:1 | External | 102.18 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00172 | 123.17 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 123.35 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00123 | 104.64 | P24:345:XEL:8E7 ECL BS | External | 104.65 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00021 | 152.5 | P23:345:MEC:MONTEZUMA 901 | External | 152.5 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.69 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External | 112.34 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 116.15 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 116.05 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 109.39 | Base Case | External | 109.28 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15801 | 126.97 | 78002: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 126.16 | 0.81
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 104.67 | P23:345:MEC:GDMEC 901 | External | 104.57 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 118.25 | P11:345:AMMO::CALLAWAY:1 | External | 118.15 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.66 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 141.68 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 104.79 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.76 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00069 | 144.05 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 144.1 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00049 | 114.56 | P23:345:XEL:8P5 KING | External | 114.45 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.1 | P13:500:EES-EAI:ARK_NU:T2 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 123.29 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 123.03 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01524 | 124.74 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 124.68 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0027 | 128.86 | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | External | 128.78 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0091 | 112.22 | P23:345:MEC:ATCHISON CO 903 | External | 112.1 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01045 | 115.98 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 115.91 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00517 | 108.93 | 104628: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 300082 5GEORGE 161 541209 SEDALIA5 161 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541271 SEDN 2 69.0 541273 KELHYS 2 69.0 1 | External | 108.85 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 160.85 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00111 | 107.42 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 107.27 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00109 | 105.89 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 134.02 | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 133 | 1.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533035 CHISHLM4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03682 | 109.69 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal | 109.52 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06422 | 108.81 | P12:138:ITCGP:FLATRIDGE-THISTLE:: | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00362 | 101.4 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 101.27 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 105.81 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 105.8 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 140.57 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 140.46 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0053 | 128.44 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 128.36 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 107.64 | 81751: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | Internal | 106.3 | 1.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.73 | P23:500:EAI:NBF_WHITE ~1 | Internal | 104.27 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 118.21 | P23:345:XEL:8P6 KING | External | 118.05 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 141.23 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 141.16 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00097 | 119.48 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 119.29 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 120.98 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 120.79 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00404 | 107.15 | 300336 2HOLDEN 69 300124 5HOLDEN 161 1: 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | External | 107.05 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00051 | 100.14 | P23:345-161:XEL:ADAMS_I:681_S | External | 100.07 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01126 | 149.34 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 149.26 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 135.62 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 135.67 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01038 | 111.1 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00167 | 100.6 | P23:345:MEC:MONTEZUMA 901 | External | 100.64 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00565 | 105.22 | P23:345:MEC:HILLS 934 | External | 105.18 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00173 | 113.93 | 620362 OAKES 4 230 620363 FORMAN 4 230 1: 620362 OAKES 4 230 620363 FORMAN 4 230 1 | External | 114.18 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.19 | P11:24:AEPW:TURKCOAL | External | 100.07 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00352 | 130.29 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 130.27 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 150.74 | 603065 CHISAGO7 115 605269 LINDSTM7 115 1: 603065 CHISAGO7 115 605269 LINDSTM7 115 1 | External | 150.66 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00111 | 112.48 | P23:345:MEC:TIFFIN 944 | External | 111.53 | 0.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00163 | 123.56 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 123.51 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 147.97 | P23:345:MEC:MONTEZUMA 901 | External | 148.15 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 109.84 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 109.77 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.01 | 84491: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 117.96 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.53 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 146.53 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.16 | P11:345:AMMO::CALLAWAY:1 | External | 101.08 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00062 | 141.28 | P23:345:MEC:MONTEZUMA 901 | External | 141.38 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 106.58 | 631075 CARBIDE5 161 630006 CARBIDE8 69 1: 631075 CARBIDE5 161 630006 CARBIDE8 69.0 1 | External | 106.42 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.21 | P11:HV:EES::1WAT U3!:1 | External | 104.17 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 108.07 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 108.32 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00453 | 113.01 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 113.35 | -0.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 107.91 | 83954: 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 524043 NICHOLS 3 115 524021 NICHOLS_1 1 13.8 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 106.34 | 1.57
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00053 | 108.2 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 108.09 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 110.15 | P23:345-161:XEL:ADAMS_I:681_S | External | 110.06 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01087 | 103.62 | P23:345:XEL:8S25 WLM AS | External | 103.63 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 110.47 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 110.47 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.24 | P11:24:AEPW:TURKCOAL | External | 104.11 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 103.25 | Base Case | Internal | 101.81 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00207 | 113.16 | P23:345:XEL:SPS 8S81 SSL | External | 113.29 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00186 | 104.15 | 345027 5MARIOSA 161 345238 7MARIOSA 345 1: 345027 5MARIOSA 161 345238 7MARIOSA 345 1 | External | 104.14 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.0689 | 109.66 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal | 107.96 | 1.7
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 103.66 | P23:345:MEC:HILLS 984 | External | 103.58 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 114.36 | P23:345:XEL:8N28 SHC | External | 114.2 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997578 345-161 161 1 | 500 | 500 | 0.00037 | 104.72 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 104.68 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 111.5 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 111.42 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00014 | 114.08 | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00124 | 104.33 | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1: 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | External | 104.1 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00165 | 119.1 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 119.31 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.46 | P11:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00327 | 106.17 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00032 | 102.21 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 102.14 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 101.2 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16673 | 121.45 | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 120.4 | 1.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.76 | P23:345:GRE:CHL 304JB22 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06899 | 106.41 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Internal | 104.96 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 111.53 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 111.46 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00055 | 100.24 | P12:345:XEL:SPS WLM-SSL | External | 100.2 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 141.29 | 620327 HANKSON4 230 620329 WAHPETN4 230 1: 620327 HANKSON4 230 620329 WAHPETN4 230 1 | External | 141.51 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.87 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 103.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 109.04 | 92665: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514941 HSL 4 138 514944 HSL 9G 13.8 1 514941 HSL 4 138 514945 HSL 10G 13.8 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514941 HSL 4 138 514936 HSL 7S 20.9 1 514941 HSL 4 138 514939 HSL 8G 22.8 1 514927 HSLEAST2 69.0 514938 HSL 7G 13.2 1 514941 HSL 4 138 514935 HSL 6G 17.1 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00453 | 113.47 | P23:345:MEC:MONTEZUMA 901 | External | 113.41 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00117 | 115.81 | P21:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 115.81 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 110.74 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 110.74 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01245 | 124.52 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 124.5 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 7e-05 | 116.72 | P23:345:XEL:8M54 SCO | External | 116.71 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00113 | 113.36 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 113.32 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00079 | 118.07 | P23:345:AMMO::ZACHARY:2 | External | 117.9 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 125.26 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 125.14 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.08 | P12:EHV:EES::8ANO%:1(1) | External | 102.05 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997578 345-161 161 1 | 500 | 500 | 0.00037 | 106.34 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 106.3 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06947 | 112.58 | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 111.2 | 1.38
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00067 | 119.55 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 119.37 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00043 | 128.41 | P12:345:XEL:ASAK-ECL | External | 128.58 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 118.01 | P23:345:XEL:8P5 KING | External | 118.23 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 131.31 | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 130.29 | 1.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00126 | 109.39 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 109.37 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07059 | 115.48 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 113.94 | 1.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.85 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 153.02 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00079 | 118.07 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 117.9 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 115.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 115.01 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 104.66 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 104.69 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.83 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.84 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00671 | 110.73 | P23:345:MEC:SUB 56 934 OR 937 | External | 110.65 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 109.04 | 104894: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00219 | 102.34 | P12:161:WAUW:# 3102 #: TI IN MT. TI-TT-SH2 & TT-RY-HV | External | 102.16 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.24 | P22:345:OPPD:S3458 NEBCTY1G | External | 103.21 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00027 | 104.49 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00116 | 104.56 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External | 104.61 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00145 | 106.75 | P12:345:XEL:SPS WLM-SSL | External | 106.81 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 105.34 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 105.27 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 115.15 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 115.01 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 108.24 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 108.16 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0056 | 115.34 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External | 115.24 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00409 | 104.83 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 104.74 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01039 | 101.34 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.21 | 92666: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External | 100.2 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0006 | 141.77 | P23:345:XEL:8M54 SCO | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997578 345-161 161 1 | 500 | 500 | 0.00037 | 104.72 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 104.68 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 7e-05 | 129.24 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 129.2 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.0013 | 102.34 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 102.39 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 135.63 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1:::: | External | 135.66 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06899 | 105.94 | P23:345:MEC:GDMEC 901 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00127 | 100.13 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 100.04 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00985 | 117.52 | P12:345:MEC:TIFFIN 9T1 SPS | External | 117.44 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 107.99 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 108.34 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 112.32 | P11:115:XEL:HBR #6 7 8 | External | 112.18 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00414 | 103.47 | P46:345:GRDA:GRDA CB400T | External | 103.37 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.32 | P13:138-24:AEPW:TURK 4 | External | 111.22 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 105.02 | P23:345:ALTW:MITCHLCO:1130 | External | 105.11 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.62 | P23:345:ALTW:MITCHLCO:1140 | External | 106.5 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 141.36 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 141.34 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 147.62 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 147.59 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.22 | P22:345:OPPD:S3458 NEBCTY2G | External | 103.2 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00031 | 119.59 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 119.75 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00985 | 117.58 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 117.51 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 104.4 | 345409 5OVERTON 161 346117 2OVERTON 69 1: 345409 5OVERTON 161 346117 2OVERTON 69.0 1 | External | 104.34 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 5e-05 | 116.84 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | External | 116.79 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01037 | 108.06 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 107.99 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00072 | 153.41 | P23:345:ITCM:SALEM 3 2835:IA-NE | External | 153.12 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 103.86 | 105856: 648516 GRPR11 9 34.5 645065 GRPR11 W 0.69 1 648523 GRPR21 9 34.5 645067 GRPR21 W 0.69 1 648519 GRPR12 9 34.5 645066 GRPR12 W 0.69 1 648513 GRPR1 3 345 648520 GRPR2 3 345 1 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 648513 GRPR1 3 345 997246 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997245 GRPR1 TFMR 2 34.5 1 648526 GRPR22 9 34.5 645068 GRPR22 W 0.69 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z 652532 GR PRAIRIE 3 345 579457 G16-075XFMR1 34.5 1 648514 GRPR11X9 34.5 648516 GRPR11 9 34.5 Z1 648514 GRPR11X9 34.5 997246 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997246 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997244 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997245 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997244 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997243 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997243 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997253 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997252 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997253 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997253 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997251 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997252 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997251 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997250 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997250 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997244 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997243 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997244 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997244 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997242 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997243 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997242 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997241 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997241 GRPR2 TFMR 2 34.5 1 | External | 103.82 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 115.23 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 115.33 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.68 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1: 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06983 | 123.92 | 78001: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 122.49 | 1.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 110.9 | P11:115:XEL:HBR #6 7 8 | External | 110.68 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 111.16 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 111.28 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 122.76 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 122.73 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01241 | 125.82 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 125.76 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 137.34 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 137.51 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.19 | 346004 7GOSCK 345 3WXFMR GSK2 GSU 1: 346004 7GOSCK 345 998844 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998844 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998844 GSK2 GSU 13.8 1 346004 7GOSCK 345 998847 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998847 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998847 GSK2 GSU 13.8 1 346004 7GOSCK 345 998851 GSK2 GSU 13.8 1 346000 1GOSCK 3 13.8 998851 GSK2 GSU 13.8 1 346001 1GOSCK 4 13.8 998851 GSK2 GSU 13.8 1 | External | 110.09 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.69 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 100.68 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 107.21 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 107.24 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 157.65 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 157.58 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.24 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16673 | 121.45 | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 120.4 | 1.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.38 | 92479: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 106.49 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.61 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00352 | 130.29 | P23:345:MEC:MONTEZUMA 901 | External | 130.27 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01028 | 105.38 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 131.97 | P23:345:MEC:GDMEC 901 | External | 131.88 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14606 | 125.22 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 124.24 | 0.98
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 124.51 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 124.42 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 601050 HELENA 3 345 615649 GRE-CHUBLAK3 345 1 | 1792.6 | 1792.6 | 0.00443 | 100.08 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 100.03 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.67 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 134.67 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0016 | 135.81 | P23:345:XEL:SPS 8S81 SSL | External | 135.88 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 136.46 | P23:345:MEC:MONTEZUMA 901 | External | 136.53 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0116 | 128.3 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 128.17 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00085 | 100.71 | 300165 4SFORKK 138 301339 4SFORKKTP 138 1: 300165 4SFORKK 138 301339 4SFORKKTP 138 1 | External | 100.66 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01028 | 113.9 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 114.03 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00168 | 120.96 | P23:345:AMMO::ZACHARY:2 | External | 120.92 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01028 | 115.06 | P23:345:XEL:8E5 ECL BS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.59 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 101.55 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00111 | 115 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 114.77 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 119.13 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 119.23 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 119.18 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 119.06 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07025 | 118.52 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal | 117.07 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00111 | 106.32 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 106.28 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533013 MOUND 4 138 997898 MOUN TX-2 115 1 | 250 | 275 | 0.06846 | 121.87 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 121.58 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.35 | 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26 1: 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26.0 1 | External | 100.3 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.55 | P11:21:EES:RVB:1 | External | 100.37 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00985 | 109 | P23:345:MEC:TIFFIN 944 | External | 108.94 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00064 | 113.08 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 113 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 133.43 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 133.47 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 101.87 | 631109 BRLGTN 5 161 630038 BRLGTN28 69 1: 631109 BRLGTN 5 161 630038 BRLGTN28 69.0 1 | External | 101.98 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00132 | 109.35 | 636050 WRIGHT 5 161 636051 WRIGHT 8 69 1: 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 116.22 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 116.63 | -0.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 125.74 | 631110 WAPELLO5 161 631112 APANOSE5 161 1: 631110 WAPELLO5 161 631112 APANOSE5 161 1 | External | 125.4 | 0.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 138.16 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 138.02 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00083 | 105.12 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 105.14 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 2e-05 | 118.26 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 118.76 | -0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00039 | 170.2 | P23:345:XEL:8P5 KING | External | 169.91 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 112.78 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1 | External | 112.15 | 0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 111.53 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 111.46 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.28 | P11:HV:EES::PIRKEY 1:1 | External | 104.15 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06905 | 111.53 | P12:115:MKEC:MEDICINELODGE-SHOOTINGSTARTAP:: | Internal | 110.07 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.3 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 100.25 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 4e-05 | 157.36 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 157.47 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01234 | 119 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 118.85 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 114.77 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 114.95 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00058 | 111.59 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 112.04 | -0.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06961 | 111.9 | 830510: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 110.45 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 111.87 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 111.83 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 125.01 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 124.91 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.11 | 601003 PR ISLD3 345 600004 PR IS32G 20 1: 601003 PR ISLD3 345 600004 PR IS32G 20.0 1 | External | 141.18 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 101.36 | P24:345:AMMO::LABADIE:15H | External | 101.31 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00169 | 102.44 | P23:345-161:XEL:ADAMS_I:680_S | External | 102.42 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 245.29 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 245.28 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00022 | 153.66 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 153.57 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00152 | 114.79 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 114.79 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.19 | 346004 7GOSCK 345 3WXFMR GSK3 GSU 1: 346004 7GOSCK 345 998843 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998843 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998843 GSK3 GSU 13.8 1 346004 7GOSCK 345 998846 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998846 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998846 GSK3 GSU 13.8 1 346004 7GOSCK 345 998850 GSK3 GSU 13.8 1 346002 1GOSCK 5 13.8 998850 GSK3 GSU 13.8 1 346003 1GOSCK 6 13.8 998850 GSK3 GSU 13.8 1 | External | 110.09 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 101.91 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 101.89 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 120.34 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00985 | 119.17 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 120.49 | -1.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00209 | 101.81 | P23:345:MEC:SYCAMORE 905 | External | 101.78 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 119.72 | P23:345:MEC:GDMEC 901 | External | 119.64 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00131 | 128.58 | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1: 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | External | 128.34 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.18 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 142.21 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 115.92 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 115.37 | 0.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00453 | 113.47 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 113.41 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.08 | P12:EHV:EES::8ISES%:1 | External | 105.91 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 105.68 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3 | External | 105.97 | -0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.64 | P13:138-24:AEPW:TURK 4 | External | 101.54 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00116 | 113.4 | P23:345:ITCM:SALEM 3 215:IA-NE | External | 113.2 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00057 | 110.06 | P13:161-345:ALTW:AUTO-SINGLE:HUNTLEY5:HUNTLEY3:1 | External | 109.77 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00035 | 113.81 | P23:345:MEC:HILLS 9114 | External | 113.68 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 112.95 | P12:230:GRE-OTP:AUTO-SINGLE:GRE-RMSYCB24:PRAIRIE4:1 | External | 112.83 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.88 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00018 | 104.77 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 104.37 | 0.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 136.63 | P23:345:ALTW:MITCHLCO:1140 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00025 | 103.11 | P12:345:XEL:ASK-ECL SPS | External | 103.1 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.00293 | 132.03 | P23:345:MEC:SYCAMORE 905 | External | 131.98 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 126.95 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 126.96 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 118.28 | 104647: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 118.2 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 100.53 | 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z: 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z | External | 100.39 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00228 | 128.71 | 104651: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 128.66 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00108 | 141.87 | 105985: 656191 HAMPTON5 161 656207 HAMPTONTAP5 161 1 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 636230 FRANKLN5 161 656207 HAMPTONTAP5 161 1 | External | 141.67 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.05 | P12:HV:EES::PIRKEY 4:1 | External | 103.94 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01038 | 112.45 | P23:345-161:XEL:ADAMS_I:681_S | External | 112.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00381 | 112.68 | P22:345:AMMO::LABADIE:1 | External | 112.55 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00412 | 104.95 | P24:345:AMMO::LABADIE:8H | External | 104.84 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.7 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18 1: 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00545 | 115.18 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 115.16 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15801 | 124.01 | 78002: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 123.14 | 0.87
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.166 | 120.56 | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 119.26 | 1.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00271 | 102.09 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997749 HAWTHORN20 161 20 543665 HAWTHN5 161 997748 HAWTHORN22 161 22 543665 HAWTHN5 161 997756 HAWTHORN20 161 20 543665 HAWTHN5 161 997755 HAWTHORN22 161 22 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | External | 102.15 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 115.85 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 115.94 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.53 | 92369: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 102.46 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 116.46 | P23:345:MEC:LOUISA 924 | External | 116.25 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 110.56 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 111.06 | -0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00108 | 141.87 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 141.67 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00098 | 117.02 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 117 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.3 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 100.25 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00502 | 104.5 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 2e-05 | 117.25 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 117.3 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00035 | 104.4 | P23:345:MEC:HILLS 9114 | External | 104.28 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 1e-05 | 155.63 | 300076 5FAIRPT 161 300039 7FAIRPT 345 3: 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | External | 155.59 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.67 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 117.83 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.12 | P23:345:ALTW:MITCHLCO:1140 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 111.3 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.66 | P12:345:XEL:ASAK-ECL | External | 103.61 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 119.67 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 119.63 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00223 | 114.15 | P23:345:AMMO::ZACHARY:2 | External | 113.83 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 113.34 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 113.47 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00338 | 104.11 | P23:345:WERE:N345_345-80:: | External | 104.01 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 101.03 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 100.75 | 0.28
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00052 | 113.96 | P23:345:XEL:8P6 KING | External | 113.88 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 106.51 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.8 | P23:345:ITCM:HCKRYCK:5268-PRESENT | External | 152.87 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00119 | 124.03 | P21:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 124.02 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 133.5 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 132.46 | 1.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.0005 | 119 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 119.35 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.3 | P11:24:AEPW:TURKCOAL | External | 111.2 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.47 | 92424: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.42 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00147 | 100.09 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 122.68 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 122.65 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 114.15 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 114.24 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 133.2 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 133.24 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.28 | 81750: 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | External | 100.29 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.03491 | 119.65 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 119.31 | 0.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00061 | 152.51 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 152.33 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01176 | 133.81 | P23:345:AMMO::ZACHARY:2 | External | 133.77 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15517 | 106.43 | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | Internal | 105.29 | 1.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00126 | 109.19 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 109.14 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.00459 | 108.34 | P23:345:MEC:GDMEC 901 | External | 108.25 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 163.43 | P12:345:XEL:ASAK-ECL SPS | External | 163.5 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00031 | 109.24 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 110.04 | -0.8
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00983 | 115.48 | P23:345:ALTW:MITCHLCO:1130 | External | 115.59 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 114.24 | P12:345:XEL:ASAK-ECL | External | 114.32 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00097 | 121.28 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 121.16 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00025 | 126.29 | P12:230:OTP::BIGSTON4:HANKSON4 | External | 126.33 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00014 | 126.68 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 126.49 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00328 | 131.5 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 131.62 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00125 | 110.96 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 111.4 | -0.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00221 | 146.63 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 146.77 | -0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00459 | 106.51 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 106.39 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.09 | P12:EHV:EES::8WHT BLUFF%:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 110.9 | P24:345:XEL:8E7 ECL BS | External | 110.6 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01052 | 111.45 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 111.38 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 122.02 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 121.91 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00014 | 105.14 | P23:345-161:XEL:ADAMS_I:680_S | External | 105.08 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.96 | P13:230:EES:WATERF:T6:T7 | External | 101.87 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05277 | 101.52 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 101.3 | 0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01176 | 133.62 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 133.58 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.98 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 155.5 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 155.56 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01447 | 119.82 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | External | 119.69 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.21 | P12:HV:EES::TURK 4%:1(1) | External | 100.09 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 112.86 | P12:115:OTP-GRE::BIGSTON7:TORONTO7 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.29 | P11:345:OPPD:NEBCTY1G | External | 103.26 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 111.5 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 111.85 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00035 | 104.22 | P23:345:GRE:PVS 19JB3 | External | 104.2 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01142 | 128.95 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 128.89 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 119.57 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 119.53 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 119.67 | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | External | 119.63 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.56 | P12:EHV:EES::7CALAWY 1:1 | External | 106.27 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00132 | 112.43 | 636050 WRIGHT 5 161 636051 WRIGHT 8 69 1: 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | External | 112 | 0.43
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00016 | 116.97 | P23:345:ITCM:SALEM 3 215:IA-NE | External | 116.77 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0004 | 245.29 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 245.28 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.53 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 114.66 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0001 | 150.03 | P23:345:MEC:LOUISA 954 | External | 150.04 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 113.56 | 84403: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 113.48 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.38 | P12:345:XEL:ASAK-ECL SPS | External | 118.51 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.62 | P11:HV:EES::TURKCOAL:1 | External | 101.53 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00132 | 107.31 | P12:161:MEC:AUTO-SINGLE:HAYES5:POMEROY5:1 | External | 107.3 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00152 | 111.04 | P23:345:XEL:SPS 8S81 SSL | External | 111.1 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 117.79 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 117.73 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 149.76 | 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1: 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 149.66 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 105.62 | 620314 BIGSTON4 230 3WXFMR BSP 230 1: 620314 BIGSTON4 230 997504 BSP 230 115 1 620316 BIGSTON9 13.8 997504 BSP 230 115 1 620314 BIGSTON4 230 997512 BSP 230 115 1 620316 BIGSTON9 13.8 997512 BSP 230 115 1 620314 BIGSTON4 230 997505 BSP 230 115 1 620316 BIGSTON9 13.8 997505 BSP 230 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 110.73 | P12:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 110.66 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 124.61 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 124.51 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.06 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 110.99 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 117.64 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 117.72 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 131.05 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 130.01 | 1.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00069 | 132.49 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 131.99 | 0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00011 | 103.22 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 103.19 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00051 | 104.88 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 104.44 | 0.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.99 | P11:21:EES:RVB:1 | External | 106.79 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01107 | 127.75 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | External | 128.16 | -0.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.38 | 92350: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 106.49 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 111.25 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 111.41 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00671 | 113.75 | P23:345:MEC:WALCOTT 934 | External | 113.74 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 119.57 | P23:345:AMIL::SANDBURG:3 | External | 119.4 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 113.59 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01239 | 121.72 | P24:345:AMMO::LABADIE:8H | External | 121.68 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 121.05 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 120.96 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01025 | 107.58 | P12:345:XEL:ASK-ECL SPS | External | 107.64 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01164 | 126.97 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | External | 127.01 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00166 | 114.36 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 114.34 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00022 | 116.72 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 116.59 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00027 | 117.69 | P12:161:ITCM-DPC:LORE5-STONEMAN5:IA-NE | External | 117.59 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00171 | 122.08 | P23:345:MEC:GDMEC 901 | External | 122.03 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 123.92 | P23:345:ALTW:MITCHLCO:1160 | External | 123.83 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.38 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 106.49 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 114.28 | P12:345:XEL:ASK-ECL SPS | External | 114.5 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01142 | 128.95 | P23:345:MEC:MONTEZUMA 902 | External | 128.89 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05798 | 100.85 | 40231: 530580 PAWNEE 2 69.0 530585 BAZINE 2 69.0 1 530585 BAZINE 2 69.0 530700 WALNTCRK3 69.0 1 530580 PAWNEE 2 69.0 530598 CHSPIP 2 69.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01228 | 123.47 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 123.41 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00017 | 102.93 | P23:345:MEC:LOUISA 924 | External | 103.09 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00025 | 103.4 | P23:345:XEL:8P5 KING | External | 103.09 | 0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01539 | 123.9 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 123.85 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01227 | 124.53 | P12:345:XEL:ASAK-ECL | External | 124.55 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.47 | P13:500:EES-EAI:INDEP2:MT2 | External | 101.42 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00119 | 124.03 | P12:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 124.02 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00127 | 107.15 | 636235 WALL LK5 161 636236 WALL LK8 69 1: 636235 WALL LK5 161 636236 WALL LK8 69.0 1 | External | 106.94 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00122 | 119.57 | P23:345:AMIL::SANDBURG:1 | External | 119.4 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 6e-05 | 114.46 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01038 | 110.86 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.55 | P12:HV:EES::PIRKEY 4:1 | External | 101.47 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.86 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 111.8 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 110.91 | 92666: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal | 109.5 | 1.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 117.91 | P12:345:XEL:ASAK-ECL SPS | External | 118.07 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00165 | 119.1 | P23:345:MEC:MONTEZUMA 901 | External | 119.31 | -0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00061 | 127.39 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 127.3 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01026 | 105.26 | P12:345:XEL:ASAK-ECL | External | 105.43 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00564 | 113.78 | 104253: 542969 STILWEL5 161 543126 LACKMAN5 161 1 300071 5CLINTN 161 542969 STILWEL5 161 1 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | External | 113.64 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 119.57 | Base Case | External | 119.43 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 124.83 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 124.91 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00083 | 120.13 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 119.94 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.83 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.84 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.51 | 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26 1: 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26.0 1 | External | 103.42 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.53 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | Internal | 105.07 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 104.78 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.76 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00121 | 119.97 | P23:345:MEC:OAK GROVE 903 | External | 118.88 | 1.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0006 | 107.1 | P12:345:AMIL-MEC::OAKGROVE:SANDBURG:1 | External | 107.15 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05916 | 106.71 | 78002: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 105.22 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 128.19 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 128.27 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 106.35 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 6e-05 | 113.34 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 113.9 | -0.56
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00112 | 113.1 | P23:345:GRE:PVS 19JB2 | External | 113.2 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.87 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.79 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00073 | 154.1 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 153.86 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.8 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.83 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15188 | 101.23 | Base Case | Internal | 100.08 | 1.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.01 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 104.08 | P23:345:ALTW:MITCHLCO:1150 | External | 103.74 | 0.34
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00147 | 118.11 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 117.91 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00215 | 100.95 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 100.88 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01069 | 103.45 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 103.38 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00094 | 127.59 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 127.36 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.29 | P23:345:ALTW:MITCHLCO:1160 | External | 112.11 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 110.74 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 110.74 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00075 | 117.5 | P23:345:AMIL::SANDBURG:1 | External | 117.47 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00047 | 104.82 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 111.47 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 111.46 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 105.19 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 105.14 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.96 | P11:HV:EES::1WAT U3!:1 | External | 101.88 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.11 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 125.94 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00539 | 114.2 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 114.13 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00157 | 108.15 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 108.12 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01181 | 123.29 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01032 | 110.88 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 110.79 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 110.43 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 110.37 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 531451 MINGO 7 345 531465 SETAB 7 345 1 | 762.5 | 762.5 | 0.04699 | 105.6 | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 105.46 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00116 | 110.36 | P23:345-161:XEL:ADAMS_I:681_S | External | 110.38 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 111.06 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 111.06 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.91 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 104.9 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00025 | 103.07 | P23:345:XEL:8P6 KING | External | 102.86 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00539 | 114.2 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 114.13 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 147.97 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 148.15 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01038 | 101.75 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 101.64 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.95 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 103.84 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.21 | P11:25:EES:WATERF:1 | External | 104.17 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00117 | 115.81 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 115.81 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00062 | 139.05 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 139.12 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 107.44 | P11:HV:EES::1WAT U3!:1 | External | 107.25 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.1 | 337909 8ANO% 500 337911 1ANO U2 22 1: 337909 8ANO% 500 337911 1ANO U2 22.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 103.94 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 104.27 | -0.33
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 112.78 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01031 | 111.33 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 111.21 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00144 | 132.52 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 132.64 | -0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00352 | 130.29 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 130.27 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00019 | 123.61 | P23:345:XEL:8S25 WLM AS | External | 123.66 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01176 | 133.62 | P23:345:AMMO::ZACHARY:2 | External | 133.58 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 100.86 | P12:115:XEL:CHI-LIN-SHF-LCR | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 128.63 | P11:HV:EES::TURKCOAL:1 | External | 128.5 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01107 | 127.75 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 128.16 | -0.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 106.27 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 105.35 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.27 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0005 | 114.1 | P12:345:XEL:ASAK-ECL SPS | External | 114.19 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.75 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 100.77 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00034 | 102.78 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 102.85 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.76 | P23:345:XEL:8P5 KING | External | 117.98 | -0.22
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 139.98 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1 | External | 140.07 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00122 | 104.69 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 104.57 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997522 CHL345-115-1 115 1 | 448 | 448 | 0.00042 | 105.33 | P23:345:XEL:8S51 HMP | External | 105.29 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.39 | P12:EHV:EES::8ANO%:1(1) | External | 106.19 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 101.99 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 101.86 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.86 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 111.77 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 111.04 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External | 111.13 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00019 | 111.11 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 111.13 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 108.24 | P21:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 108.14 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.8 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 134.83 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.09 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 111.02 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 128.69 | 81750: 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | External | 128.73 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 108.95 | P23:345:ATC:ARPIN:424-S_GD | External | 109.18 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 107.94 | P24:345:AMMO::LABADIE:15H | External | 107.44 | 0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.23 | P12:HV:EES::PIRKEY 4:1 | External | 111.14 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01045 | 106.73 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 106.67 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00117 | 115.81 | P12:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 115.81 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01069 | 113.32 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 113.26 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00566 | 114.09 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 113.99 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00223 | 114.15 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 113.83 | 0.32
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 108.16 | Base Case | External | 107.55 | 0.61
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 108.96 | 81750: 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | Internal | 107.52 | 1.44
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.45 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 101.51 | P11:18:ALTW:AUTO-SINGLE:PRCRK4G:4 | External | 101.39 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14606 | 127.15 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 126.18 | 0.97
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.88 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External | 103.81 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00407 | 118.01 | 104071: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00011 | 100.93 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | External | 100.99 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 119.04 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 119.02 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00051 | 100.14 | P23:345-161:XEL:ADAMS_I:680_S | External | 100.07 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.09302 | 100.6 | P13:115-230:MIDW:RICE COUNTY | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00984 | 117.68 | P23:345:MEC:TIFFIN 954 | External | 117.62 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06899 | 106.89 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | Internal | 105.54 | 1.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.00073 | 154.1 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 153.86 | 0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01197 | 128.32 | P23:345:ITCM:HAZLTON3 9985:IA-NE | External | 128.24 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 108.63 | P23:345:MEC:TIFFIN 954 | External | 108.61 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 137.34 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 147.81 | P24:345:AMMO::LABADIE:8H | External | 147.66 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 101.25 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 100.98 | 0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 114.53 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.12 | 601003 PR ISLD3 345 600003 PR IS31G 20 2: 601003 PR ISLD3 345 600003 PR IS31G 20.0 2 | External | 141.18 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 107.13 | P24:345:XEL:8E7 ECL BS | External | 106.78 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681523 GENOA 5 161 681528 HARMONY5 161 1 | 240 | 264 | 0.00059 | 106.56 | P12:161:ITCM:AUTOSINGLE:LANSINGW:GENOA:1 | External | 106.54 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 124.83 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 124.91 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 601055 SCOTTCO3 345 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00294 | 109.05 | P23:345:XEL:8M57 SCO | External | 109.14 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 111.38 | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1: 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | External | 111.02 | 0.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 107.83 | P11:024:DPC:ALMA2:6 | External | 107.98 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06877 | 109.57 | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 108.18 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 107.8 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 107.26 | 0.54
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.01 | P11:EHV:EES::1ANO U2:1 | External | 103.91 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 112.88 | P12:230:GRE:AUTO-SINGLE:GRE-RAMSEY4:GRE-RMSYCB14:Z | External | 113.23 | -0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01028 | 114.11 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 114.24 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.78 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 104.67 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 119.83 | 104894: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 144.14 | P12:115:XEL:AUTO-SINGLE:WILOWRV7:THREELAKES7:1 | External | 144.05 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00021 | 152.5 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 152.5 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.10234 | 141.92 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 139.66 | 2.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00983 | 106.76 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 106.79 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 109.22 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External | 109.38 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00436 | 104.61 | P23:345:AMMO::MONTGOMERY:V43 | External | 104.22 | 0.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00014 | 114.08 | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00408 | 118.19 | 92270: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External | 118.12 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00204 | 162.74 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 162.64 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 107.98 | P12:345:MEC:TIFFIN-ARNOLD | External | 107.91 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.46 | P11:345:AMMO::LABADIE:4 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 146.77 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 146.9 | -0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.77 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External | 152.8 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 115.09 | P23:345:GRE:PVS 19JB3 | External | 115.03 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.57 | 92670: 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 104.54 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00535 | 125.61 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 125.56 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 101.63 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 101.86 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 103.35 | P13:69-161:ALTW:AUTO-SINGLE:BRLGTN18:BRLGTN5:1 | External | 103.28 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00018 | 123.51 | P23:345:XEL:SPS 8S81 SSL | External | 123.45 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01307 | 121.48 | P23:345:XEL:8S27 WLM AS | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 105.68 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 105.93 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00055 | 100.24 | P12:345:XEL:SPS HNA-SSL | External | 100.18 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01142 | 136.05 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 135.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.19 | 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26 1: 337651 8WHT BLUFF% 500 337652 1WHT BLUF U1 26.0 1 | External | 100.15 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00038 | 105.41 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 105.3 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 107.77 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 107.74 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00083 | 120.13 | P12:161:MEC-CBPC:FRANKLIN-HAMPTON-SHEFFIELD | External | 119.95 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 119.91 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 119.88 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0029 | 100.57 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 100.51 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01225 | 126.06 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 126 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.25 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 111.16 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.8 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 153.82 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 112 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 111.94 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 113.23 | P12:345:XEL:SPS WLM-SSL | External | 113.18 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0001 | 107.78 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00422 | 107.69 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External | 107.63 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.0002 | 100.08 | 300626 2CHAMOI 69 300067 5CHAMOI 161 1: 300626 2CHAMOI 69.0 300067 5CHAMOI 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00086 | 119.54 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 119.49 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00982 | 118.6 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 118.58 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.38 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998338 COLAUTO3 138 1 512705 COLLINS4 138 998346 COLAUTO3 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 | External | 101.35 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997477 WEB AB 161 1 | 560 | 560 | 0.00132 | 106.15 | 636025 HAYES 5 161 636030 POMEROY5 161 1: 636025 HAYES 5 161 636030 POMEROY5 161 1 | External | 106.14 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00224 | 100.36 | 635635 MADISON3 345 635640 NORWLK3 345 1: 635635 MADISON3 345 635640 NORWLK3 345 1 | External | 100.25 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00096 | 101.11 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 101.13 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.25 | P12:EHV:EES::8WHT BLUFF%:1 | External | 101.21 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00145 | 106.71 | P12:345:XEL:SPS HNA-SSL | External | 106.81 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 163.87 | P12:345:XEL:ASAK-ECL | External | 164.24 | -0.37
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 101.75 | 601028 EAU CL 3 345 694003 ARPIN B4 345 1: 601028 EAU CL 3 345 694003 ARPIN B4 345 1 | External | 101.83 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00119 | 111.22 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 111.05 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00096 | 101.11 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 101.13 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01028 | 114.11 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00215 | 100.95 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.88 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00055 | 106.22 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 106.17 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00025 | 103.08 | P24:345:XEL:8E7 ECL BS | External | 103.1 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01045 | 116.24 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 116.16 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 114.66 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 114.92 | -0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.6 | 92455: 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External | 101.51 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00983 | 116.04 | P23:345:ALTW:MITCHLCO:1160 | External | 115.93 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.36 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 118 | 0.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 114.05 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 113.74 | 0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00166 | 105.12 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 105.04 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.0006 | 101.53 | 603065 CHISAGO7 115 605269 LINDSTM7 115 1: 603065 CHISAGO7 115 605269 LINDSTM7 115 1 | External | 101.46 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.73 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 113.65 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 115 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 114.37 | 0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00463 | 105.28 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.17 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01541 | 123.93 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 123.9 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 107.77 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 107.74 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08885 | 140.68 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 138.89 | 1.79
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00088 | 101.74 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 101.68 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.76 | 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26 1: 337651 8WHT BLUFF% 500 337653 1WHT BLUF U2 26.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00132 | 107.31 | 636025 HAYES 5 161 636030 POMEROY5 161 1: 636025 HAYES 5 161 636030 POMEROY5 161 1 | External | 107.3 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.4 | 337909 8ANO% 500 337910 1ANO U1 22 1: 337909 8ANO% 500 337910 1ANO U1 22.0 1 | Internal | 104.92 | 1.48
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00041 | 113.41 | P42:345:NPPD:BKR-CPR-3304 | External | 115.09 | -1.68
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00016 | 112.57 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 112.52 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00016 | 112.57 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 112.52 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15517 | 103.93 | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | Internal | 102.89 | 1.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 2e-05 | 159.87 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | External | 159.84 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00079 | 124.29 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 124.26 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00016 | 116.97 | P23:345:ITCM:SALEM 3 2870:IA-NE | External | 116.78 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0119 | 125.25 | P23:345:GRE:PVS 19JB2 | External | 125.19 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06983 | 123.91 | 78000: 532771 RENO 7 345 587884 G16-111-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 122.49 | 1.42
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18708 | 100.87 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 105.68 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 105.93 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 106.09 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 106.06 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.10739 | 100.85 | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 100.54 | 0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.25 | P23:500:EES-EAI:PD:INDEP2:LN:FK479 | External | 106.06 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01244 | 120.04 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 119.92 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.78 | P12:EHV:EES::WELSH 7:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 113.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00387 | 112.51 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 112.41 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 104.09 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 106.52 | P11:345-24:CLEC::DOLHILL7:1 | External | 106.47 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00018 | 123.46 | P12:345:XEL:SPS HNA-SSL | External | 123.4 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 116.41 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 116.4 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 101.13 | Base Case | External | 101.05 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00012 | 116.9 | P23:345:XEL:8S25 WLM AS | External | 117.05 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.85 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 103.81 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 135.2 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 135.16 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0004 | 169.53 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 169.64 | -0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01164 | 127 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | External | 127.07 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.84 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 110.76 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00081 | 105.29 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External | 105.26 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.54 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 100.36 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 100.35 | P12:EHV:EES::8WHT BLUFF%:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 111.47 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 111.46 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00215 | 100.95 | P23:345:MEC:MONTEZUMA 902 | External | 100.88 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.0747 | 121.59 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 120.04 | 1.55
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 6e-05 | 125.88 | P23:345:XEL:8M54 SCO | External | 125.85 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.18 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 111.1 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 131.96 | P23:345:MEC:GDMEC 902 | External | 131.84 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 111.3 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00412 | 103.51 | P23:345:AMMO::SPENCERCREEK:V3 | External | 103.44 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 114.75 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 114.76 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 135.33 | 106084: 656025 FRDRCKSB8 69.0 656039 LAWLERTP8 69.0 1 656039 LAWLERTP8 69.0 656061 PETERSON8 69.0 1 656039 LAWLERTP8 69.0 656041 LAWLR8 69.0 1 | External | 134.28 | 1.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00027 | 120.25 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 120.14 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00117 | 108.13 | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1: 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | External | 108.21 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00027 | 107.76 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 107.69 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 123.85 | P23:345:ALTW:MITCHLCO:1150 | External | 123.77 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.12 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 103.07 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00981 | 107.25 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 107.24 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 106.93 | P23:345:MEC:SUB 56 934 OR 937 | External | 106.84 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01126 | 132.43 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 132.33 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00983 | 115.46 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 115.7 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00018 | 154.83 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 154.88 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00017 | 120.9 | 105811: 620263 FORMN 7 115 652438 FORMAN 7 115 1 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1 652438 FORMAN 7 115 652462 ELLIOTT7 115 1 652438 FORMAN 7 115 659172 LUDDEN -CP7 115 1 652438 FORMAN 7 115 997172 FO KY1A 69.0 1 652439 FORMAN 8 69.0 655630 COGSWELL-CP8 69.0 1 652327 FORMAN 9 41.8 652439 FORMAN 8 69.0 1 652439 FORMAN 8 69.0 997172 FO KY1A 69.0 1 652393 FORMAN9 12.5 997172 FO KY1A 69.0 1 620262 GWINNER7 115 620263 FORMN 7 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 652438 FORMAN 7 115 997179 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997179 FO KY1A 69.0 1 652393 FORMAN9 12.5 997179 FO KY1A 69.0 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 652438 FORMAN 7 115 997170 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997170 FO KY1A 69.0 1 652393 FORMAN9 12.5 997170 FO KY1A 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00981 | 107.25 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 107.24 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 105.44 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External | 104.91 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 117.89 | 65701: 601014 AS KING3 345 601018 CHIS CO3 345 1 601014 AS KING3 345 601023 REDROCK3 345 1 601014 AS KING3 345 601028 EAU CL 3 345 1 601028 EAU CL 3 345 694003 ARPIN B4 345 1 601028 EAU CL 3 345 997649 EAU CL 3 161 9 602021 EAU CLA5 161 997649 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997649 EAU CL 3 161 9 601028 EAU CL 3 345 997655 EAU CL 3 161 9 602021 EAU CLA5 161 997655 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997655 EAU CL 3 161 9 601028 EAU CL 3 345 997652 EAU CL 3 161 9 602021 EAU CLA5 161 997652 EAU CL 3 161 9 605734 EAUCLAIRE9 9 13.8 997652 EAU CL 3 161 9 | External | 118.53 | -0.64
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 106.36 | P22:345:MEC:SUB 92 | External | 106.29 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00984 | 109.11 | P23:345:MEC:TIFFIN 954 | External | 109.05 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01176 | 125.96 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 125.91 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00423 | 105.06 | P13:161-345:AMMO::OVERTON:1 | External | 104.95 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.77 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | External | 150.79 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 112.13 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 112.49 | -0.36
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 141.36 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 141.34 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 118.63 | P24:345:XEL:8E7 ECL BS | External | 118.18 | 0.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00029 | 105.63 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 105.63 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 103.35 | 631109 BRLGTN 5 161 630037 BRLGTN18 69 1: 631109 BRLGTN 5 161 630037 BRLGTN18 69.0 1 | External | 103.28 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.00094 | 127.59 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 127.36 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.1 | P12:EHV:EES::WELSH 7:1(1) | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00388 | 112.78 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | External | 112.75 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01032 | 111.09 | P23:500:EAI:NBF_SAN SOUC | External | 111.01 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 103.22 | P13:23-345:OPPD:NEBCTY2G | External | 103.2 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 123.81 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 123.78 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 110.2 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 110.13 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 119.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 119.02 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00026 | 118 | 631060 TRK RIV5 161 681519 STONEMAN 161 1: 631060 TRK RIV5 161 681519 STONEMAN 161 1 | External | 117.86 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.73 | P11:345:AMMO::CALLAWAY:1 | External | 106.46 | 0.27
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 107.83 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 107.98 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00165 | 105.95 | P23:345:MEC:BLACK HAWK 901 | External | 105.99 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05978 | 100.86 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05916 | 106.63 | 78001: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 105.21 | 1.42
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00177 | 129.67 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 129.61 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 102.08 | 337909 8ANO% 500 337911 1ANO U2 22 1: 337909 8ANO% 500 337911 1ANO U2 22.0 1 | External | 102.05 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01052 | 101.79 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 101.72 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 123.9 | 344011 7HUGHES 345 344012 7HPW-N 345 1: 344011 7HUGHES 345 344012 7HPW-N 345 1 | External | 123.75 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00074 | 111.38 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:NEWPORT5:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00122 | 136.8 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 136.62 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 118.93 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 119.03 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00566 | 114.09 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 113.99 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0006 | 109.35 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00053 | 100.77 | P24:345:AMMO::LABADIE:8H | External | 100.79 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01052 | 111.68 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 111.61 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00024 | 103.22 | 300575 2MONTGY 69 300099 5MONTCT 161 1: 300575 2MONTGY 69.0 300099 5MONTCT 161 1 | External | 103.16 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.00352 | 130.29 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 130.27 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 104.13 | P23:345:ALTW:MITCHLCO:1160 | External | 104.06 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 111.49 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 111.42 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 117.54 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 117.57 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 145.52 | P23:345:ITCM:HCKRYCK:5267-PRESENT | External | 145.51 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00044 | 105.12 | P23:345:MEC:MONTEZUMA 901 | External | 105.36 | -0.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 112.3 | P23:345:ALTW:MITCHLCO:1150 | External | 112.1 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.35 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 118.09 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00276 | 112.94 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 112.9 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 156.42 | P23:345:ALTW:MITCHLCO:1140 | External | 156.39 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00121 | 103.55 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998347 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998346 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998355 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998354 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 103.47 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00089 | 112.79 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 112.6 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01149 | 102.69 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01032 | 111.09 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 111.01 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 188.48 | P11:024:DPC:ALMA2:6 | External | 188.39 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 107.84 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 107.82 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15094 | 100.98 | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | Internal | 100.17 | 0.81
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 131.45 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 131.47 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00121 | 111.99 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 111.88 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15351 | 102.8 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 101.57 | 1.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00424 | 105.48 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 105.32 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00053 | 100.94 | P24:345:AMMO::LABADIE:20H | External | 100.97 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.43 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.51 | -0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00113 | 114.02 | Base Case | External | 113.88 | 0.14
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00381 | 112.87 | P23:345:MEC:LOUISA 964 | External | 112.81 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00085 | 120.89 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 120.69 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00029 | 145.87 | P23:345-161:XEL:ADAMS_I:680_S | External | 145.77 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.00098 | 105.25 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 105.88 | -0.63
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00056 | 145.25 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 145.19 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01045 | 115.98 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 115.91 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 112.44 | P12:230:GRE:AUTO-SINGLE:GRE-RMSYCB14:GRE-RMSYCB24:Z | External | 113.22 | -0.78
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00017 | 122.74 | P12:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 122.7 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.98 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External | 106.78 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 112.99 | P23:345:GRE:CHL 304JB20 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00129 | 104.04 | 104894: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 105.05 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 105.05 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 118.28 | P12:345:XEL:ASAK-ECL SPS | External | 118.15 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.8 | 631017 PRAR CK7 115 629066 PR CRK4G 18 1: 631017 PRAR CK7 115 629066 PR CRK4G 18.0 1 | External | 110.67 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00565 | 114.02 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External | 113.89 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0091 | 112.46 | P23:345:MEC:ATCHISON CO 903 | External | 112.34 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00355 | 107.01 | P23:345:MEC:KOSSUTH 904 | External | 106.96 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 110.78 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 111.25 | -0.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00119 | 111.22 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 111.05 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.82 | P12:EHV:EES::8ANO%:1(1) | Internal | 105.43 | 1.39
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 6e-05 | 124.59 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 124.44 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00166 | 103.77 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 103.75 | 0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 101.37 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 101.28 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 109.04 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 156.38 | P23:345:ALTW:MITCHLCO:1130 | External | 156.54 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15801 | 126.24 | 78000: 532771 RENO 7 345 587884 G16-111-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 125.19 | 1.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.86 | P11:345:AMMO::LABADIE:4 | External | 112.79 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.96 | P23:345:XEL:8P6 KING | External | 117.81 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00218 | 101.85 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997726 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997726 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997733 RIVERTON 69.0 1 547469 RIV4525 161 997733 RIVERTON 69.0 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 | External | 101.79 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 142.18 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 142.21 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00044 | 116.75 | P23:345:AMMO::MONTGOMERY:V43 | External | 117.42 | -0.67
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00126 | 100.45 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 100.4 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00413 | 126 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 126.04 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00031 | 134.61 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 134.56 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 118.83 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00985 | 117.87 | P12:345:MEC:TIFFIN-ARNOLD | External | 117.8 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 118.67 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 118.68 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 117.84 | P23:345-161:XEL:ADAMS_I:680_S | External | 117.85 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07024 | 117.01 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal | 115.55 | 1.46
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 104.74 | P23:345:XEL:8P5 KING | External | 104.93 | -0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00072 | 136.46 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 136.53 | -0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00288 | 117.17 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 117.14 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00144 | 132.52 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 126.64 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 126.49 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00471 | 121.75 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 121.63 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 100.55 | P24:345:AMMO::RUSHISLAND:V6 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.16 | P11:21:EES:RVB:1 | External | 112.08 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 126.04 | P22:345:XEL:ADAMS 3 N1:MN | External | 125.96 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00169 | 121.37 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 121.55 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00408 | 118.19 | 104096: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External | 118.11 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 120.42 | P23:345:XEL:8P5 KING | External | 118.65 | 1.77
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 3e-05 | 130.04 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 129.97 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 113.45 | P23:345:XEL:8N17 SHC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 154.61 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 154.62 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00025 | 128.33 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 128.34 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.49 | P11:HV:EES::PIRKEY 1:1 | External | 112.36 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.13 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 118.43 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 118.3 | 0.13
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00011 | 117.86 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 117.71 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00981 | 116.07 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 116.07 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00119 | 137.82 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2 | External | 138.07 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00062 | 142.51 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 142.39 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 111.86 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | External | 111.8 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00073 | 120.02 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 119.67 | 0.35
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 107 | 620314 BIGSTON4 230 620315 BIGSTN1G 24 1: 620314 BIGSTON4 230 620315 BIGSTN1G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 117.74 | P22:345:XEL:ADAMS 3 N1:MN | External | 117.64 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 117.7 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 117.87 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00413 | 126 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 126.04 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00089 | 112.79 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 112.6 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 113.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | External | 113.21 | -0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01191 | 123.36 | P23:345:ALTW:MITCHLCO:1130 | External | 123.42 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 108.65 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 108.35 | 0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.0001 | 101.45 | 631141 ROCK CK3 345 631063 ROCK CK5 161 1: 631141 ROCK CK3 345 631063 ROCK CK5 161 1 | External | 101.41 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.59 | P11:HV:EES::JTEC GEN#2 1:2 | External | 103.52 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01142 | 136.05 | P23:345:MEC:MONTEZUMA 902 | External | 135.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00181 | 146.92 | P23:345:MEC:GDMEC 901 | External | 146.86 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 115.85 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 115.94 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 4e-05 | 112.27 | P23:345:XEL:8N17 SHC | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 142.01 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 141.89 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 110.19 | 346004 7GOSCK 345 3WXFMR GSK1 GSU 1: 346004 7GOSCK 345 998845 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998845 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998845 GSK1 GSU 13.8 1 346004 7GOSCK 345 998848 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998848 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998848 GSK1 GSU 13.8 1 346004 7GOSCK 345 998852 GSK1 GSU 13.8 1 345998 1GOSCK 1 13.8 998852 GSK1 GSU 13.8 1 345999 1GOSCK 2 13.8 998852 GSK1 GSU 13.8 1 | External | 110.09 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00097 | 119.48 | P12:161:UMZ:# 5519 #: IN . PROPER N-1 (LINE) FOR 636230-656207-1 | External | 119.29 | 0.19
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00216 | 113.56 | 104645: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 113.49 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00144 | 110.39 | P23:345:AMMO::ZACHARY:2 | External | 110.42 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00182 | 147.97 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 148.15 | -0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00119 | 137.82 | P12:345:XEL-ITC:AMD-PVS-MTC AS | External | 138.07 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00367 | 119.99 | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 119.99 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 112.71 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 112.71 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07005 | 112.71 | P42:345:SPS:FINNEY_OR70_19L | Internal | 111.24 | 1.47
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00158 | 100.69 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 100.68 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00027 | 113.84 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | External | 113.75 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00089 | 121.17 | P23:345:AMIL::HERLEMAN:1 | External | 121.02 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 101.54 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 101.45 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06932 | 112.71 | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 111.26 | 1.45
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00051 | 110.71 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 111 | -0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 100.91 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 100.85 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00052 | 108.87 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | External | 108.97 | -0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 107.71 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 107.86 | -0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00127 | 107.15 | P13:161-69:MEC:AUTO-SINGLE:WALLLK5:WALLLK8:1 | External | 106.94 | 0.21
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01043 | 120.89 | P23:345:MEC:BLACK HAWK 901 | External | 120.72 | 0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00055 | 110.73 | P42:345:NPPD:BKR-CPR-3304 | External | 111.25 | -0.52
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 111.53 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 111.42 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 2 | 500 | 500 | 0.00037 | 107.29 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 107.25 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00132 | 104.17 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 104.07 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00115 | 110.96 | P12:161:ALTW:AUTO-SINGLE:GRMND5:MQOKETA5:1 | External | 110.81 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00108 | 110.56 | P23:345:XEL:8P6 KING | External | 111.06 | -0.5
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00011 | 103.22 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 103.19 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.4 | P13:500:EES-EAI:ARK_NU:T1 | Internal | 104.92 | 1.48
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 126.64 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 126.49 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 100.81 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 100.52 | 0.29
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00382 | 112.89 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External | 112.78 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01043 | 120.56 | P23:345:MEC:BLACK HAWK 901 | External | 120.4 | 0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00033 | 188.98 | P12:345:XEL:ASAK-ECL | External | 189.23 | -0.25
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00286 | 101.59 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External | 101.55 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.5 | P12:161:AMMO-ITC::APANOSE:ADAIR:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 160.13 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1 | External | 160.13 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00136 | 132.91 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 132.88 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15879 | 131.02 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 129.98 | 1.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14644 | 127.93 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 126.98 | 0.95
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01001 | 114.38 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | External | 114.42 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01176 | 125.96 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 125.91 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 113.13 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 113.17 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00238 | 102.49 | 344815 5JC ZION TP 161 345027 5MARIOSA 161 1: 344815 5JC ZION TP 161 345027 5MARIOSA 161 1 | External | 102.42 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 149.58 | 71593: 603065 CHISAGO7 115 603172 WYOMING7 115 1 603136 HUGO 7 115 603172 WYOMING7 115 1 603065 CHISAGO7 115 605269 LINDSTM7 115 1 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 149.54 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.00765 | 111.54 | P23:345:MEC:LOUISA 964 | External | 111.46 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18231 | 150.06 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 148.8 | 1.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 105.19 | P24:345:AMMO::RUSHISLAND:V6 | External | 105.08 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 108.26 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 134.8 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.83 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 108.26 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.04 | 337909 8ANO% 500 337910 1ANO U1 22 1: 337909 8ANO% 500 337910 1ANO U1 22.0 1 | External | 105.81 | 0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.0021 | 102.7 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 102.69 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 110.24 | 344225 1CAL G1 25 344224 7CALAWY 1 345 1: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 110.29 | -0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 138.16 | 620327 HANKSON4 230 620329 WAHPETN4 230 1: 620327 HANKSON4 230 620329 WAHPETN4 230 1 | External | 138.39 | -0.23
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 122.02 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 121.91 | 0.11
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00171 | 122.05 | P23:345:MEC:GDMEC 902 | External | 121.99 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 118.52 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 118.52 | 0
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 105.78 | P11:24:CLEC::G1DOLHIL:1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 211 | 211 | 0.00168 | 101.27 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 101.24 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05798 | 100.85 | 40230: 530580 PAWNEE 2 69.0 530585 BAZINE 2 69.0 1 530585 BAZINE 2 69.0 530700 WALNTCRK3 69.0 1 530580 PAWNEE 2 69.0 530598 CHSPIP 2 69.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00668 | 110.73 | 636615 SB 56 3 345 636620 WALCOTT3 345 1: 636615 SB 56 3 345 636620 WALCOTT3 345 1 | External | 110.66 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05978 | 100.77 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 152.85 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | External | 153.02 | -0.17
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00101 | 115.21 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 115.18 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 112.78 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 113.08 | -0.3
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00193 | 101.09 | P23:345:MEC:SYCAMORE 901 | External | 101.04 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00108 | 141.87 | P12:161:UMZ:# 5519 #: IN . PROPER N-1 (LINE) FOR 636230-656207-1 | External | 141.67 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00027 | 105.61 | P23:345:ITCM:HCKRYCK:5269-PRESENT | External | 105.51 | 0.1
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 104.56 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 104.59 | -0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01245 | 118.78 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 133.5 | P24:345:XEL:8E7 ECL BS SPS | External | 133.59 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01033 | 109.34 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 109.43 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00019 | 123.59 | P23:345:XEL:8S27 WLM AS | External | 123.68 | -0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0003 | 111.95 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 111.83 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.15 | P23:500:EES-EAI:INDEP2:B6126 | External | 105.97 | 0.18
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01248 | 120.42 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External | 120.34 | 0.08
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00181 | 146.89 | P23:345:MEC:GDMEC 902 | External | 146.83 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0002 | 107.98 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 107.91 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00072 | 123.59 | P23:345:MEC:MONTEZUMA 901 | External | 123.65 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01048 | 111.69 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 111.63 | 0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 103.87 | 337909 8ANO% 500 337911 1ANO U2 22 1: 337909 8ANO% 500 337911 1ANO U2 22.0 1 | External | 103.83 | 0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00128 | 108.65 | P22:345:XEL:345KV SEC 2 ECL SPS | External | 108.69 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00124 | 100.19 | P11:HV:EES::TURKCOAL:1 | External | 100.07 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 124.19 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 124.04 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00413 | 126 | P23:345:MEC:MONTEZUMA 901 | External | 126.04 | -0.04
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 101.97 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 101.9 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15956 | 133.71 | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 132.47 | 1.24
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00985 | 115.94 | P23:345:MEC:HILLS 984 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00135 | 114.1 | P23:345:XEL:8S25 WLM AS | External | 114.12 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01236 | 124 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 123.93 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0001 | 121.98 | P13:41-115-230:OTP:AUTO-SINGLE:FORMN9:FORMN7:FORMAN4:1 | External | 121.45 | 0.53
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997477 WEB AB 161 1 | 560 | 560 | 0.00331 | 115.55 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 115.61 | -0.06
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0027 | 128.85 | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | External | 128.76 | 0.09
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 105.3 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 105.25 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 110.93 | 81749: 514942 REDBUD4G 18.0 998286 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998298 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998286 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998296 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998297 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998298 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998297 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998296 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998294 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998306 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998294 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998304 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998305 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998306 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998305 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998304 REDBUD3 18.0 1 514942 REDBUD4G 18.0 998291 REDBUD4 18.0 1 514899 REDBUD1S 18.0 998303 REDBUD1 18.0 1 514940 REDBUD4S 18.0 998291 REDBUD4 18.0 1 514905 REDBUD3S 18.0 998301 REDBUD3 18.0 1 514911 REDBUD2G 18.0 998302 REDBUD2 18.0 1 514910 REDBUD1G 18.0 998303 REDBUD1 18.0 1 514900 REDBUD2S 18.0 998302 REDBUD2 18.0 1 514912 REDBUD3G 18.0 998301 REDBUD3 18.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00021 | 108.38 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 108.26 | 0.12
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 163.73 | P24:345:XEL:8E7 ECL BS SPS | External | 163.66 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.38 | 104745: 532852 JEC 6 230 532651 JEC U1 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 | Internal | 104.89 | 1.49
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.98 | P12:230-21:EES:FCY:RVB | External | 106.78 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00065 | 106.98 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 106.78 | 0.2
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00998 | 116.84 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 116.77 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01033 | 111.48 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 111.47 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0013 | 105.95 | P13:161-69:ITCM:LIME CK5 T1:IA-NW | External | 105.8 | 0.15
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00986 | 117.8 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 117.73 | 0.07
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05887 | 101.76 | P12:230:WERE:SUMM-MWE_230:: | Internal | 100.36 | 1.4
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 102.18 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.15 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01033 | 111.25 | 92671: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 | External | 111.24 | 0.01
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 116.96 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 116.91 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | 327 | 327 | 0.00055 | 106.22 | P23:345:ITCM:HCKRYCK:FUT1 | External | 106.17 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00024 | 103.1 | 300575 2MONTGY 69 300099 5MONTCT 161 1: 300575 2MONTGY 69.0 300099 5MONTCT 161 1 | External | 103.05 | 0.05
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 4e-05 | 106.94 | 657757 MORANVI4 230 3WXFMR MORANVILLE 1: 657757 MORANVI4 230 997111 MORANVILLE 69.0 1 657999 MORANVI8 69.0 997111 MORANVILLE 69.0 1 657757 MORANVI4 230 997118 MORANVILLE 69.0 1 657999 MORANVI8 69.0 997118 MORANVILLE 69.0 1 657770 MORANV39 13.8 997118 MORANVILLE 69.0 1 657757 MORANVI4 230 997109 MORANVILLE 69.0 1 657999 MORANVI8 69.0 997109 MORANVILLE 69.0 1 657770 MORANV39 13.8 997109 MORANVILLE 69.0 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 104.06 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 104.37 | -0.31
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0011 | 109.22 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1: 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | External | 109.38 | -0.16
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00982 | 110.11 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 110.08 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06897 | 106.5 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | Internal | 105.09 | 1.41
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01289 | 124.63 | 631113 POWESHK5 161 631117 REASNOR5 161 1: 631113 POWESHK5 161 631117 REASNOR5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00116 | 110.36 | P23:345-161:XEL:ADAMS_I:680_S | External | 110.38 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 118.19 | P23:345:AMIL::HERLEMAN:3 | External | 118.16 | 0.03
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00974 | 116.09 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00116 | 108.69 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00123 | 133.11 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 132.85 | 0.26
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 131.45 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 131.47 | -0.02
Thermal | 00NR | S2 | 24SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 106.95 | P12:345:ATC:8E2:ASKING3:EAUCL3 | External | 107.07 | -0.12
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 140.2 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.2 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00019 | 113.15 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.15 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00028 | 109.49 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 109.49 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 109.95 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.95 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 146.24 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 146.23 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 104.56 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 104.55 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 221.53 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 221.52 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 4e-05 | 103.81 | Base Case | External | 103.81 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 221.53 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 221.52 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 146.24 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 146.23 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 106.92 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 106.92 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00019 | 117.05 | P23:500:EES-EAI:WH_BLF:B7914 | External | 117.05 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997059 GLENHAM TR1 115 1 | 25 | 31 | 0.00028 | 105.01 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 105 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 0.00012 | 110.58 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00056 | 111.09 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 111.08 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00038 | 221.53 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 221.52 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00031 | 108.95 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 108.93 | 0.02
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 136.17 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 136.17 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 125.79 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 125.79 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00056 | 111.55 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 111.55 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 0.00012 | 111.38 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 111.38 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00423 | 104.61 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 104.59 | 0.02
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01498 | 100.58 | P24:345:AMMO::MCCREDIE:1 | External | 100.5 | 0.08
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00565 | 103.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 103.88 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00017 | 142.88 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.88 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 101.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.29 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00043 | 142.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 142.44 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 111.4 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.4 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 106.92 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 106.92 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 111.06 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.06 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 6e-05 | 116.18 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 116.18 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 6e-05 | 116.34 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 116.34 | 0
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00031 | 109.02 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 109 | 0.02
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997617 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00052 | 120.8 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 120.79 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 106.6 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 106.59 | 0.01
Thermal | 04HVER | S1 | 19WP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00043 | 120.22 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.22 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00018 | 136.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.28 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 104.96 | 67791: 336426 3CLAB8! 115 336458 3MICH N! 115 1 336462 6MICHO% 230 500360 FRONTST6 230 1 336412 3PATER! 115 336442 3SFORS 115 1 336442 3SFORS 115 336444 3MICH S! 115 1 | External | 104.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | 336462 6MICHO% 230 500360 FRONTST6 230 1: 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 121.26 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 121.26 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 115.89 | P23:500:EES:BF335618-1~3 | External | 115.85 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 114.49 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 114.49 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 110.86 | P12:HV:EES::6BLPNT!:6TEZCUCO%:1 | External | 110.86 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.67 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 105.63 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.41 | P12:500-230:EES:WILGLN:WATERF | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00073 | 104.49 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 104.48 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 104.79 | P23:500:EES:ABF_WG-A | External | 104.81 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.75 | P23:500:EES:ABF_WG-A | External | 105.78 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.51 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.48 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 104.47 | 336137 6SLIDEL! 230 500360 FRONTST6 230 1: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 | External | 104.47 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.38 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 104.36 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 102.55 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 102.55 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00034 | 101.91 | P12:230:EES:WATERF:VACHER:1 | External | 101.91 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 102.79 | P12:230:EES:PANAMA:DBAYOU:1 | External | 102.79 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 103.26 | P23:500:EES:BF335618-1~3 | External | 103.24 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.77 | P12:500-230:EES:WILGLN:WATERF | External | 102.76 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 114.49 | P12:230:EES:TEZCUC:WATERF:1 | External | 114.49 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 104.79 | P23:500:EES:ABF_WG-A | External | 104.81 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 104.84 | P23:500:EES:BF335618-1~3 | External | 104.81 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.67 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 105.63 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.94 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 108.93 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.68 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.65 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06939 | 121.38 | 177400: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.9 | 0.48
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.97 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.78 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 105.74 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 114.58 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 114.56 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 102.79 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 102.79 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 8e-05 | 101.37 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 101.39 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.77 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 102.76 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 118.23 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.26 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 118.28 | P12:230:EES:IRONMN:L_GPSY:1 | External | 118.28 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 128.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.38 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.09 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 108.08 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 112.38 | P12:230:EES:BELPNT:TEZCUC:L_GPSY:1 | External | 112.38 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.87 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.84 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06939 | 121.38 | 805051: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.9 | 0.48
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.78 | P23:500:EES:BF335618-133 | External | 105.74 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 101.41 | P12:230:EES:WELCOM:STJAME:1 | External | 101.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 103.49 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 103.47 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.88 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 105.85 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 104.99 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 104.97 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 125.87 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.9 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 2e-05 | 128.82 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 128.82 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.46 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 104.44 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 117.14 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 117.14 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 110.86 | 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1: 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1 | External | 110.86 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 109.12 | P12:HV:EES::6TEZCUCO%:6IRONMAN%:1 | External | 109.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.44 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.41 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 117.14 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 117.14 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 104.84 | P23:500:EES:BF335618-1~3 | External | 104.81 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.94 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 108.93 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0003 | 100.4 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 100.4 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.41 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.75 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 108.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 102.79 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 102.79 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 111.51 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 111.51 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.54 | P23:500:EES:ABF_WG-E | External | 104.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.83 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 102.82 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00028 | 102.8 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.77 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.31 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.28 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00014 | 159.35 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 159.36 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.41 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 111.51 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 111.51 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 103.84 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 103.82 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.48 | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.97 | 0.51
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 104.51 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.47 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 115.96 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 115.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.31 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 115.28 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 8e-05 | 102.74 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 102.77 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 111.51 | P12:230:EES:PANAMA:DBAYOU:1 | External | 111.51 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 102.55 | P12:230:EES:TEZCUC:WATERF:1 | External | 102.55 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.56 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.64 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 104.61 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 120.09 | P23:500:EES:BF335618-1~3 | External | 120.05 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 102.98 | P12:HV:EES::6STJAME!:6VACHRE!:1 | External | 102.98 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.41 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.56 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 119.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 118.87 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 118.85 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.69 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 105.66 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 115.96 | P12:230:EES:PANAMA:DBAYOU:1 | External | 115.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 2e-05 | 104.7 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 104.7 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.10412 | 101.42 | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 100.81 | 0.61
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.34 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.32 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.53 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 119.5 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.41 | P12:500-230:EES:WILGLN:WATERF | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 109.02 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 108.99 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.53 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 119.5 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.77 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 102.76 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.63 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 101.62 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 103.23 | P23:500:EES:ABF_WG-A | External | 103.24 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.22 | 64573: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.22 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 121.26 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 121.26 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 115.96 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 115.96 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.48 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.45 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 109.27 | P23:500:EES:BF335618-1~3 | External | 109.24 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.38 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 104.36 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.31 | P12:500-230:EES:WILGLN:WATERF | External | 115.28 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | P12:HV:EES::6MICHO%:FRONTST6:1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.46 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 104.44 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00034 | 105.67 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 105.67 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 102.98 | 336006 6STJAME! 230 336007 6VACHRE! 230 1: 336006 6STJAME! 230 336007 6VACHRE! 230 1 | External | 102.98 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00016 | 109.21 | P23:500:EES:ABF_WG-A | External | 109.24 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00074 | 104.42 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 104.41 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.75 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.56 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.63 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 119.6 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00014 | 142.53 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 142.55 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.41 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.54 | P23:500:EES:ABF_WG-E | External | 104.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.56 | P12:500-230:EES:WILGLN:WATERF | External | 119.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 9e-05 | 121.14 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 121.14 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0003 | 100.4 | P12:230:EES:TEZCUC:WATERF:1 | External | 100.4 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.6 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 115.57 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.54 | P23:500:EES:BF335618-133 | External | 104.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.89 | P23:500:EES:ABF_WG-E | External | 102.87 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 8e-05 | 117.14 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 117.14 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.10437 | 101.61 | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal | 100.97 | 0.64
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.0001 | 115.49 | P23:500:EES:BF335618-133 | External | 115.46 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.75 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 108.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.0001 | 101.21 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 101.24 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.97 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.74 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 108.7 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 101.3 | P12:230:EES:WELCOM:STJAME:VACHER | External | 101.3 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.22 | 80163: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 105.22 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 105.12 | P12:230:EES-CLEC::6MICHO%:FRONTST6:1 | External | 105.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 7e-05 | 114.49 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 114.49 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.74 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 105.7 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.41 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00017 | 130.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.83 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.81 | P23:500:EES:BF335618-1~3 | External | 105.78 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06811 | 119.38 | P13:230-345:MIDW:POST ROCK | Internal | 119.11 | 0.27
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.69 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 105.66 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.74 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 108.7 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.75 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 6e-05 | 102.55 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 102.55 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 115.82 | P23:500:EES:ABF_WG-A | External | 115.86 | -0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.97 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 115.19 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 115.19 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.38 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 104.36 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.82 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 108.79 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.69 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 105.66 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00014 | 112.5 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.52 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.68 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 119.65 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.92 | P23:500:EES:ABF_WG-E | External | 108.89 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 109.23 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.26 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00032 | 102.98 | P12:230:EES:STJAME:VACHER:1 | External | 102.98 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.38 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 115.35 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.51 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.48 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.38 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 104.36 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00012 | 138.97 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00011 | 104.47 | P12:230:EES-CLEC::6SLIDEL!:FRONTST6:1 | External | 104.47 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.10437 | 101.61 | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | Internal | 100.97 | 0.64
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 115.19 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 115.19 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.75 | P12:500-230:EES:WILGLN:WATERF | External | 108.72 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 121.48 | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.97 | 0.51
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 2e-05 | 102.99 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 102.99 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.77 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 102.76 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.34 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.32 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.97 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.22 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.19 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 119.72 | P23:500:EES:BF335618-133 | External | 119.69 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.54 | P23:500:EES:BF335618-133 | External | 104.51 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.31 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 115.28 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.31 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.28 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.0001 | 115.49 | P23:500:EES:ABF_WG-E | External | 115.46 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 196.8 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 196.81 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 120.02 | P23:500:EES:ABF_WG-A | External | 120.05 | -0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.74 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 102.73 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.64 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 104.61 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 103.84 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 103.82 | 0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 8e-05 | 121.26 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 121.26 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00014 | 112.5 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 112.52 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 118.28 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 118.28 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.69 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 105.66 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 119.72 | P23:500:EES:ABF_WG-E | External | 119.69 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 2e-05 | 128.64 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 128.64 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 109.12 | P12:230:EES:TEZCUC:IRONMN:1 | External | 109.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.86 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 102.85 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00012 | 138.97 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 138.97 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.56 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 119.53 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.41 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.29 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 115.26 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00011 | 115.29 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 115.26 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 129.42 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 129.44 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 9e-05 | 117.09 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 117.09 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 120.9 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.42 | 0.48
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.74 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 102.73 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00026 | 165.38 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 165.38 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.78 | P23:500:EES:ABF_WG-E | External | 105.74 | 0.04
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.98 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 102.97 | 0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 4e-05 | 105.69 | P12:500-230:EES:WILGLN:WATERF | External | 105.66 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 109.12 | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1: 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | External | 109.12 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00012 | 102.47 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 102.47 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.10412 | 101.42 | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | Internal | 100.81 | 0.61
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.0001 | 106.31 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 106.32 | -0.01
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00013 | 104.41 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00011 | 146.74 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 146.76 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 324 | 359 | 0.10437 | 101.61 | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal | 100.97 | 0.64
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00033 | 104.41 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 104.41 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00013 | 104.41 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.38 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.0698 | 120.9 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.42 | 0.48
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00015 | 108.92 | P23:500:EES:BF335618-133 | External | 108.89 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00011 | 119.84 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 119.81 | 0.03
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00013 | 111.31 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 111.33 | -0.02
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00012 | 118.28 | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1: 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | External | 118.28 | 0
Thermal | 04NR | S2 | 24L0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.06939 | 121.38 | 805050: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal | 120.9 | 0.48
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.68 | 300007 1NM G2 22 300046 7NEWMAD 345 1: 300007 1NM G2 22.0 300046 7NEWMAD 345 1 | External | 116.31 | 0.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.53 | P23:345:MEC:TIFFIN 944 | External | 118.77 | -0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 122.44 | Base Case | External | 122.37 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01117 | 111.56 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 111.37 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01008 | 123.06 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 122.95 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00067 | 100.83 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 100.69 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00017 | 152.55 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 152.3 | 0.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 148.73 | P12:HV:EES::PIRKEY 4:1 | External | 148.62 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00139 | 121.15 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 121.26 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 138.05 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.05 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01185 | 119.91 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0099 | 110.09 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 110.64 | -0.55
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 106.54 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.08914 | 116.92 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 115.43 | 1.49
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 109.78 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 109.57 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01121 | 117.1 | P23:345:XEL:8S27 WLM AS | External | 117.29 | -0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00115 | 106.32 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 106.22 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 109.99 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 109.79 | 0.2
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 105.73 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 105.66 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.59 | 92381: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.7 | 104268: 532780 CANEYRV7 345 532781 CANEYWF7 345 1 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | Internal | 101.57 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.37 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 102.38 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0041 | 123.64 | 84399: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 123.56 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01086 | 116.58 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 116.51 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.04 | 300007 1NM G2 22 300046 7NEWMAD 345 1: 300007 1NM G2 22.0 300046 7NEWMAD 345 1 | External | 105.7 | 0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01119 | 107.29 | P12:345:XEL:SPS HNA-SSL | External | 107.21 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.22 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 121.37 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.07 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 120.99 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 103.08 | 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1: 608626 BOSWELL4 230 608775 BOSWE44G 22.8 1 | External | 103.06 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01141 | 108.56 | P23:345:MEC:KOSSUTH 904 | External | 108.49 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01085 | 109.16 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 109.14 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 117.41 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 117.34 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00409 | 138.29 | 300043 7KINGDM 345 300044 7MCCRED 345 1: 300043 7KINGDM 345 300044 7MCCRED 345 1 | External | 138.23 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05337 | 100.44 | 104702: 542966 WGARDNR5 161 543132 BNSF 5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | Internal | 100.22 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.99 | P12:345:MEC:HILLS-SUB T-LOUISA + REACTOR | External | 103.98 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 104.15 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 104.19 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.4 | P11:022:NPPD:COOPER1G:1:983 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | 717.1 | 717.1 | 0.03341 | 101.9 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | Internal | 101.14 | 0.76
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.01 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 116.01 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.83 | P11:24:AEPW:PIRKEY 1 | External | 116.83 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05336 | 100.54 | 104701: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | Internal | 100.46 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00258 | 123.1 | 345027 5MARIOSA 161 345238 7MARIOSA 345 1: 345027 5MARIOSA 161 345238 7MARIOSA 345 1 | External | 123.03 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.04 | P11:HV:EES::1NELSON_G6!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 103.1 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 103.15 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.43 | 82336: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.41 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.00025 | 18424.11 | P11:HV:EES::PIRKEY 1:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 109.42 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 109.45 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 111.58 | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | External | 111.54 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 136.57 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 135.41 | 1.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00372 | 122.14 | 300088 5HUBEN 161 300042 7HUBEN 345 1: 300088 5HUBEN 161 300042 7HUBEN 345 1 | External | 122.07 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0099 | 120.09 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 120.75 | -0.66
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 126.65 | 92230: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 126.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 137.99 | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 135.3 | 2.69
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00491 | 104.23 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 103.91 | 0.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 135.88 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 135.06 | 0.82
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 114.83 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.08956 | 102.85 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 102.13 | 0.72
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.9 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 127.83 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00068 | 101.16 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 100.99 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01066 | 105.71 | P23:500:EES:PERYVL:R7372 | External | 105.68 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.68 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 116.31 | 0.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.38 | P12:345:MEC:TIFFIN 9T1 SPS | External | 118.3 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01218 | 110.6 | P21:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 110.59 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 101.34 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 101.34 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00376 | 121.93 | P24:345:AMMO::RUSHISLAND:V14 | External | 121.76 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92405: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 121.44 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05336 | 100.54 | 84582: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | Internal | 100.46 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 128.11 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 128.13 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 155.39 | 613330 RICE 5 161 693755 JADE AVE 161 1: 613330 RICE 5 161 693755 JADE AVE 161 1 | External | 155.35 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01107 | 119.94 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 119.8 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 148.73 | P13:138-24:AEPW:PIRKEY 4 | External | 148.62 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 6e-05 | 120.01 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 120.04 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01011 | 115.38 | P23:345:MEC:HILLS 984 | External | 115.1 | 0.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.46 | 92473: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 102.46 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 115.15 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 115.27 | -0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15187 | 104.5 | Base Case | Internal | 103.21 | 1.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00375 | 125.12 | 104711: 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541235 DUNCAN 5 161 541250 SIBLEYPL 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 541151 SIBLEY#3 22.0 541250 SIBLEYPL 161 1 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 2 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 3 541250 SIBLEYPL 161 541346 RTCHFLD5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.19 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 108.19 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.88 | 338187 8DELL% 500 338340 8CC_DELL 500 1: 338187 8DELL% 500 338340 8CC_DELL 500 1 | External | 115.76 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 112.61 | 84403: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 112.63 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 139.96 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 139.96 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01137 | 118.05 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 118 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00957 | 108.51 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | External | 108.49 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.95 | P13:138-24:AEPW:TURK 4 | External | 106.81 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 100.98 | P12:345:MEC:AUTO-SINGLE:SEPOLK3:GDMEC:1 | External | 100.9 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.20294 | 102.3 | P12:230:WERE:CIRC-EMCP_230:: | Internal | 100.79 | 1.51
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0045 | 126.02 | 84363: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 542969 STILWEL5 161 542994 HICKMAN5 161 1 542969 STILWEL5 161 543050 ANTIOCH5 161 1 542969 STILWEL5 161 543053 REDEL 5 161 1 542969 STILWEL5 161 543057 BUCYRUS5 161 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 542969 STILWEL5 161 997752 STILWELL11 161 11 542969 STILWEL5 161 997751 STILWELL22 161 22 542969 STILWEL5 161 997759 STILWELL11 161 11 542969 STILWEL5 161 997758 STILWELL22 161 22 542969 STILWEL5 161 997755 STILWELL11 161 11 542969 STILWEL5 161 997754 STILWELL22 161 22 | External | 125.98 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.19594 | 105.57 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 104.06 | 1.51
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 109.38 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.39 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 106.9 | 92447: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 106.84 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.98 | P11:18:EES-EAI:ETTA:1 | External | 120.89 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00987 | 120.36 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 120.39 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01026 | 121.97 | P21:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 121.96 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00519 | 116.88 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 116.72 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01251 | 106.88 | P22:345:AMMO::RUSHISLAND:1 | External | 106.82 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 143.41 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01091 | 117.04 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 116.98 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00065 | 107.25 | P23:345:MEC:LOUISA 954 | External | 107.35 | -0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01251 | 107.27 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 107.25 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.48 | P23:345:MEC:TIFFIN 944 | External | 127.78 | -0.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01342 | 108.52 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 108.48 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 5e-05 | 104.64 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:MAPLER3:1 | External | 104.62 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 108.19 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 108.19 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 108.54 | 104647: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 108.5 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01249 | 106.85 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 106.71 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.79 | P11:138:AMMO::SIOUX:2 | External | 116.47 | 0.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01051 | 110.49 | 635017 ATCHSN 3 345 640139 COOPER 3 345 1: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 | External | 110.46 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01345 | 107.68 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998392 VALIANT1 138 2 510911 VALIANT7 345 998391 VALIANT3 138 1 510911 VALIANT7 345 998400 VALIANT1 138 2 510911 VALIANT7 345 998399 VALIANT3 138 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 104.89 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01078 | 117.89 | P23:345-161:XEL:ADAMS_I:681_S | External | 117.78 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00325 | 105.74 | 104525: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 997777 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997784 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | External | 105.56 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.1454 | 107.24 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 106.13 | 1.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00395 | 103.75 | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | External | 104.09 | -0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.43 | P11:HV:EES::1NELSON_G6!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01251 | 107.07 | 63170: 345667 7RUSH 1 345 345857 7TYSON 3 345 1 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 345840 4TAUM S 2 138 345841 1TS G2 13.8 1 345832 1TS G1 13.8 356 1330 1 344822 7JOACHIM 345 345668 7RUSH 2 345 1 345841 1TS G2 13.8 356 1330 2 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 345831 4TAUM S 1 138 345832 1TS G1 13.8 1 345831 4TAUM S 1 138 346145 1TAUM S 34.5 1 | External | 107 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0102 | 116.71 | 82344: 635000 CBLUFFS3 345 645456 S3456 3 345 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 116.62 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01119 | 117.07 | P12:345:XEL:SPS WLM-SSL | External | 117.01 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 101.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 101.13 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92369: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 121.45 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0038 | 133.64 | P12:345:AMMO::CALLAWAY:LOOSECREEK:1 | External | 133.55 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15405 | 104.25 | P42:345:SPS:FINNEY_OR70_19L | Internal | 103.16 | 1.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 106.83 | P11:23:EES-EAI:PLUM17:1 | External | 106.8 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00518 | 116.7 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.89 | P11:24:AEPW:PIRKEY 1 | External | 107.87 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01681 | 109.39 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 108.69 | 0.7
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00139 | 121.15 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 121.26 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.04 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 105.7 | 0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01315 | 107.88 | P23:345:XEL:8S25 WLM AS | External | 107.79 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 100.18 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 100.18 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 106.04 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 105.97 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00058 | 111.77 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:GLENMONT:1 | External | 111.78 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.43 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.41 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 124.35 | 345409 5OVERTON 161 346117 2OVERTON 69 1: 345409 5OVERTON 161 346117 2OVERTON 69.0 1 | External | 124.27 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00171 | 112.35 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 112.25 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.29 | 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2: 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2 | External | 108.23 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01403 | 107 | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | External | 106.91 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01153 | 105.65 | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | External | 105.6 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01263 | 107.12 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 107.04 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997063 GLENHAM TR1 115 1 | 25 | 31 | 0.00031 | 103.56 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 103.54 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 109.43 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 109.43 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00371 | 120.92 | 63170: 345667 7RUSH 1 345 345857 7TYSON 3 345 1 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 345840 4TAUM S 2 138 345841 1TS G2 13.8 1 345832 1TS G1 13.8 356 1330 1 344822 7JOACHIM 345 345668 7RUSH 2 345 1 345841 1TS G2 13.8 356 1330 2 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 345831 4TAUM S 1 138 345832 1TS G1 13.8 1 345831 4TAUM S 1 138 346145 1TAUM S 34.5 1 | External | 120.86 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.2 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 114.11 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0037 | 120.9 | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | External | 120.76 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.43 | P11:022:NPPD:COOPER1G:1:983 | External | 102.41 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01066 | 115.99 | P23:500:EMI:ABF_PRYVL-B | External | 115.94 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.2 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC | External | 114.11 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0117 | 108.09 | 82344: 635000 CBLUFFS3 345 645456 S3456 3 345 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 108.03 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 123.38 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 123.31 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17687 | 103.63 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal | 102.24 | 1.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.57 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 114.56 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00024 | 100.82 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 100.78 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 117.14 | P11:24:AEPW:TURKCOAL | External | 117.32 | -0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00013 | 116.89 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 116.87 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00357 | 109.2 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 109.1 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00031 | 114.68 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 114.53 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.91 | 300001 1THLG1 20 300120 5THMHILB1 161 1: 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 103.85 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.031 | 101.69 | P22:345:AMMO::OVERTON:1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.41 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 121.39 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00018 | 136.34 | P23:500:EMI-EES:ABF_FRKLN-A | External | 136.34 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00327 | 105.09 | 104532: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 542982 IATAN 7 345 1 | External | 104.9 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92424: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 121.46 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 100.4 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 100.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00104 | 118.06 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 117.96 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00362 | 125.52 | P13:161-345:AMMO::MONTGOMERY:1 | External | 125.44 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.9 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 127.83 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.11 | P11:24:AEPW:PIRKEY 1 | External | 117.11 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00987 | 110.05 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 110.07 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00053 | 109.32 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 109.18 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00065 | 107.93 | P23:345:MEC:HILLS 9114 | External | 107.71 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00034 | 107.86 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 107.89 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01008 | 122.69 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 122.58 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00411 | 124.76 | 104177: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 124.66 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01172 | 101.71 | P13:161:MEC:SE POLK 9T1 | External | 101.63 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 104.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 104.55 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 140.9 | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 138.02 | 2.88
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01011 | 124.24 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 123.95 | 0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01089 | 118.2 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 118.06 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 351 | 0.03534 | 129.08 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 128.6 | 0.48
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01028 | 118.83 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 118.75 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00072 | 106.48 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 106.33 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0107 | 116.83 | P23:500:EAI:NBF_SAN SOUC | External | 116.69 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.0351 | 116.12 | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 115.55 | 0.57
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.06 | 337754 8ETTA% 500 337755 8DUKE HS-1! 500 1: 337754 8ETTA% 500 337755 8DUKE HS-1! 500 1 | External | 148.91 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 140.69 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.69 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.46 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 128.11 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 128.13 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01175 | 120.96 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 120.87 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92432: 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 121.45 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01077 | 116 | 63170: 345667 7RUSH 1 345 345857 7TYSON 3 345 1 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 345840 4TAUM S 2 138 345841 1TS G2 13.8 1 345832 1TS G1 13.8 356 1330 1 344822 7JOACHIM 345 345668 7RUSH 2 345 1 345841 1TS G2 13.8 356 1330 2 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 345831 4TAUM S 1 138 345832 1TS G1 13.8 1 345831 4TAUM S 1 138 346145 1TAUM S 34.5 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00028 | 108.56 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External | 108.16 | 0.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01185 | 119.61 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.12 | P11:138:AMMO::SIOUX:2 | External | 105.85 | 0.27
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01051 | 110.49 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | External | 110.46 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.25 | P11:HV:EES::JTEC GEN#2 1:2 | External | 121.22 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 116.25 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 115.89 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 106.85 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 106.85 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.09 | P11:24:AEPW:TURKCOAL | External | 106.21 | -0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.23 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 102.71 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1 | External | 102.69 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01137 | 107.95 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 107.89 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01137 | 117.76 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 117.7 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01119 | 116.99 | P23:345:XEL:SPS 8S81 SSL | External | 116.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.11 | P12:HV:EES::TURK 4%:1(1) | External | 107.94 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01078 | 115.64 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 115.63 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00521 | 102.62 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00258 | 123.14 | 344327 7LOOSECRK 345 345238 7MARIOSA 345 1: 344327 7LOOSECRK 345 345238 7MARIOSA 345 1 | External | 123.08 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17687 | 100.92 | P12:115:MIDW:RICE-LYONS | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0102 | 106.55 | 82344: 635000 CBLUFFS3 345 645456 S3456 3 345 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 106.47 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01285 | 107.7 | 300076 5FAIRPT 161 300087 5HICKCK 161 1: 300076 5FAIRPT 161 300087 5HICKCK 161 1 | External | 107.55 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0107 | 116.11 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 116.04 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01068 | 116.77 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.61 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01267 | 110.22 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 110.13 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.98 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01173 | 100.96 | P23:345:MEC:GDMEC 904 | External | 100.9 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.4 | 661015 COYOTE1G 24 661016 COYOTE 3 345 1: 661015 COYOTE1G 24.0 661016 COYOTE 3 345 1 | External | 102.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00403 | 132.51 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External | 132.42 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00108 | 106.2 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 106.03 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 115.87 | 92381: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 109.41 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 109.32 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.0109 | 108.7 | P12:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | External | 108.64 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 154.95 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 152.42 | 2.53
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00071 | 106.81 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00018 | 151.25 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 151.19 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01107 | 119.94 | 631085 PARNEL 5 161 636401 HILLS 5 161 1: 631085 PARNEL 5 161 636401 HILLS 5 161 1 | External | 119.8 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00515 | 104.07 | P22:345:AMMO::OVERTON:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.03094 | 101.5 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00056 | 117.24 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 117.29 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.09 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18 1: 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | External | 116.23 | -0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.65 | P12:HV:EES::TURK 4%:1(1) | External | 103.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 108.34 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 108.31 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.05 | P12:HV:EES::5NEWMAD!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 110.02 | Base Case | External | 109.97 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01012 | 123.82 | P23:345:MEC:HILLS 974 | External | 123.69 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 114.57 | Base Case | External | 114.56 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00041 | 110.57 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.62 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01078 | 107.6 | P23:345-161:XEL:ADAMS_I:681_S | External | 107.5 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 6e-05 | 102.81 | 93771: 652426 BISMARK4 230 659128 HERBERTW-KM4 230 1 652444 JAMESTN4 230 659128 HERBERTW-KM4 230 1 652426 BISMARK4 230 652456 WASHBRN4 230 1 652456 WASHBRN4 230 659106 LELAND_O-BE4 230 1 652325 WASHBRN9 41.8 652456 WASHBRN4 230 1 652296 WARD 4 230 652426 BISMARK4 230 1 652426 BISMARK4 230 652444 JAMESTN4 230 1 652426 BISMARK4 230 652466 HILKEN 4 230 1 652426 BISMARK4 230 652499 CAMPBELL 4 230 1 652426 BISMARK4 230 997178 BS KV3A 115 1 652426 BISMARK4 230 997177 BS KV8A 115 1 652426 BISMARK4 230 997185 BS KV3A 115 1 652426 BISMARK4 230 997184 BS KV8A 115 1 652426 BISMARK4 230 997176 BS KV3A 115 1 652426 BISMARK4 230 997175 BS KV8A 115 1 | External | 102.79 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01008 | 123.06 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 122.95 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01097 | 109.14 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 108.99 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 112.61 | 300070 5CLARK 161 541208 NEVADA 5 161 1: 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 112.63 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.16587 | 126.33 | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 125.38 | 0.95
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00519 | 116.24 | P22:345:AMMO::OVERTON:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00589 | 130.78 | 84385: 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541273 KELHYS 2 69.0 541275 SEDPLT 2 69.0 1 | External | 130.69 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 138.79 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 137.83 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01185 | 119.61 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01026 | 122.3 | P21:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 122.28 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.28 | P11:24:AEPW:TURKCOAL | External | 149.49 | -0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.5 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596) | External | 144.5 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.59 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 149.77 | -0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.74 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 127.76 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 5e-05 | 104.64 | 601067 BISON 3 345 620361 MAPLE R3 345 1: 601067 BISON 3 345 620361 MAPLE R3 345 1 | External | 104.62 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01141 | 117.98 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 101.05 | 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22 1: 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 | External | 101.04 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0124 | 107.49 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 158.98 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 158.87 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 130.26 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 129.13 | 1.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00527 | 103.67 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 103.34 | 0.33
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 135.95 | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 136.57 | -0.62
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 105.53 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 105.53 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00068 | 100.93 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 100.75 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 113.94 | 601086 COYOTE RIDGE 345 606131 J432 COY COL 34.5 1: 601086 COYOTE RIDGE 345 606131 J432 COY COL 34.5 1 | External | 113.9 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.73 | P12:HV:EES::PIRKEY 4:1 | External | 116.66 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 117.14 | P11:HV:EES::TURKCOAL:1 | External | 117.32 | -0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05182 | 101.37 | 8612: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | Internal | 101.16 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 128.29 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 128.14 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 117.09 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 117.26 | -0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 149.81 | P23:345:MEC:LOUISA 954 | External | 149.9 | -0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01011 | 115.38 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 115.1 | 0.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.66 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 116.48 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01089 | 108.11 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 107.98 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00364 | 102.91 | 63170: 345667 7RUSH 1 345 345857 7TYSON 3 345 1 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 345840 4TAUM S 2 138 345841 1TS G2 13.8 1 345832 1TS G1 13.8 356 1330 1 344822 7JOACHIM 345 345668 7RUSH 2 345 1 345841 1TS G2 13.8 356 1330 2 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 345831 4TAUM S 1 138 345832 1TS G1 13.8 1 345831 4TAUM S 1 138 346145 1TAUM S 34.5 1 | External | 102.84 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.4 | 300007 1NM G2 22 300046 7NEWMAD 345 1: 300007 1NM G2 22.0 300046 7NEWMAD 345 1 | External | 116.04 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01163 | 109.78 | 83253: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 109.69 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.98 | P11:HV:EES::TURKCOAL:1 | External | 107.13 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.08 | P12:HV:EES::JTEC 5:1 | External | 120.96 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 222.42 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 222.41 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.17 | P12:EHV:EES::WELSH 7:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00106 | 107.47 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 107.38 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 115.18 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 115.08 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00036 | 100.64 | P12:345:XEL:SPS WLM-SSL | External | 100.62 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00352 | 103.08 | 344001 5ADAIR2 161 344004 5ADAIR1 161 Z: 344001 5ADAIR2 161 344004 5ADAIR1 161 Z | External | 103.03 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00221 | 128.61 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 128.58 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 143.51 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 143.54 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15343 | 105.96 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 104.96 | 1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00018 | 151.2 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00727 | 107.4 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 107.37 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01251 | 107.28 | P23:500:EAI:NBF_SAN SOUC | External | 107.19 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.75 | P11:EHV:EES::1DUKE HS S1:1 | External | 115.6 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00361 | 122.56 | P12:138:AMMO::BLAND:OSAGE:6030 | External | 122.48 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 116.25 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 115.89 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.49 | P11:024:DPC:ALMA2:6 | External | 149.49 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 100.73 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External | 100.75 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01012 | 124.16 | P23:345:MEC:HILLS 974 | External | 124.02 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 127.65 | P12:345:MEC:TIFFIN 9T1 SPS | External | 127.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.16587 | 128.48 | 830510: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 127.52 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00369 | 103.17 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0098 | 119.25 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 119.15 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01267 | 110.19 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 110.08 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01092 | 118.17 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 118 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.28 | P12:345:AMMO::MAYWOOD:SUBT:77 | External | 103.25 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.0037 | 103.04 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.2058 | 100.17 | 104291: 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 997917 EMCP TX-1 115 1 532872 EMCPHER6 230 997924 EMCP TX-1 115 1 532872 EMCPHER6 230 997920 EMCP TX-1 115 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.03094 | 101.5 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01068 | 116.51 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.35 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14565 | 131.67 | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 130.79 | 0.88
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.49 | 92381: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01091 | 117.04 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 116.98 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.0019 | 104.52 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 104.43 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01011 | 123.87 | P23:345:MEC:HILLS 984 | External | 123.59 | 0.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.05 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 119.01 | Base Case | External | 118.94 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01068 | 106.29 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 106.14 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.88 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 118.88 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.59 | P23:500:EAI:NBF_SAN SO~1 | External | 149.77 | -0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00034 | 107.27 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 107.3 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01335 | 109.4 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 109.31 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 109.18 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 109.13 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00732 | 108.03 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 108 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.46 | P13:138-24:AEPW:PIRKEY 4 | External | 116.39 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01139 | 117.24 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998392 VALIANT1 138 2 510911 VALIANT7 345 998391 VALIANT3 138 1 510911 VALIANT7 345 998400 VALIANT1 138 2 510911 VALIANT7 345 998399 VALIANT3 138 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 | External | 117.18 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01008 | 114.08 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 113.98 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.28 | P23:345:MEC:TIFFIN 944 | External | 114.43 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00064 | 118.37 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 118.31 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15405 | 102.16 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 101.05 | 1.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 177.76 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 177.8 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 103.26 | P12:161:AMMO-ITC::APANOSE:ADAIR:1 | External | 103.28 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01026 | 122.3 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 122.28 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01185 | 109.29 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.97 | P11:HV:EES::FLINTCR1:1 | External | 120.9 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.15 | P23:345:MEC:HILLS 9114 | External | 151.73 | 0.42
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00108 | 106.65 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 106.75 | -0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.09 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB | External | 116.09 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01267 | 110.19 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 110.08 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.65 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 121.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.4 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 116.04 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.35 | P12:HV:EES::PIRKEY 4:1 | External | 106.3 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.65 | 92453: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 | External | 121.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00388 | 129.38 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 129.3 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.08 | P11:EHV:EES::1PLUM PT U1:1 | External | 120.99 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 156.36 | P12:161:DPC:AUTO-SINGLE:WABACO5:ALMA5:1 | External | 156.28 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0038 | 133.64 | 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 | External | 133.55 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.81 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB | External | 115.81 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00392 | 102.92 | 104088: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.42 | P12:HV:EES::5NEWMAD!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01002 | 110.2 | P23:345:MEC:MADISON CO 901 | External | 110.15 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 113.67 | 635633 ADAIR 5 161 635636 ADAIR B2 9 34.5 1: 635633 ADAIR 5 161 635636 ADAIR B2 9 34.5 1 | External | 113.62 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 112.83 | 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1: 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 112.78 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 102.4 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 102.42 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 110.72 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 110.69 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 127.84 | P12:345:MEC:TIFFIN-ARNOLD | External | 128.15 | -0.31
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00787 | 124.03 | P23:345:MEC:GRIMES 901 | External | 124.08 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00227 | 106.63 | P23:345:MEC:KOSSUTH 904 | External | 106.57 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01313 | 107.52 | P23:345:XEL:SPS 8S81 SSL | External | 107.46 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 158.49 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 158.46 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.83 | P12:EHV:EES::WELSH 7:1 | External | 105.74 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01185 | 109.29 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.65 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 105.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.01 | P12:EHV:EES::8SANS SOUCI%:1 | External | 116.01 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.23 | 92463: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.12 | P11:138:AMMO::SIOUX:2 | External | 102.93 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.31 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 2: 602030 WHT 14 5 161 997625 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997625 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997625 WHT 14 5 13.8 2 602030 WHT 14 5 161 997632 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997632 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997632 WHT 14 5 13.8 2 | External | 106.29 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00376 | 125.3 | P23:345:AMMO::BLAND:V15 | External | 125.23 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01026 | 112.85 | P21:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 112.83 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00096 | 104.18 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 104.14 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.17 | P12:HV:EES::5NEWMAD!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 102.14 | P12:345:WERE:CANR-LATH_345:: | Internal | 101.98 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00403 | 132.51 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External | 132.42 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.005 | 106.75 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 106.64 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 351 | 0.03353 | 130.3 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 129.86 | 0.44
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.08 | P13:138-24:AEPW:TURK 4 | External | 105.97 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 119.99 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 119.9 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 103.05 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 103.11 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01131 | 110.83 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 110.85 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 106.85 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 106.85 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 102.87 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 102.89 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.44 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 144.44 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.28 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC | External | 127.2 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00028 | 112.1 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 112.04 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.95 | 42751: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | Internal | 101.81 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.42 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 127.32 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.98 | 337754 8ETTA% 500 337755 8DUKE HS-1! 500 1: 337754 8ETTA% 500 337755 8DUKE HS-1! 500 1 | External | 120.89 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.03 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 115.94 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 108.59 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 108.54 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 108.34 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 108.31 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 113.89 | P13:161-69:EES-EAI:HERGET:AT2 | External | 113.88 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01135 | 113.04 | P23:345:MEC:NORWALK 901 | External | 113.03 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01026 | 121.97 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 121.96 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 101.06 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:GDMEC:1 | External | 100.99 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 112.6 | 84404: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 | External | 112.63 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00512 | 118.24 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 118.16 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 108.54 | 84406: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 108.5 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 119.06 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 119.04 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.69 | P11:24:AEPW:PIRKEY 1 | External | 106.68 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 103.78 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 103.83 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00094 | 113.62 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 113.59 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01239 | 107.26 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1: 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | External | 107.26 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0041 | 124.36 | 104529: 541205 BLSPE 5 161 541211 BLSPS 5 161 1 541206 PRALEE 5 161 541211 BLSPS 5 161 1 541205 BLSPE 5 161 541226 GRAINVL5 161 1 | External | 124.27 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.03096 | 101.6 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 101.04 | 0.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00022 | 102.98 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External | 102.93 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.35 | P13:138-24:AEPW:PIRKEY 4 | External | 106.3 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.03 | P11:23:EES-EAI:PLUM17:1 | External | 116.03 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01152 | 116.41 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 116.19 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01026 | 112.85 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 112.83 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01261 | 107.89 | P23:345-161:XEL:ADAMS_I:681_S | External | 107.8 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15174 | 101.33 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal | 100.37 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 110.34 | 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1: 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1 | External | 110.29 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0107 | 116.82 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 116.99 | -0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01153 | 115.98 | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | External | 115.93 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00058 | 108.6 | P12:115:XEL:AUTO-SINGLE:CRYSTAL7:RIVFLSN7:1 | External | 108.52 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 101.34 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 101.34 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01552 | 111.78 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 120.55 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 120.41 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01267 | 109.41 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 109.39 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01264 | 107.02 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 106.95 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01175 | 121.27 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 121.17 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00026 | 108.67 | P23:345-161:XEL:ADAMS_I:681_S | External | 108.58 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14565 | 129.84 | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 128.9 | 0.94
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 108.69 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 108.64 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 154.52 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 153.39 | 1.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.65 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 101.66 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 100.18 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 100.18 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01107 | 110.43 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 110.31 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.53 | P12:345:MEC:TIFFIN-ARNOLD | External | 118.77 | -0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.28 | 345435 7MAYWOOD 345 636645 SUB T HSK 3 345 1: 345435 7MAYWOOD 345 636645 SUB T HSK 3 345 1 | External | 103.25 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00032 | 114.36 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External | 114.38 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.0109 | 108.7 | 635640 NORWLK3 345 635650 SE POLK 3 345 1: 635640 NORWLK3 345 635650 SE POLK 3 345 1 | External | 108.64 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.35 | 92465: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External | 121.36 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.09 | P11:HV:EES::TURKCOAL:1 | External | 106.21 | -0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 112.23 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 112.08 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 109.34 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 109.31 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.89 | P11:HV:EES::PIRKEY 1:1 | External | 107.87 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.99 | P23:345:MEC:HILLS 924 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.02 | P11:EHV:EES::1DUKE HS S1:1 | External | 115.87 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.07 | 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1: 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1 | External | 107.99 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.28 | P12:345:MEC:TIFFIN-ARNOLD | External | 114.43 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 102.12 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 102.13 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00425 | 150.65 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 150.54 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 106.5 | P23:500:EAI:NBF_SAN SO~1 | External | 106.64 | -0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.73 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 102.74 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01207 | 112.38 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 112.14 | 0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.58 | 338187 8DELL% 500 338340 8CC_DELL 500 1: 338187 8DELL% 500 338340 8CC_DELL 500 1 | External | 105.47 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 102.88 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 102.99 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 116.28 | 63170: 345667 7RUSH 1 345 345857 7TYSON 3 345 1 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 345840 4TAUM S 2 138 345841 1TS G2 13.8 1 345832 1TS G1 13.8 356 1330 1 344822 7JOACHIM 345 345668 7RUSH 2 345 1 345841 1TS G2 13.8 356 1330 2 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 345831 4TAUM S 1 138 345832 1TS G1 13.8 1 345831 4TAUM S 1 138 346145 1TAUM S 34.5 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 115.62 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 115.49 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.7 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB | External | 105.68 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.65 | P13:138-24:AEPW:TURK 4 | External | 103.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.38 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 116.2 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.42 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 127.32 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00335 | 128.8 | P12:161:KCPL:AECINORTON-KCPLNORTON-MARSHALLJCT | External | 128.72 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01121 | 117.39 | P23:345:XEL:8S25 WLM AS | External | 117.28 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00035 | 100.95 | P23:345:XEL:8S25 WLM AS | External | 100.9 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.15 | 338187 8DELL% 500 338340 8CC_DELL 500 1: 338187 8DELL% 500 338340 8CC_DELL 500 1 | External | 116.03 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 154.71 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 153.62 | 1.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.35 | P13:69-161:AECI-ALTW:AUTO-SINGLE:2HENRY:HENRYCO5:1 | External | 102.39 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00221 | 127.37 | 104649: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 119.53 | 7.84
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00355 | 112.76 | 300076 5FAIRPT 161 300107 5OSBORN 161 1: 300076 5FAIRPT 161 300107 5OSBORN 161 1 | External | 112.69 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 102.86 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.42 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 127.32 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01114 | 117.81 | P23:345:XEL:SPS 8S72 HNA | External | 117.67 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 158.49 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 158.46 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01185 | 119.91 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 115.68 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 115.62 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0119 | 115.72 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 115.57 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 110.25 | 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2: 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2 | External | 110.18 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01121 | 117.67 | P23:345:XEL:8S25 WLM AS | External | 117.56 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.11 | P11:HV:EES::PIRKEY 1:1 | External | 117.11 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 137.83 | Base Case | External | 137.78 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.22 | 92386: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 121.37 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01459 | 107.25 | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | External | 107.24 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00357 | 108.3 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00388 | 129.62 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 129.55 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01313 | 107.6 | P12:345:XEL:SPS WLM-SSL | External | 107.53 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00392 | 102.94 | 104081: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 | External | 102.85 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 154.01 | P12:161:ALTW-MEC:AUTO-SINGLE:EMERY5:FLOYD5:1 | External | 154.08 | -0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01606 | 107.93 | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300099 5MONTCT 161 300523 5WLMSBG 161 1 | 273 | 273 | 0.00348 | 101.39 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External | 102.73 | -1.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00408 | 125.76 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 125.69 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.49 | 603307 J512 ZEPHYR7 115 605577 J512_MAINTR 115 Z1: 603307 J512 ZEPHYR7 115 605577 J512_MAINTR 115 Z1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01085 | 110.53 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 110.4 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.23 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 116.19 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.0001 | 106.11 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 106.12 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15187 | 106.1 | Base Case | Internal | 104.78 | 1.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.4 | 104890: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 144.3 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.46 | P12:HV:EES::PIRKEY 4:1 | External | 116.39 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 111.95 | P12:161:XEL:AUTO-SINGLE:LAWCRK5:STCROIG:1 | External | 111.89 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18724 | 102.25 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal | 101.03 | 1.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 113.93 | 635633 ADAIR 5 161 635634 ADAIR B1 9 34.5 1: 635633 ADAIR 5 161 635634 ADAIR B1 9 34.5 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00518 | 116.7 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00426 | 126.42 | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | External | 126.91 | -0.49
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01139 | 117.51 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998392 VALIANT1 138 2 510911 VALIANT7 345 998391 VALIANT3 138 1 510911 VALIANT7 345 998400 VALIANT1 138 2 510911 VALIANT7 345 998399 VALIANT3 138 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 | External | 117.45 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01175 | 110.56 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 110.46 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 114.92 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 114.82 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 100.81 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 100.83 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00531 | 102.4 | 104653: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 | External | 102.27 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.07 | P13:500:EES-EAI:ND:8SANS SOUCI%:1 | External | 120.99 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 113.67 | 635633 ADAIR 5 161 635634 ADAIR B1 9 34.5 1: 635633 ADAIR 5 161 635634 ADAIR B1 9 34.5 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01169 | 114.63 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 114.54 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00364 | 123.43 | 104212: 542972 HAWTH 7 345 997748 HAWTHORN22 161 22 542972 HAWTH 7 345 997749 HAWTHORN20 161 20 542972 HAWTH 7 345 997755 HAWTHORN22 161 22 542972 HAWTH 7 345 997756 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | External | 123.32 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00548 | 102.6 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 102.51 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.22 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 121.32 | -0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.75 | P12:EHV:EES::8COTNWOOD2!:8HARTBRG%:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 100.18 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 100.18 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92382: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 121.45 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01153 | 115.71 | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | External | 115.66 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.27 | P12:HV:EES::TURK 4%:1(1) | External | 149.18 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.08 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 107.05 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.93 | 92478: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External | 101.94 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 109.08 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 109.12 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 161.14 | P12:161:DPC:ALM-ROC | External | 161.04 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.51 | P11:138:AMMO::SIOUX:2 | External | 116.2 | 0.31
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01098 | 108.23 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 108.26 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 127.57 | 84410: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 119.7 | 7.87
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.1 | P11:345:AMMO::RUSHISLAND:U1 | External | 115.85 | 0.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.26 | P11:345:AMMO::RUSHISLAND:U2 | External | 116.7 | -0.44
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01006 | 127.61 | P23:345:MEC:TIFFIN 954 | External | 127.91 | -0.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.98 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.99 | 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1: 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1 | External | 107.89 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 6e-05 | 120.01 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 120.04 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.95 | 42750: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | Internal | 101.81 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01152 | 106.03 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 105.85 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.82 | P12:EHV:EES::WELSH 7:1(1) | External | 105.74 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 120.28 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 120.18 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 100.91 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 100.9 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 109.38 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 109.39 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.08 | P11:HV:EES::1NELSON_G6!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01078 | 117.89 | P23:345-161:XEL:ADAMS_I:680_S | External | 117.78 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.29 | 344012 7HPW-N 345 344013 7HPW-S 345 1: 344012 7HPW-N 345 344013 7HPW-S 345 1 | External | 108.22 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 5e-05 | 105.64 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.64 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00023 | 156.66 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9: 601002 ADAMS 3 345 997679 ADAMS 3 161 9 631046 ADAMS 5 161 997679 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997679 ADAMS 3 161 9 601002 ADAMS 3 345 997686 ADAMS 3 161 9 631046 ADAMS 5 161 997686 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997686 ADAMS 3 161 9 601002 ADAMS 3 345 997682 ADAMS 3 161 9 631046 ADAMS 5 161 997682 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997682 ADAMS 3 161 9 | External | 156.63 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00031 | 114.76 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 114.61 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 112.61 | 104644: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 112.63 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01097 | 118.97 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 118.81 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01166 | 109.01 | P42:345:MEC-OPPD:S3456-S3458&CBL | External | 108.94 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 113.89 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 113.88 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00984 | 118.67 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 118.58 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.83 | P11:HV:EES::PIRKEY 1:1 | External | 116.83 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.7 | P12:HV:EES::5NEWMAD!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00059 | 110.29 | 71568: 601024 TERMINL3 345 997652 90198-B 115 10 603110 TERMINL7 115 997652 90198-B 115 10 605516 TERTER19 34.5 997652 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997659 C0512551 115 9 603084 KOLMNLK7 115 997659 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997659 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 601024 TERMINL3 345 997659 90198-B 115 10 603110 TERMINL7 115 997659 90198-B 115 10 605516 TERTER19 34.5 997659 90198-B 115 10 601021 KOLMNLK3 345 997666 C0512551 115 9 603084 KOLMNLK7 115 997666 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997666 C0512551 115 9 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 | External | 110.19 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01052 | 115.43 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 115.39 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 108.93 | P11:024:DPC:ALMA2:6 | External | 108.93 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.08956 | 104.44 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 103.66 | 0.78
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 103.64 | 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1: 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.21 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 114.21 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 102.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | External | 102.49 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01272 | 117.5 | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.1 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 102.12 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00355 | 121.32 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 121.23 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.012 | 114.41 | P23:345:MEC:TIFFIN 954 | External | 114.55 | -0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15405 | 104.25 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 103.16 | 1.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01098 | 118.61 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 118.67 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01121 | 107.61 | P23:345:XEL:8S25 WLM AS | External | 107.51 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00021 | 112.84 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 112.79 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.69 | P11:HV:EES::PIRKEY 1:1 | External | 106.68 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.06 | P11:23:EES-EAI:PLUM17:1 | External | 149.11 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.93 | 338187 8DELL% 500 338340 8CC_DELL 500 1: 338187 8DELL% 500 338340 8CC_DELL 500 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.0372 | 113.33 | P23:345:WERE:SWIS_345-5:: | Internal | 113.25 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01141 | 118.06 | P23:345:MEC:KOSSUTH 904 | External | 117.99 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00957 | 118.4 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | External | 118.38 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00056 | 117.24 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 117.29 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 112.23 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 112.08 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00058 | 109.61 | P12:115:XEL:AUTO-SINGLE:WILOWRV7:THREELAKES7:1 | External | 109.6 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.78 | 104278: 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532800 LATHAMS7 345 532801 ELKRVR17 345 1 | Internal | 101.65 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01086 | 116.86 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 116.78 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.10276 | 120.62 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | Internal | 118.8 | 1.82
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01552 | 111.78 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 132.05 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 131.05 | 1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.31 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 103.22 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00426 | 126.42 | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | External | 126.91 | -0.49
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01008 | 122.69 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 122.58 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00055 | 107.86 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 107.82 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00409 | 138.27 | 300090 5KINGDM 161 300043 7KINGDM 345 1: 300090 5KINGDM 161 300043 7KINGDM 345 1 | External | 138.2 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.89 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 105.84 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01105 | 110.31 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 110.35 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01186 | 119.69 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 118.83 | 0.86
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 132.05 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 131.05 | 1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 100.91 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 100.9 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.7 | P23:345:WERE:CANR_BKRS:: | Internal | 101.57 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01114 | 107.83 | P23:345:XEL:SPS 8S72 HNA | External | 107.69 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 120.85 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 120.7 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.20294 | 101.09 | P12:230:WERE:CIRC-EMCP_230:: | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05182 | 101.37 | 104266: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | Internal | 101.16 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00034 | 100.66 | P23:345:XEL:SPS 8S81 SSL | External | 100.63 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01315 | 107.69 | P23:345:XEL:8S27 WLM AS | External | 107.8 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.27 | P12:EHV:EES::8SANS SOUCI%:1 | External | 116.27 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 101.05 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External | 101.04 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0001 | 110.48 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 110.48 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.09 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.012 | 112.28 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 112.17 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01107 | 120.22 | 631085 PARNEL 5 161 636401 HILLS 5 161 1: 631085 PARNEL 5 161 636401 HILLS 5 161 1 | External | 120.08 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01121 | 117.38 | P23:345:XEL:8S27 WLM AS | External | 117.58 | -0.2
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00019 | 107.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.25 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 100.69 | P12:345:WERE:LATH-ROSE_345:: | Internal | 100.5 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 100.67 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External | 100.68 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00027 | 101.85 | 620363 FORMAN 4 230 3WXFMR 230/115 1: 620363 FORMAN 4 230 997498 230/115 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 620363 FORMAN 4 230 997505 230/115 115 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 | External | 101.83 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00403 | 131.19 | P12:161:AECI:M:HUNTSDL:C_PERCH:1 | External | 131.09 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00446 | 125.09 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 125.01 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01121 | 111.39 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 112.02 | -0.63
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00022 | 102.98 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 102.93 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0107 | 116.82 | P23:500:EAI:NBF_SAN SO~1 | External | 116.99 | -0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00388 | 129.03 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 128.94 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00063 | 118.16 | P12:161:DPC:RCE-HAR5 | External | 118.1 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.31 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 116.27 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.42 | P11:24:AEPW:TURKCOAL | External | 117.61 | -0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 128.35 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 128.14 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00036 | 119.35 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 118.8 | 0.55
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01155 | 109.02 | 82320: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 645456 S3456 3 345 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 | External | 108.97 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.37 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 107.18 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01078 | 117.61 | P23:345-161:XEL:ADAMS_I:680_S | External | 117.51 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 111.28 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.28 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.08 | P11:23:EES-EAI:PLUM17:1 | External | 120.99 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.73 | P13:138-24:AEPW:PIRKEY 4 | External | 116.66 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01026 | 112.85 | 636400 HILLS 3 345 636420 TIFFIN 3 345 1: 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | External | 112.83 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01085 | 110 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 109.91 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.2 | 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1: 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1 | External | 102.19 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.54 | P12:HV:EES::PIRKEY 4:1 | External | 107.52 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00093 | 112.17 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 112.14 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.96 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT | External | 115.92 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01141 | 118.31 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01139 | 107.17 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998392 VALIANT1 138 2 510911 VALIANT7 345 998391 VALIANT3 138 1 510911 VALIANT7 345 998400 VALIANT1 138 2 510911 VALIANT7 345 998399 VALIANT3 138 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 | External | 107.12 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00306 | 102.89 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.45 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 149.11 | 0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 100.4 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 100.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997621 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00061 | 118.31 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 118.22 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15174 | 103.12 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal | 102.13 | 0.99
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00984 | 108.49 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 108.41 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337600 3REED% 115 337602 3DUMAS% 115 1 | 106 | 106 | 0.00018 | 109.13 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.12 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.66 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 101.57 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00547 | 102.33 | 104253: 542969 STILWEL5 161 543126 LACKMAN5 161 1 300071 5CLINTN 161 542969 STILWEL5 161 1 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | External | 102.25 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.38 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 149.19 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.2 | P12:345:MEC:TIFFIN 9T1 SPS | External | 114.11 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 111.37 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 111.29 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0001 | 103.29 | P23:345:XEL:8N22 SHC | External | 103.27 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.012 | 112.28 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 112.17 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.07 | P12:EHV:EES::WELSH 7:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 157.95 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 154.87 | 3.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01207 | 112.38 | P23:345:MEC:HILLS 984 | External | 112.14 | 0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.26 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 116.38 | -0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 112.79 | P12:115:XEL:CHI-LIN-SHF-LCR | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 109.08 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 109.12 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00036 | 110.74 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 110.71 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.67 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 101.69 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 103.43 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 103.37 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.66 | P11:345:AMMO::RUSHISLAND:U2 | External | 106.04 | -0.38
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.77 | P11:HV:EES::1NELSON_G6!:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 146.57 | Base Case | External | 146.55 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.56 | 92455: 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External | 121.47 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.16587 | 126.01 | 830510: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 125.14 | 0.87
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00067 | 100.6 | 631083 TRAER 5 161 631086 DYSART 5 161 1: 631083 TRAER 5 161 631086 DYSART 5 161 1 | External | 100.45 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 117.42 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01052 | 115.69 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 115.65 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17035 | 102.33 | P12:115:WERE:RENO-WMCP_115:: | Internal | 100.96 | 1.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01028 | 108.47 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 108.39 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00221 | 127.37 | 84408: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 119.53 | 7.84
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 113.41 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:APANOSE5:1 | External | 113.44 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01078 | 107.6 | P23:345-161:XEL:ADAMS_I:680_S | External | 107.5 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00521 | 102.62 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.37 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External | 121.27 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.01 | 345668 7RUSH 2 345 345671 1RUSH G2 18 1: 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | External | 105.85 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 117.12 | P12:HV:EES::TURK 4%:1(1) | External | 116.96 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00372 | 103.72 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 103.65 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01554 | 111.86 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 111.57 | 0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00381 | 122.64 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 122.57 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.31 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 149.31 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.67 | P13:13-13-161:XEL:AUTO-SINGLE:WHT51G:WHT52G:WHT145:1 | External | 106.65 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 138.64 | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 139.66 | -1.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 130.26 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 129.13 | 1.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997481 WEB AB 161 1 | 560 | 560 | 0.00349 | 104.21 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 104.14 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 138.31 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 137.35 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01078 | 115.35 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 115.34 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00984 | 118.36 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 118.27 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0098 | 119.57 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 119.46 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00019 | 110.87 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.86 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 127.65 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC | External | 127.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 127.57 | 104651: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 119.7 | 7.87
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 119.35 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 119.32 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01201 | 114.57 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 114.56 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00108 | 106.2 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 106.03 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01006 | 127.98 | P23:345:MEC:TIFFIN 954 | External | 128.28 | -0.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 102.4 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 102.42 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00556 | 103.38 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 103.29 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00085 | 108.04 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 107.99 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.45 | 300007 1NM G2 22 300046 7NEWMAD 345 1: 300007 1NM G2 22.0 300046 7NEWMAD 345 1 | External | 149.11 | 0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.11 | P11:24:AEPW:PIRKEY 1 | External | 149.08 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01091 | 117.32 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 117.25 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01121 | 107.36 | P23:345:XEL:8S27 WLM AS | External | 107.52 | -0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15174 | 101.33 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal | 100.37 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00077 | 101.92 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 101.88 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01335 | 109.51 | P23:345:MEC:KOSSUTH 904 | External | 109.44 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 128.81 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 128.73 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01119 | 117.35 | P12:345:XEL:SPS WLM-SSL | External | 117.29 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.51 | P11:345:MEC-NPPD:COOPER 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00369 | 103.17 | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1: 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 103.1 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.7 | P11:HV:EES::1NM G1:1 | External | 116.07 | 0.63
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.85 | 335190 6NELSON% 230 335206 1NELSON_G6! 20 1: 335190 6NELSON% 230 335206 1NELSON_G6! 20.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.89 | P12:EHV:EES::WELSH 7:1(1) | External | 115.81 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.06 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 104.96 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.17 | P12:EHV:EES::WELSH 7:1(1) | External | 116.08 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00372 | 103.72 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 103.65 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.0109 | 108.7 | P21:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | External | 108.64 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00034 | 100.63 | P12:345:XEL:SPS HNA-SSL | External | 100.6 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01216 | 108.55 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 108.44 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 102.38 | P23:345:AMIL::HERLEMAN:3 | External | 102.43 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.28 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 127.2 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01261 | 106.58 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 106.48 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.99 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 116.1 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 108.11 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 108.07 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01152 | 116.13 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 115.92 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01052 | 105.54 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 105.48 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 103.78 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 103.83 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01186 | 119.98 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 119.13 | 0.85
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0041 | 124.36 | P23:161-345:GMO:BLUESPRINGSE_R4-12::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 124.27 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 126.59 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 126.59 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 116.38 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 116.31 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 116.48 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 116.43 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14565 | 130.38 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 129.45 | 0.93
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00013 | 116.89 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 116.87 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.19594 | 103.41 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 101.96 | 1.45
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01091 | 117.32 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 117.25 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.005 | 106.75 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 106.64 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.6 | P23:500:EAI:NBF_SAN SOUC | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.00094 | 113.62 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 113.59 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00395 | 103.75 | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | External | 104.09 | -0.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17337 | 106.66 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 105.32 | 1.34
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 113.41 | 631110 WAPELLO5 161 631112 APANOSE5 161 1: 631110 WAPELLO5 161 631112 APANOSE5 161 1 | External | 113.44 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01131 | 120.16 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 120.23 | -0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.4 | P12:HV:EES::TURK 4%:1(1) | External | 117.24 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0003 | 102.19 | P23:345:XEL:SPS 8S72 HNA | External | 102.1 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.08 | P12:HV:EES::TURK 4%:1(1) | External | 105.97 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00376 | 121.85 | 63177: 344154 7BLAND 345 344885 7LABADIE2 345 1 344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00371 | 104.26 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11 | External | 103.5 | 0.76
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01078 | 105.6 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 105.58 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0037 | 120.55 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 120.46 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.48 | P12:345:MEC:TIFFIN-ARNOLD | External | 127.78 | -0.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 102.12 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 102.13 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00096 | 104.18 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 104.14 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 139.96 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 139.96 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 9e-05 | 112.2 | P23:345:GRE:PVS 19JB1 | External | 112.35 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 118.88 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 118.84 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00101 | 102.4 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 102.42 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01078 | 117.61 | P23:345-161:XEL:ADAMS_I:681_S | External | 117.51 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00034 | 101 | 105811: 620263 FORMN 7 115 652438 FORMAN 7 115 1 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1 652438 FORMAN 7 115 652462 ELLIOTT7 115 1 652438 FORMAN 7 115 659172 LUDDEN -CP7 115 1 652438 FORMAN 7 115 997172 FO KY1A 69.0 1 652439 FORMAN 8 69.0 655630 COGSWELL-CP8 69.0 1 652327 FORMAN 9 41.8 652439 FORMAN 8 69.0 1 652439 FORMAN 8 69.0 997172 FO KY1A 69.0 1 652393 FORMAN9 12.5 997172 FO KY1A 69.0 1 620262 GWINNER7 115 620263 FORMN 7 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 652438 FORMAN 7 115 997179 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997179 FO KY1A 69.0 1 652393 FORMAN9 12.5 997179 FO KY1A 69.0 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 652438 FORMAN 7 115 997170 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997170 FO KY1A 69.0 1 652393 FORMAN9 12.5 997170 FO KY1A 69.0 1 | External | 100.99 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 130.26 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 129.13 | 1.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00152 | 101.38 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.38 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.45 | 672621 SHAND 4 230 672321 SHAND 1G 18 1: 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | External | 144.45 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.05 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 109.41 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 109.32 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00015 | 102.21 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 102.21 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.07 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB | External | 116.13 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01141 | 108.49 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05318 | 100.6 | P23:345:WERE:SWIS_345-5:: | Internal | 100.51 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15396 | 102.16 | P42:345:SPS:FINNEY_OR70_19L | Internal | 101.05 | 1.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00227 | 106.54 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 106.18 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 109.52 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.48 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 104.84 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 104.85 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01008 | 122.69 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 122.58 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 112.07 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 111.91 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00013 | 102.32 | P23:345:XEL:8N28 SHC | External | 102.32 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00104 | 118.06 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 117.96 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.44 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 103.42 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.0042 | 105.03 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 104.9 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 109.78 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 109.57 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01119 | 107.31 | P12:345:XEL:SPS WLM-SSL | External | 107.25 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.95 | 92448: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 155.39 | P13:161-34:ALTW-WPS:AUTO-SINGLE:RICE5:G551_TAP:1 | External | 155.35 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.05 | P11:HV:EES::1NM G1:1 | External | 105.49 | 0.56
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 154.19 | P13:069:MEC:FLOYD AB | External | 154.22 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01279 | 107.96 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 107.91 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00072 | 116.89 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 116.88 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00057 | 108.46 | P23:345:MEC:TIFFIN 944 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.91 | P11:EHV:EES::1TRACTBEL C1:1 | External | 120.93 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 117.45 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 117.09 | P23:500:EAI:NBF_SAN SOUC | External | 116.96 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.8 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB | External | 115.85 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00222 | 128.29 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 128.14 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00376 | 122.09 | P22:345:AMMO::RUSHISLAND:2 | External | 122.05 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.42 | P11:EHV:EES::1DUKE HS S1:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.09299 | 104.12 | P13:115-230:MIDW:RICE COUNTY | Internal | 103.27 | 0.85
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15343 | 103.92 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 102.96 | 0.96
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0098 | 109.3 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 109.22 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.97 | P11:22:AEPW:FLINTCR1 | External | 120.9 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.38 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC | External | 118.3 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.11 | P11:HV:EES::PIRKEY 1:1 | External | 149.08 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00364 | 123.43 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 | External | 123.32 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00036 | 119.35 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 118.8 | 0.55
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.43 | 92482: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.41 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00071 | 102.28 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 102.29 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 5e-05 | 104.62 | P12:345:MPC:BISON-MAPLE RIVER:BISON 3:MAPLE R3 | External | 104.6 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.52 | 105877: 659105 LELAND_O-BE3 345 659111 LELAND_2-BEG 20.0 1 | External | 144.52 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.12 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 107.18 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 136.7 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 135.65 | 1.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 120.85 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 120.7 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 105.73 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 105.66 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.08 | P11:20:EES:NELSON_E:1 | External | 148.91 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01091 | 106.92 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 106.87 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 110.92 | 344011 7HUGHES 345 344012 7HPW-N 345 1: 344011 7HUGHES 345 344012 7HPW-N 345 1 | External | 110.81 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 102.71 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External | 102.69 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.67 | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1: 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00021 | 112.84 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 112.79 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 103.13 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 103.1 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 160.93 | 681532 WABACO 5 161 681537 ROCHSTR5 161 1: 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | External | 160.74 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.76 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 115.68 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.57 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 116.52 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 100.98 | 635650 SE POLK 3 345 635690 GDMEC 3 345 1: 635650 SE POLK 3 345 635690 GDMEC 3 345 1 | External | 100.9 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01107 | 120.22 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 120.08 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01089 | 117.94 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 117.81 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01038 | 111.23 | 635635 MADISON3 345 635640 NORWLK3 345 1: 635635 MADISON3 345 635640 NORWLK3 345 1 | External | 111.17 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05337 | 100.44 | 84583: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | Internal | 100.22 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 222.42 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 222.41 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04291 | 101.78 | P23:345:WERE:LATH_BKRS:: | Internal | 101.65 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.95 | P12:HV:EES::TURK 4%:1(1) | External | 106.81 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 100.91 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 100.9 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00053 | 109.8 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 109.66 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.36 | P11:HV:EES::1NM G1:1 | External | 121.27 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00701 | 102.47 | P23:345:MEC:SYCAMORE 906 | External | 102.41 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01186 | 109.37 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 108.62 | 0.75
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.66 | P11:24:AEPW:TURKCOAL | External | 103.74 | -0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.99 | P22:345:MEC:SUB T | External | 103.98 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 142.08 | P11:024:DPC:ALMA2:6 | External | 142.08 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00258 | 123.14 | P12:345:AMMO::LOOSECREEK:MARIOSADELTA:1 | External | 123.08 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.07 | P12:EHV:EES::8SANS SOUCI%:1 | External | 120.99 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 128.76 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 128.86 | -0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01119 | 117.28 | P23:345:XEL:SPS 8S81 SSL | External | 117.19 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01261 | 107.89 | P23:345-161:XEL:ADAMS_I:680_S | External | 107.8 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.98 | P11:24:AEPW:TURKCOAL | External | 107.13 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.43 | 104890: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 102.41 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 110.47 | 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1: 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1 | External | 110.42 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | 717.1 | 717.1 | 0.03177 | 100.14 | P23:345:WERE:RENO_345-160:: | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 104.09 | P23:345:MEC:LOUISA 964 | External | 104.06 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00548 | 102.6 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 102.51 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 105.73 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 105.66 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 108.93 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 108.93 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01091 | 106.92 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 106.87 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 5e-05 | 105.78 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.78 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17337 | 104.59 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 103.29 | 1.3
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01086 | 106.75 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 106.68 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 7e-05 | 149.08 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 148.98 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00026 | 108.67 | P23:345-161:XEL:ADAMS_I:680_S | External | 108.58 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 142.08 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 142.08 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 110.56 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 110.59 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01218 | 110.6 | 636400 HILLS 3 345 636420 TIFFIN 3 345 1: 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | External | 110.59 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01008 | 123.06 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 122.95 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01186 | 114.25 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 114.22 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01314 | 119.59 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 118.83 | 0.76
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00732 | 108.03 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 108 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.0351 | 116.12 | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 115.55 | 0.57
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01011 | 107.54 | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.82 | P12:HV:EES::FLINTCR5:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0001 | 110.48 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 110.48 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 117.78 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 117.74 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.46 | P11:HV:EES::1NM G1:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01131 | 119.79 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 119.86 | -0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00727 | 107.4 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 107.37 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.29 | P11:23:EES-EAI:PLUM17:1 | External | 116.29 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 103.43 | P13:161-345:AMMO::ZACHARY:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 104.04 | P23:345:MEC:HILLS 914 | External | 104.01 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 118.03 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00392 | 103.73 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997749 HAWTHORN20 161 20 542972 HAWTH 7 345 997756 HAWTHORN20 161 20 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | External | 103.75 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.92 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 106 | -0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01092 | 118.43 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 118.26 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00547 | 102.47 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External | 102.38 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00957 | 117.01 | P23:345:MEC:ATCHISON CO 903 | External | 116.91 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0019 | 109.38 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.39 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 106.5 | P23:500:EAI:NBF_SAN SOUC | External | 106.37 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.17 | P11:HV:EES::1NM G1:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 127.65 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 127.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 5e-05 | 104.64 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:MAPLER3:1 | External | 104.62 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01066 | 116.25 | P23:500:EMI:ABF_PRYVL-B | External | 116.2 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 159.35 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 159.22 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01267 | 109.79 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 109.64 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.73 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 120.84 | -0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 101.06 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:GDMEC:1 | External | 100.99 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0052 | 123.34 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 122.95 | 0.39
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00022 | 102.98 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 102.93 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.69 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB | External | 105.72 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 102.68 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 102.63 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01119 | 117.04 | P12:345:XEL:SPS HNA-SSL | External | 116.97 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.03685 | 113.91 | 8612: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | Internal | 113.69 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 126.65 | 104501: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 126.57 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01107 | 110.43 | 631085 PARNEL 5 161 636401 HILLS 5 161 1: 631085 PARNEL 5 161 636401 HILLS 5 161 1 | External | 110.31 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14565 | 129.07 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 128.09 | 0.98
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.42 | P11:HV:EES::TURKCOAL:1 | External | 117.61 | -0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 156.36 | 681532 WABACO 5 161 681543 ALMA 5 161 1: 681532 WABACO 5 161 681543 ALMA 5 161 1 | External | 156.28 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.21 | P13:161-69:EES-EAI:HERGET:AT1 | External | 114.21 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01326 | 111.71 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 111.68 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 106.07 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 106.02 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00732 | 108.03 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 108 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 100.87 | Base Case | External | 100.82 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.69 | P12:EHV:EES::8SANS SOUCI%:1 | External | 105.67 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00227 | 106.54 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 106.18 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.86 | 345407 4OSG_7&8TAP 138 345399 1OSAGE 7&8 13.8 1: 345407 4OSG_7&8TAP 138 345399 1OSAGE 7&8 13.8 1 | External | 120.79 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997481 WEB AB 161 1 | 560 | 560 | 0.00349 | 102.95 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 102.88 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01313 | 107.56 | P12:345:XEL:SPS HNA-SSL | External | 107.5 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.26 | 603271 FARIBALT GEN 115 600050 FEP CT G 18 1: 603271 FARIBALT GEN 115 600050 FEP CT G 18.0 1 | External | 102.25 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00019 | 103.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 103.78 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01534 | 113.09 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 112.98 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00957 | 116.73 | P23:345:MEC:ATCHISON CO 903 | External | 116.63 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00585 | 130.62 | 104628: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 300082 5GEORGE 161 541209 SEDALIA5 161 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541271 SEDN 2 69.0 541273 KELHYS 2 69.0 1 | External | 130.53 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 106.26 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 106.32 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.54 | 92415: 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 121.45 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 102.68 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 102.63 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.36 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18 1: 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | External | 116.51 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00424 | 121.09 | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | External | 121.02 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00362 | 125.52 | 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1: 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1 | External | 125.44 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00029 | 137.99 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 138.05 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.08 | 335190 6NELSON% 230 335206 1NELSON_G6! 20 1: 335190 6NELSON% 230 335206 1NELSON_G6! 20.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01038 | 111.23 | P21:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 111.17 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.37 | P12:HV:EES::5NEWMAD!:1 | External | 121.27 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 112.47 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 112.48 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.42 | 92485: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.4 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01534 | 113.09 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 112.98 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 111.19 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 111.1 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00063 | 109.99 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 109.79 | 0.2
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.36 | 92487: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 102.36 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01045 | 111.49 | 69833: 631078 WNTRST 5 161 635641 NORWLK5 161 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635635 MADISON3 345 635640 NORWLK3 345 1 | External | 111.39 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 139.14 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 138.08 | 1.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00633 | 105.21 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 105.2 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01085 | 120.55 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 120.41 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.27 | P13:138-24:AEPW:TURK 4 | External | 149.18 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 114.54 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 114.52 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00403 | 131.19 | 300500 5HUNTSDL 161 343004 5PERCHE 161 1: 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | External | 131.09 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00149 | 100.7 | Base Case | External | 100.61 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 2e-05 | 115.48 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 115.1 | 0.38
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.08 | P11:345:AMMO::RUSHISLAND:U1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 102.43 | P12:161:AMMO-AECI::SOUTHRIVER:ADAIR:1 | External | 102.44 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.74 | P11:HV:EES::1GYP U3!:1 | External | 120.74 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.66 | P11:HV:EES::TURKCOAL:1 | External | 103.74 | -0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 104.7 | Base Case | External | 104.68 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 103.51 | P11:HV:EES::PIRKEY 1:1 | External | 103.48 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.42 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.71 | P11:23:EES-EAI:PLUM17:1 | External | 105.7 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.4 | 627062 BISON 3 345 627063 GLDN PLNS3 345 1: 627062 BISON 3 345 627063 GLDN PLNS3 345 1 | External | 102.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01085 | 110.53 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 110.4 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.38 | P11:345:AMMO::RUSHISLAND:U1 | External | 116.13 | 0.25
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 106.5 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 106.64 | -0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00327 | 105.09 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN | External | 104.9 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00419 | 121.37 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 121.26 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01119 | 107.25 | P23:345:XEL:SPS 8S81 SSL | External | 107.17 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 177.76 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 177.8 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 100.11 | Base Case | External | 100.12 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04288 | 100.79 | P23:345:WERE:ROSE_345-20:: | Internal | 100.62 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01305 | 112.52 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 112.37 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 112.76 | 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1: 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 | External | 112.89 | -0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01314 | 108.86 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 108.23 | 0.63
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 108.59 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 108.54 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 113.26 | 603065 CHISAGO7 115 605269 LINDSTM7 115 1: 603065 CHISAGO7 115 605269 LINDSTM7 115 1 | External | 113.2 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.54 | P13:138-24:AEPW:PIRKEY 4 | External | 107.52 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18724 | 100.1 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 100.98 | P21:345:MEC:AUTO-SINGLE:SEPOLK3:GDMEC:1 | External | 100.9 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0021 | 112.6 | 104645: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 112.63 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 6e-05 | 100.49 | P12:115:OTP:AUTO-SINGLE:BIGSTON7:HIWY127:1 | External | 100.48 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 100.96 | P23:345:MEC:GDMEC 903 | External | 100.9 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 115.18 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External | 115.11 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00034 | 107.38 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 107.42 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.99 | P11:345:AMMO::RUSHISLAND:U2 | External | 116.43 | -0.44
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.74 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 127.76 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01008 | 114.08 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 113.98 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01038 | 111.23 | P12:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 111.17 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00531 | 102.55 | 104177: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 102.45 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.7 | 300006 1NM G1 22 300103 5NEWMAD 161 1: 300006 1NM G1 22.0 300103 5NEWMAD 161 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01314 | 119.29 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External | 118.53 | 0.76
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 116.42 | P11:HV:EES::1NM G1:1 | External | 115.8 | 0.62
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.05 | P13:500:EES-EAI:ND:8SANS SOUCI%:1 | External | 149.11 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.49 | P11:138:AMMO::SIOUX:2 | External | 107.22 | 0.27
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00268 | 126.53 | 104518: 541201 SIBLEY 7 345 997774 SIBLEY11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 997781 SIBLEY11 161 11 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | External | 126.45 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 117.78 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 117.74 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.36 | P23:345:MEC:TIFFIN 944 | External | 103.39 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.67 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 106.65 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01028 | 118.55 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 118.47 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.89 | P23:345:MEC:SUB TIC 944 | External | 103.77 | 0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01092 | 108.34 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 108.19 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.012 | 112.28 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 112.17 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00957 | 106.86 | P23:345:MEC:ATCHISON CO 903 | External | 106.77 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.38 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 118.3 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00069 | 222.42 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 222.41 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01066 | 105.73 | P23:500:EMI:ABF_PRYVL-B | External | 105.67 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 117.09 | P23:500:EAI:NBF_SAN SO~1 | External | 117.26 | -0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00106 | 107.47 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 107.38 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01335 | 160.7 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 160.5 | 0.2
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00727 | 107.4 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 107.37 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01006 | 118.65 | P23:345:MEC:TIFFIN 954 | External | 118.89 | -0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01308 | 108.01 | P23:345:XEL:SPS 8S72 HNA | External | 107.9 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 159.97 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 160.05 | -0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.22 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 121.37 | -0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01383 | 107.25 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17687 | 102.08 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal | 100.76 | 1.32
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01026 | 122.3 | 636400 HILLS 3 345 636420 TIFFIN 3 345 1: 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | External | 122.28 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00365 | 103.41 | P23:345:MEC:TIFFIN 954 | External | 103.44 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01114 | 117.52 | P23:345:XEL:SPS 8S72 HNA | External | 117.38 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 103.26 | 344001 5ADAIR2 161 631112 APANOSE5 161 1: 344001 5ADAIR2 161 631112 APANOSE5 161 1 | External | 103.28 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.07735 | 104.85 | P12:230:WERE:CIRC-GRTBND_230:: | Internal | 103.64 | 1.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01095 | 111.08 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 110.97 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.0047 | 103.18 | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01087 | 107.24 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00375 | 123.19 | P12:345:AMMO::BLAND:FRANKS:3 | External | 123.1 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15174 | 103.12 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal | 102.13 | 0.99
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 109.52 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 109.48 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01272 | 117.22 | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 144.48 | P11:345:UMZB:# 32 #: AVS IN ND. ANTELOPE VALLEY 2 | External | 144.48 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.06 | P11:18:EES-EAI:ETTA:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00022 | 103.1 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 103.15 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01152 | 109.04 | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External | 108.96 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.21 | 631206 QUINN3 345 631207 J416_WF3 345 1: 631206 QUINN3 345 631207 J416_WF3 345 1 | External | 102.18 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01261 | 106.94 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 106.91 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00034 | 107.74 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 107.77 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 112.47 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 112.48 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.41 | 300007 1NM G2 22 300046 7NEWMAD 345 1: 300007 1NM G2 22.0 300046 7NEWMAD 345 1 | External | 121.39 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.86 | P11:20:EES:NELSON_E:1 | External | 120.76 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 117.4 | P13:138-24:AEPW:TURK 4 | External | 117.24 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00702 | 102.41 | P23:345:MEC:SYCAMORE 904 | External | 102.36 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.0001 | 106.11 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 106.12 | -0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 110.25 | 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1: 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1 | External | 110.18 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00028 | 108.68 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External | 108.28 | 0.4
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01251 | 107.27 | P23:500:EAI:NBF_SAN SO~1 | External | 107.25 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00995 | 128.94 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 128.32 | 0.62
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15921 | 136.21 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 135.43 | 0.78
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01135 | 113.04 | P13:161:MEC:NORWALK 9T1 | External | 113.03 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00325 | 105.74 | P23:161-345:GMO:STJOE_R14-33::STJOE-EASTOWNE-STJOET1 | External | 105.56 | 0.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00152 | 101.38 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.38 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01109 | 119.56 | P23:345:AMIL::HERLEMAN:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 158.98 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 158.87 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00497 | 127.9 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 127.83 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.28 | P11:HV:EES::TURKCOAL:1 | External | 149.49 | -0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00055 | 112.69 | 71593: 603065 CHISAGO7 115 603172 WYOMING7 115 1 603136 HUGO 7 115 603172 WYOMING7 115 1 603065 CHISAGO7 115 605269 LINDSTM7 115 1 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 112.66 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.09 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 148.96 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00064 | 118.37 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 118.31 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 100.72 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 100.72 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.67 | P11:HV:EES::TURKCOAL:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 157.49 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 156.38 | 1.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00456 | 125.87 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 125.78 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 137.52 | Base Case | External | 137.47 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 7e-05 | 149.08 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 148.98 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.18196 | 158.02 | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | Internal | 156.84 | 1.18
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.62 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 101.64 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.06 | P12:EHV:EES::WELSH 7:1(1) | External | 106.95 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00029 | 137.99 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 138.05 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.35 | 300439 2HENRY 69 631106 HENRYCO5 161 1: 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | External | 102.39 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 661093 MERRCRT4 230 661982 MPT 34.5 KV 34.5 1 | 75 | 75 | 0.0001 | 100.15 | P11:345:UMZB:# 15 #: LO IN ND. LELAND OLDS 1 | External | 100.15 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00512 | 118.24 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 118.16 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.15842 | 138.68 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 137.69 | 0.99
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17687 | 102.47 | P12:115:MIDW:RICE-LYONS | Internal | 101.1 | 1.37
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 107.15 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 107.15 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 108.11 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 108.07 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 102.4 | P23:345:AMIL::HERLEMAN:1 | External | 102.47 | -0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.79 | P11:345:AMMO::RUSHISLAND:U1 | External | 105.55 | 0.24
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0099 | 120.41 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 121.08 | -0.67
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01172 | 101.71 | P23:345:MEC:SE POLK 901 OR 902 | External | 101.63 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01383 | 107.31 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 107.17 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01007 | 127.28 | P12:345:MEC:TIFFIN 9T1 SPS | External | 127.2 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.11 | P13:138-24:AEPW:TURK 4 | External | 107.94 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00032 | 114.36 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External | 114.38 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01007 | 118.88 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | External | 118.88 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 117.12 | P13:138-24:AEPW:TURK 4 | External | 116.96 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 160.93 | P12:161:DPC:AUTO-SINGLE:WABACO5:ROCHSTR5:1 | External | 160.74 | 0.19
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00097 | 116.25 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 116.24 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.4 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1:::: | External | 102.4 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.09299 | 102.54 | P13:115-230:MIDW:RICE COUNTY | Internal | 101.77 | 0.77
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00063 | 112.07 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 111.91 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.34 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 115.21 | 0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.31 | P13:13-13-161:XEL:AUTO-SINGLE:WHT53G:WHT54G:WHT145:2 | External | 106.29 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0102 | 116.42 | 82344: 635000 CBLUFFS3 345 645456 S3456 3 345 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 116.34 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.52 | 92452: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 121.44 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 100.03 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 100.03 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00217 | 118.38 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 118.3 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01007 | 127.84 | P23:345:MEC:TIFFIN 944 | External | 128.15 | -0.31
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00036 | 110.74 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 110.71 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01026 | 121.97 | 636400 HILLS 3 345 636420 TIFFIN 3 345 1: 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | External | 121.96 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01008 | 114.08 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 113.98 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 114.21 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 114.21 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 103.42 | 344006 5ADAIR3 161 344010 5ZACKARY 161 1: 344006 5ADAIR3 161 344010 5ZACKARY 161 1 | External | 103.37 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00367 | 128.81 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 128.73 | 0.08
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01109 | 119.34 | P23:345:AMIL::HERLEMAN:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 252 | 252 | 0.00038 | 113.57 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | External | 113.35 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0124 | 107.25 | 601012 ROSEAUN2 500 667501 RIEL 2 500 1: 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00987 | 120.04 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 120.08 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 107.21 | P11:345:AMMO::RUSHISLAND:U2 | External | 107.43 | -0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00024 | 100.82 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 100.78 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 2e-05 | 158.44 | 630139 ADAMS 8 69 631046 ADAMS 5 161 1: 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | External | 158.38 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00075 | 107.15 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 107.15 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00399 | 103.13 | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | External | 103.02 | 0.11
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01218 | 110.6 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 110.59 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01071 | 105.77 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18 1: 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | External | 105.89 | -0.12
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.16052 | 103.3 | P12:115:MKEC:SAINTJOHN-SAINTJOHN(MIDWEST):: | Internal | 102.02 | 1.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 113.89 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 113.88 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 114.57 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.27 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 116.27 | 0
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01119 | 117.32 | P12:345:XEL:SPS HNA-SSL | External | 117.25 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 100.78 | 657747 ASH1 9 34.5 657701 BARNES 4 230 1: 657747 ASH1 9 34.5 657701 BARNES 4 230 1 | External | 100.76 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 121.23 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 121.32 | -0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 100.78 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1 | External | 100.76 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00112 | 128.35 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 128.14 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 115.9 | P12:EHV:EES::WELSH 7:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01166 | 101.06 | 635680 BONDRNT3 345 635690 GDMEC 3 345 1: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 | External | 100.99 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 111.65 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.64 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01141 | 118.38 | P23:345:MEC:KOSSUTH 904 | External | 118.32 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01097 | 119.25 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 119.09 | 0.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01109 | 109.13 | P23:345:AMIL::HERLEMAN:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01011 | 123.87 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 123.59 | 0.28
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.14604 | 132.05 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 131.05 | 1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01011 | 124.24 | P23:345:MEC:HILLS 984 | External | 123.95 | 0.29
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.05 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 149.11 | -0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00063 | 120.29 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 120.23 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.85 | P12:LV-HV:EES::6NELSON%:1NELSON_G6!:1 | External | 120.76 | 0.09
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.17687 | 100.74 | P12:115:MIDW:LYONS-WHEATLANDS | Internal
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00027 | 101.85 | P13:41-115-230:OTP:AUTO-SINGLE:FORMN9:FORMN7:FORMAN4:1 | External | 101.83 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 149.6 | P23:500:EAI:NBF_SAN SO~2 | External | 149.43 | 0.17
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 134.32 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 134.45 | -0.13
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01098 | 118.39 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 118.44 | -0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00995 | 128.53 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 127.92 | 0.61
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.1454 | 108.99 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 107.83 | 1.16
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.48 | P11:345:MEC-NPPD:COOPER 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.13 | P11:24:AEPW:TURKCOAL | External | 108.1 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.16587 | 128.92 | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | Internal | 127.97 | 0.95
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 9e-05 | 103.13 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 103.1 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01252 | 108.13 | P11:HV:EES::TURKCOAL:1 | External | 108.1 | 0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00067 | 100.6 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 100.45 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00369 | 120.98 | P11:EHV:EES::1DUKE HS S1:1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01279 | 107.96 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 107.91 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 114.54 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 114.52 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 1e-05 | 109.42 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 109.45 | -0.03
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 101.67 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 101.69 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00549 | 102.73 | 84363: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 542969 STILWEL5 161 542994 HICKMAN5 161 1 542969 STILWEL5 161 543050 ANTIOCH5 161 1 542969 STILWEL5 161 543053 REDEL 5 161 1 542969 STILWEL5 161 543057 BUCYRUS5 161 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 542969 STILWEL5 161 997752 STILWELL11 161 11 542969 STILWEL5 161 997751 STILWELL22 161 22 542969 STILWEL5 161 997759 STILWELL11 161 11 542969 STILWEL5 161 997758 STILWELL22 161 22 542969 STILWEL5 161 997755 STILWELL11 161 11 542969 STILWEL5 161 997754 STILWELL22 161 22 | External | 102.68 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 125.5 | 125.5 | 0.08914 | 116.92 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 115.43 | 1.49
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00995 | 120.15 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 119.6 | 0.55
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 103.05 | P13:115-230:OTP:BIGSTON4:T1 | External | 103.07 | -0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01207 | 112.3 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA | External | 112.16 | 0.14
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01071 | 116.92 | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1: 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00057 | 109.52 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 109.48 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 102.17 | P11:18:XEL:AUTO-SINGLE:FEPCTG:1 | External | 102.16 | 0.01
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00054 | 111.96 | 602042 LAW CRK5 161 3WXFMR 82578T7IC002 5: 602042 LAW CRK5 161 997619 82578T7IC002 115 5 603197 LAW CRK7 115 997619 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997619 82578T7IC002 115 5 602042 LAW CRK5 161 997626 82578T7IC002 115 5 603197 LAW CRK7 115 997626 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997626 82578T7IC002 115 5 602042 LAW CRK5 161 997620 82578T7IC002 115 5 603197 LAW CRK7 115 997620 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997620 82578T7IC002 115 5 | External | 111.9 | 0.06
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01071 | 117.74 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 6e-05 | 103.02 | 105800: 652392 BISMARK9 12.5 997177 BS KV8A 115 1 652426 BISMARK4 230 659128 HERBERTW-KM4 230 1 652444 JAMESTN4 230 659128 HERBERTW-KM4 230 1 652427 BISMARK7 115 655652 E.BISMRK-CP7 115 1 652427 BISMARK7 115 661029 ESTBMRK7 115 1 652427 BISMARK7 115 997178 BS KV3A 115 1 652427 BISMARK7 115 997177 BS KV8A 115 1 652296 WARD 4 230 652426 BISMARK4 230 1 652426 BISMARK4 230 652444 JAMESTN4 230 1 652426 BISMARK4 230 652456 WASHBRN4 230 1 652426 BISMARK4 230 652466 HILKEN 4 230 1 652426 BISMARK4 230 652499 CAMPBELL 4 230 1 652426 BISMARK4 230 997178 BS KV3A 115 1 652426 BISMARK4 230 997177 BS KV8A 115 1 652456 WASHBRN4 230 659106 LELAND_O-BE4 230 1 652325 WASHBRN9 41.8 652456 WASHBRN4 230 1 652467 BISMARK29 12.5 997178 BS KV3A 115 1 652392 BISMARK9 12.5 997184 BS KV8A 115 1 652427 BISMARK7 115 997185 BS KV3A 115 1 652427 BISMARK7 115 997184 BS KV8A 115 1 652426 BISMARK4 230 997185 BS KV3A 115 1 652426 BISMARK4 230 997184 BS KV8A 115 1 652467 BISMARK29 12.5 997185 BS KV3A 115 1 652392 BISMARK9 12.5 997175 BS KV8A 115 1 652427 BISMARK7 115 997176 BS KV3A 115 1 652427 BISMARK7 115 997175 BS KV8A 115 1 652426 BISMARK4 230 997176 BS KV3A 115 1 652426 BISMARK4 230 997175 BS KV8A 115 1 652467 BISMARK29 12.5 997176 BS KV3A 115 1 | External | 103 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00062 | 106.19 | P23:345:MEC:LOUISA 964 | External | 106.15 | 0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00035 | 100.82 | P23:345:XEL:8S27 WLM AS | External | 100.92 | -0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00957 | 118.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | External | 118.67 | 0.02
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01305 | 112.52 | 631113 POWESHK5 161 631117 REASNOR5 161 1: 631113 POWESHK5 161 631117 REASNOR5 161 1 | External | 112.37 | 0.15
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01051 | 108.73 | P23:345:MEC:ATCHISON CO 903 | External | 108.63 | 0.1
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 335 | 335 | 0.00206 | 103.03 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 102.98 | 0.05
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00018 | 151.2 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00022 | 104.83 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 104.87 | -0.04
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.01045 | 113.98 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External | 113.77 | 0.21
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05337 | 100.53 | P12:345:WERE:SWIS-WGAR_345:: | Internal | 100.46 | 0.07
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.03685 | 113.91 | 104266: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | Internal | 113.69 | 0.22
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00227 | 106.54 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 106.18 | 0.36
Thermal | 00NR | S2 | 19WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 115.15 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 115.27 | -0.12
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 152.03 | P23:500:EES-EAI:WH_BLF:B7914 | External | 152.12 | -0.09
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.25 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 127.25 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 478 | 478 | 7e-05 | 100.71 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 100.71 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 102.93 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External | 102.92 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 103.24 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.75 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 116.75 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 139.18 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.25 | -0.07
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0002 | 110.1 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.15 | -0.05
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00026 | 113.09 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 113.09 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334391 4CARROLS% 138 334401 47NECHES1! 138 1 | 220 | 220 | 0.00019 | 101.27 | 334391 4CARROLS% 138 334396 47NECHES2! 138 2: 334391 4CARROLS% 138 334396 47NECHES2! 138 2 | External | 101.27 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 101.57 | P23:345:GRE:PVS 19JB4 | External | 101.57 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 108.61 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 108.6 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0002 | 106.89 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.95 | -0.06
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 149.46 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 149.46 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 100.46 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1 | External | 100.45 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 102.26 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 102.25 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 127.4 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 127.39 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997614 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00054 | 126.95 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 126.95 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 107.58 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 107.57 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334391 4CARROLS% 138 334396 47NECHES2! 138 2 | 220 | 220 | 0.0002 | 101.27 | 334391 4CARROLS% 138 334401 47NECHES1! 138 1: 334391 4CARROLS% 138 334401 47NECHES1! 138 1 | External | 101.27 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00041 | 127.4 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 127.39 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334391 4CARROLS% 138 334401 47NECHES1! 138 1 | 220 | 220 | 0.00019 | 101.27 | P12:HV:EES::4CARROLS%:47NECHES2!:1 | External | 101.27 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.59 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 117.59 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 242.83 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 242.82 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 102.24 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14 | External | 102.23 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.25 | P13:161-69:EES-EAI:HERGET:AT2 | External | 127.25 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 149.46 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 149.46 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 6e-05 | 109.23 | Base Case | External | 109.23 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 109.16 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 109.15 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.59 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 117.59 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0002 | 113.86 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.92 | -0.06
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 117.89 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.89 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00058 | 111.58 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 111.57 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00048 | 112 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 112.08 | -0.08
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.62 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 127.62 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 102.93 | 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22 1: 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 | External | 102.92 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 242.83 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 242.82 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00021 | 105.87 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 105.87 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334391 4CARROLS% 138 334396 47NECHES2! 138 2 | 220 | 220 | 0.0002 | 101.27 | P12:HV:EES::4CARROLS%:47NECHES1!:1 | External | 101.27 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00032 | 113.76 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 113.74 | 0.02
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 139.24 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 139.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.75 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 116.75 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 128.54 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 128.53 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.62 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 127.62 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 102.04 | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1: 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | External | 102.03 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00058 | 112.04 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 112.04 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 103.13 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 103.12 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 127.25 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 127.25 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0029 | 101.17 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 101.15 | 0.02
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0013 | 100.81 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 100.8 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997053 GLENHAM TR1 115 1 | 25 | 31 | 0.00028 | 112.84 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.84 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 101.55 | P23:345:GRE:PVS 19JB1 | External | 101.55 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 103.24 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 102.26 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 102.25 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 106.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 106.91 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 141.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.91 | -0.07
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 103.24 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 103.24 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00022 | 103.06 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.05 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 0.00017 | 116.75 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 116.75 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 102.24 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15 | External | 102.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 102.04 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1 | External | 102.03 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 103.24 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 132.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 132.73 | -0.05
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 109.16 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 109.15 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 3e-05 | 124.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.44 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 3e-05 | 124.61 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.61 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00032 | 113.83 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 113.82 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 103.24 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.0026 | 101.12 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 101.07 | 0.05
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 103.13 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 103.12 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 0.00017 | 117.59 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 117.59 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 127.62 | P13:161-69:EES-EAI:HERGET:AT1 | External | 127.62 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 100.46 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 100.45 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00019 | 242.83 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 242.82 | 0.01
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 117.28 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.28 | 0
Thermal | 04HVER | S1 | 24WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 102.94 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 102.94 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 5e-05 | 139.08 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.09 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.68 | 67791: 336426 3CLAB8! 115 336458 3MICH N! 115 1 336462 6MICHO% 230 500360 FRONTST6 230 1 336412 3PATER! 115 336442 3SFORS 115 1 336442 3SFORS 115 336444 3MICH S! 115 1 | External | 113.68 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | 336462 6MICHO% 230 500360 FRONTST6 230 1: 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 127.37 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 127.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00082 | 102.84 | P23:500:EES-SOCO:ABF_MCKNT-B | External | 102.84 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 100.38 | P12:HV:EES::6DNLDVL:6BYVRET!:1 | External | 100.37 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 118.24 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 118.24 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00038 | 107.75 | P12:HV:EES::6FAIRVW!:6GYPSY%:1 | External | 107.75 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 145.1 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.9 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 110.89 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00058 | 100.99 | 500060 BVISTA 4 138 500065 BVISTA 6 230 1: 500060 BVISTA 4 138 500065 BVISTA 6 230 1 | External | 100.99 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.37 | P12:500-230:EES:WILGLN:WATERF | External | 110.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00022 | 100.57 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00073 | 103.91 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 103.9 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.39 | P23:500:EES:ABF_WG-E | External | 110.38 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 110.74 | P23:500:EES:ABF_WG-A | External | 110.73 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 111.04 | P23:500:EES:ABF_WG-A | External | 111.04 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.48 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.46 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.18 | 336137 6SLIDEL! 230 500360 FRONTST6 230 1: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 | External | 113.18 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 104.54 | 80254: 500050 BSALES 4 138 500820 TECHE 4 138 1 500460 JULTAP 4 138 500820 TECHE 4 138 1 500580 MORBHAN4 138 500820 TECHE 4 138 1 500660 PATOUT 4 138 500820 TECHE 4 138 1 501823 G3TECHE 24.0 500820 TECHE 4 138 1 501824 G4TECHE 13.8 500820 TECHE 4 138 1 | External | 104.53 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 104.77 | P12:138:CLEC::BSALES 4:TECHE 4:1 | External | 104.77 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.34 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 110.34 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.82 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 126.82 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 106.25 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 106.25 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00055 | 108.95 | P12:230:EES:WATERF:VACHER:1 | External | 108.95 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 105.21 | P12:230:EES:ROMEVL:CONVRT:FRSCO | External | 105.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00014 | 100.59 | 336065 6CONVNT! 230 336066 6FRISCO! 230 1: 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | External | 100.59 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 110.48 | P12:230:EES:PANAMA:DBAYOU:1 | External | 110.48 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 107.72 | P23:500:EES:BF335618-1~3 | External | 107.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.32 | P12:500-230:EES:WILGLN:WATERF | External | 107.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 123.57 | P23:500:EES:BF335618-1~3 | External | 123.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 118.24 | P12:230:EES:TEZCUC:WATERF:1 | External | 118.24 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 110.74 | P23:500:EES:ABF_WG-A | External | 110.73 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00022 | 110.74 | P23:500:EES:BF335618-1~3 | External | 110.73 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.34 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 110.34 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.33 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 123.33 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.9 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 110.89 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 103.83 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 103.83 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.65 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.65 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 105.81 | P12:HV:EES::6ROMEVL!:6CONVNT!:1 | External | 105.81 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 111.02 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.99 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 122.34 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 122.35 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00086 | 103.32 | P23:500:EES-SOCO:ABF_MCKNT-D | External | 103.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 115 | P12:HV:EES::6BLPNT!:6TEZCUCO%:1 | External | 115 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 110.48 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 110.48 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 0.00012 | 107.35 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 107.35 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.32 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 107.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00025 | 125.79 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 125.78 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 122.77 | P12:230:EES:IRONMN:L_GPSY:1 | External | 122.76 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.93 | P23:500:EES:BF335618-133 | External | 110.93 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 103.08 | P12:230:EES:RACELA:WATERF:1 | External | 103.08 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00015 | 128.64 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.64 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0005 | 102.67 | P12:HV:EES::3LAPLAC:3GYPSY%:1 | External | 102.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 116.53 | P12:230:EES:BELPNT:TEZCUC:L_GPSY:1 | External | 116.53 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.86 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.83 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 107.52 | P12:230:LAGN:FR_BRA_E:SLIDEL:LOGTOWNW:1 | External | 107.52 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 115.75 | P23:500:EES:ABF_WG-E | External | 115.75 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 108.84 | P12:230:EES:WELCOM:STJAME:1 | External | 108.84 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 108.03 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 108.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 111.09 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 111.09 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.22 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 110.23 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 134.29 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 134.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 2e-05 | 132.17 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 132.17 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 114.74 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 114.74 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 123.69 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 123.69 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 115 | 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1: 336068 6BLPNT! 230 336069 6TEZCUCO% 230 1 | External | 115 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 113.57 | P12:HV:EES::6TEZCUCO%:6IRONMAN%:1 | External | 113.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.22 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 123.19 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00022 | 110.74 | P23:500:EES:BF335618-1~3 | External | 110.73 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.18 | P12:230:EES-CLEC::6SLIDEL!:FRONTST6:1 | External | 113.18 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 107.2 | P12:HV:EES::6CONVNT!:6FRISCO!:1 | External | 107.2 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 107.67 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 107.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 149.8 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 149.8 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.37 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.72 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 115.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 110.48 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 110.48 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 118.05 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 118.05 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 108.76 | P12:230:EES:WELCOM:STJAME:VACHER | External | 108.76 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.37 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00022 | 104.45 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.45 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.08 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 123.07 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 166.63 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 166.63 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.37 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 118.05 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 118.05 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 109.8 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 109.81 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 109.75 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 109.75 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 122.06 | P12:HV:EES::6PANAMA%:6DUTBYU%:1 | External | 122.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.08 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 123.07 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0004 | 208.39 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 208.37 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 0.00012 | 109.44 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 109.44 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 118.05 | P12:230:EES:PANAMA:DBAYOU:1 | External | 118.05 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 106.25 | P12:230:EES:TEZCUC:WATERF:1 | External | 106.25 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.41 | P12:HV:EES::6FANCY_PT%:6WATERLOO:1 | External | 102.4 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.58 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 127.26 | P23:500:EES:BF335618-1~3 | External | 127.26 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 110.44 | P12:HV:EES::6STJAME!:6VACHRE!:1 | External | 110.44 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.37 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 110.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 100.21 | P23:500:AEPW-EES:ABF_HTBG-A | External | 100.21 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.82 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 126.81 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.13 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 126.13 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.91 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 122.06 | P12:230:EES:PANAMA:DBAYOU:1 | External | 122.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336005 6WELCOM! 230 336006 6STJAME! 230 1 | 418 | 418 | 2e-05 | 109.51 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 109.51 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.47 | P12:230:EES:TEZCUC:WATERF:1 | External | 101.47 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.31 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.31 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.79 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 126.79 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.37 | P12:500-230:EES:WILGLN:WATERF | External | 110.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.79 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 126.79 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.32 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 107.72 | P23:500:EES:ABF_WG-A | External | 107.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.94 | 64573: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.94 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P12:230-21:EES:FCY:RVB | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 102.63 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 102.63 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00056 | 102.72 | 67800: 303203 6LANDRY 230 336042 6RACLND! 230 1 303203 6LANDRY 230 336041 6TEREBN% 230 1 336033 3TEREBN! 115 336034 3COTEAU! 115 1 | External | 102.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 122.06 | 336063 6PANAMA% 230 336067 6DUTBYU% 230 1: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 | External | 122.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.74 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 126.75 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00026 | 116.16 | P23:500:EES:BF335618-1~3 | External | 116.16 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.34 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 110.34 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | P12:HV:EES::6MICHO%:FRONTST6:1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.41 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 110.41 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 108.22 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 108.22 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00074 | 103.82 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 103.82 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 107.46 | 303223 6FR_BRANCH 230 336137 6SLIDEL! 230 1: 303223 6FR_BRANCH 230 336137 6SLIDEL! 230 1 | External | 107.46 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.82 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 126.81 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.87 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 126.87 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00017 | 104.38 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 104.37 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 123.11 | P23:500:EES:BF335618-133 | External | 123.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.37 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.39 | P23:500:EES:ABF_WG-E | External | 110.38 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.82 | P12:500-230:EES:WILGLN:WATERF | External | 126.82 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00013 | 127.62 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 127.62 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 107.67 | P12:230:EES:TEZCUC:WATERF:1 | External | 107.67 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 103.91 | P12:138:CLEC::BVISTA 4:ELPTAP 4:1 | External | 103.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.39 | P23:500:EES:BF335618-133 | External | 110.38 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.41 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 110.41 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0005 | 102.38 | P12:HV:EES::3BLPNT!:3LAPLAC:1 | External | 102.38 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 101.99 | P12:230:EES:PANAMA:WILTON_E:1 | External | 101.99 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 101 | P12:HV:EES::6LANDRY:6RACLND!:1 | External | 101 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 103.83 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 103.83 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.33 | P23:500:EES:ABF_WG-E | External | 107.33 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00054 | 113.58 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 113.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00048 | 100.09 | P12:230:EES:SPORT:JOLIET:1 | External | 100.09 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P11:21:EES:RVB:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00014 | 100.59 | P12:HV:EES::6CONVNT!:6FRISCO!:1 | External | 100.59 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.72 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 115.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 145.1 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 103.89 | P12:HV:EES::BVISTA 4!:WAXLAKE4!:1 | External | 103.89 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.71 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 115.71 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.94 | 80163: 336137 6SLIDEL! 230 500360 FRONTST6 230 1 336462 6MICHO% 230 500360 FRONTST6 230 1 | External | 113.94 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 103 | P12:138:CLEC::BSALES 4:WAXLAKE4:1 | External | 103 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00011 | 118.24 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 118.24 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 127.37 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 127.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.95 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 110.95 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.37 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00015 | 131.1 | P23:500:EES-EAI:WH_BLF:B7914 | External | 131.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 111.04 | P23:500:EES:BF335618-1~3 | External | 111.04 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.91 | P12:EHV:EES::8WILLOW_GL%:8WATERFO:1 | External | 110.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.71 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 115.71 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.72 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 110.44 | 336006 6STJAME! 230 336007 6VACHRE! 230 1: 336006 6STJAME! 230 336007 6VACHRE! 230 1 | External | 110.44 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 9e-05 | 106.25 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 106.25 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 106.05 | P13:230:115:EES:TRBONE:AT | External | 106.05 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00018 | 123.57 | P23:500:EES:ABF_WG-A | External | 123.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 107.52 | P12:HV:EES::6SLIDEL!:6LOGTWN W6:1 | External | 107.52 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 145.1 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 119.34 | P12:HV:EES::6BLPNT!:6GYPSY%:1 | External | 119.33 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0005 | 102.4 | P12:115:EES:BELPNT:LAPLCE:L_GPSY | External | 102.39 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 115.77 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 115.77 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.91 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00021 | 118.97 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.96 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00019 | 113.84 | P12:230:EES-CLEC::6MICHO%:FRONTST6:1 | External | 113.83 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 115.96 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 115.96 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 123.69 | P12:HV:EES::6FRISCO!:6DUTBYU%:1 | External | 123.69 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 110.44 | P12:230:EES:STJAME:VACHER:1 | External | 110.44 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1: 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.37 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.13 | 67847: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 123.13 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.48 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.46 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.34 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 110.34 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00018 | 145.1 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00026 | 106.78 | 303223 6FR_BRANCH 230 388425 6LOGTWN W6 230 1: 303223 6FR_BRANCH 230 388425 6LOGTWN W6 230 1 | External | 106.78 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.72 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 115.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00021 | 119.34 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 119.33 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.72 | P12:500-230:EES:WILGLN:WATERF | External | 115.72 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00012 | 123.69 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 123.69 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336006 6STJAME! 230 336007 6VACHRE! 230 1 | 456 | 456 | 2e-05 | 107.43 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.43 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.92 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 110.91 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.31 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.31 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 145.1 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123 | 67766: 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 123 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 126.84 | P23:500:EES:BF335618-133 | External | 126.84 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.39 | P23:500:EES:BF335618-133 | External | 110.38 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.01 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 123.05 | -0.04
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.08 | 67849: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 123.07 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00016 | 123.11 | P23:500:EES:ABF_WG-E | External | 123.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 127.26 | P23:500:EES:ABF_WG-A | External | 127.26 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.29 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 107.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 110.58 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 110.58 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0002 | 109.8 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 109.81 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00071 | 103.89 | P12:138:CLEC:BUVIS:ELPTAP4:WAXLKE:1 | External | 103.89 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 102.43 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 102.43 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00012 | 127.37 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 127.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00021 | 118.97 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 118.96 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 122.77 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 122.76 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 126.84 | P23:500:EES:ABF_WG-E | External | 126.84 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 113.57 | P12:230:EES:TEZCUC:IRONMN:1 | External | 113.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.42 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.4 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00018 | 145.1 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 145.1 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.47 | P12:HV:EES::6TEZCUCO%:6WATFRD%:1 | External | 101.47 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.37 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 110.36 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00026 | 116.16 | P23:500:EES:ABF_WG-A | External | 116.16 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.06 | 336150 8WATERFO 500 336154 6WATFRD% 230 1: 336150 8WATERFO 500 336154 6WATFRD% 230 1 | External | 123.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00024 | 115.06 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 115.07 | -0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.06 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 123.06 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00018 | 137.28 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 137.28 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00013 | 124.03 | 67792: 336063 6PANAMA% 230 336067 6DUTBYU% 230 1 336051 3SORNTO! 115 336053 3LUTCHR! 115 1 | External | 124.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00049 | 102.45 | P11:HV:EES::1RVR_BND_G1!:1 | External | 102.44 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.29 | P12:HV:EES::8WATERFO:6WATFRD%:1 | External | 107.29 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.0004 | 175.25 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 175.23 | 0.02
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.94 | P23:500:EES:ABF_WG-E | External | 110.93 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.51 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 107.51 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | 641 | 641 | 5e-05 | 110.92 | P12:500-230:EES:WILGLN:WATERF | External | 110.91 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 113.57 | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1: 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | External | 113.57 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 103.03 | P12:HV:EES::6ROMEVL!:6WILTON%:1 | External | 103.03 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.02 | 67812: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336051 3SORNTO! 115 336052 3BURNSD 115 1 | External | 107.02 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00016 | 112.85 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 112.85 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00011 | 101.47 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 101.47 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0002 | 110.37 | P12:HV-EHV:EES::8WILLOW_GL%:6WATFRD%:1 | External | 110.37 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00018 | 153.91 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 153.91 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00017 | 123.01 | P12:500-230:EES:WILGLN:WATERF | External | 123.05 | -0.04
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00053 | 112.11 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 112.11 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00019 | 107.32 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.32 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 2e-05 | 131.98 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 131.98 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | 641 | 641 | 0.00023 | 115.75 | P23:500:EES:BF335618-133 | External | 115.75 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.96 | 67848: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 126.93 | 0.03
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00021 | 102.63 | 336068 6BLPNT! 230 336190 6GYPSY% 230 1: 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | External | 102.63 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 127.07 | 67822: 335595 4ALCHEM! 138 335601 4WILLOW_GL2% 138 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 335591 4GEISMAR! 138 335610 4WILLOW_GL% 138 1 | External | 127.07 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.0002 | 116.35 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 116.35 | 0
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00019 | 122.77 | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1: 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | External | 122.76 | 0.01
Thermal | 04HVER | S1 | 24L0 | G04_G056 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00017 | 126.82 | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1: 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 126.81 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 111.07 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14 | External | 111.07 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 3e-05 | 146.46 | P23:500:EES-EAI:WH_BLF:B7914 | External | 146.51 | -0.05
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00013 | 107.41 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 107.41 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00021 | 134.19 | P23:500:EES-EAI:WH_BLF:B7914 | External | 134.22 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00093 | 108.49 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 108.48 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.26 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 101.26 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00032 | 100.08 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 100.08 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.52 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.5 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.43 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 100.34 | 0.09
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00131 | 102.69 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 102.68 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 101 | 92386: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 100.98 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 110.37 | P23:345:GRE:PVS 19JB4 | External | 110.37 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.26 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 101.26 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 100.77 | P23:345:MEC:MONTEZUMA 903 | External | 100.77 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 121.61 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 121.6 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00027 | 103.67 | P23:500:EES-EAI:WH_BLF:B7914 | External | 103.71 | -0.04
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.18 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998338 COLAUTO3 138 1 512705 COLLINS4 138 998346 COLAUTO3 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 | External | 100.16 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00153 | 102.04 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 102.02 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 171.13 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 171.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 101.03 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 100.89 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 100.88 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 108.88 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1 | External | 108.88 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 110.81 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1 | External | 110.81 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 111.99 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 111.99 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 103.41 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 103.41 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 101.03 | Base Case | External | 101.02 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00046 | 122.43 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.42 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00024 | 100.87 | P23:500:EMI-EES:ABF_FRKLN-A | External | 100.87 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00046 | 122.43 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.42 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 242.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 242.03 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P23:345:MEC:MONTEZUMA 902 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.02 | 92398: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541163 DOGWDCT1 18.0 541225 PHILL 5 161 1 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 541164 DOGWDCT2 18.0 541225 PHILL 5 161 1 | External
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00027 | 109 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.03 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 103.24 | 300320 5LEVASY 161 548808 ECKLES-161 161 1: 300320 5LEVASY 161 548808 ECKLES-161 161 1 | External | 103.24 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 100.9 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 100.89 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 171.13 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 171.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 103.41 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 103.41 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 118.13 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 118.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00027 | 112.17 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.2 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 111.04 | P23:345:SMP:BYRON 3-GRE-PL VLLY3 BKR8S16 | External | 111.04 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | 631115 OTTUMWA5 161 631118 LUCAS 5 161 1: 631115 OTTUMWA5 161 631118 LUCAS 5 161 1 | External | 102.99 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 102.78 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.77 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 106.37 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 106.36 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.8 | 92436: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 | External | 100.79 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.82 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 100.8 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00088 | 109.98 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 109.98 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 242.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 242.03 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 161.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 161.66 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00032 | 110.23 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 110.21 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.09 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.09 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997053 GLENHAM TR1 115 1 | 25 | 31 | 0.00021 | 105 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 105 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00592 | 124.25 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 124.25 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.84 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 100.82 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.69 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 100.68 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 102.3 | 672540 QE 6 138 672541 CORY 6 138 1: 672540 QE 6 138 672541 CORY 6 138 1 | External | 102.3 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 101.97 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 101.97 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 110.81 | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1: 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | External | 110.81 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 106.34 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 106.34 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 103.24 | P12:161:AECI-INDN:ECKLES-5LEVASY:: | External | 103.24 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 6e-05 | 108.88 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 108.88 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 103.68 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 103.68 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 103.68 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 103.68 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 100.22 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1: 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | External | 100.22 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 110.35 | P23:345:GRE:PVS 19JB1 | External | 110.35 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0009 | 116.07 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 116.06 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0009 | 100.52 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.5 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 109.65 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 109.64 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 102.78 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 102.77 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 100.11 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 100.11 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 105.07 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 105.06 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00104 | 102.78 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.77 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00088 | 109.98 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 109.98 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00021 | 136.75 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.78 | -0.03
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 113.28 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 113.27 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 101.21 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 101.21 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 111.99 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 111.99 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.06 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 100.06 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998889 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 116.94 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 116.94 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.72 | 92409: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 100.7 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 8e-05 | 111.05 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15 | External | 111.04 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00021 | 100.9 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 100.9 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 100.89 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 100.88 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 100.06 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 100.06 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00059 | 113.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.53 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 118.13 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 118.13 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.17 | 92419: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 100.16 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | P12:161:ALTW:AUTO-SINGLE:OTTUMWA5:LUCAS5:1 | External | 102.99 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 106.43 | P11:024:DPC:ALMA2:6 | External | 106.43 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 123.34 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 123.34 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00058 | 103.47 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 103.46 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0009 | 116.07 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.06 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 101 | 92463: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 | External | 100.98 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 123.51 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 123.51 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 111.08 | 106084: 656025 FRDRCKSB8 69.0 656039 LAWLERTP8 69.0 1 656039 LAWLERTP8 69.0 656061 PETERSON8 69.0 1 656039 LAWLERTP8 69.0 656041 LAWLR8 69.0 1 | External | 111.07 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 112.63 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 112.62 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 120.76 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 120.76 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00251 | 110.94 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 110.9 | 0.04
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 111.15 | 672621 SHAND 4 230 672321 SHAND 1G 18 1: 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | External | 111.15 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 1e-05 | 111.08 | P12:069:UMZ:# 5707 #: IN . PROPER N-1 (LINE) FOR 656025-656039-1 | External | 111.07 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.84 | 92461: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 | External | 100.82 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | P13:69-161:ALTW:AUTO-SINGLE:LUCAS8:LUCAS5:1 | External | 103 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 121.38 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 121.38 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 106.43 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 106.43 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998890 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 117.79 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 117.79 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 103.76 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.76 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00023 | 242.03 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 242.03 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.53 | 92449: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 100.51 | 0.02
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0015 | 100.53 | 92443: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External | 100.52 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 103.25 | 92154: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 103.25 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00053 | 103.25 | 104053: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 103.25 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 100.32 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.31 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 100.11 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 100.11 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00118 | 100.11 | P12:161:ITCM:AUTOSINGLE:LANSINGW:GENOA:1 | External | 100.11 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00093 | 103.18 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 103.17 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 5e-05 | 103 | 630044 LUCAS 8 69 631118 LUCAS 5 161 1: 630044 LUCAS 8 69.0 631118 LUCAS 5 161 1 | External | 103 | 0
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00032 | 110.3 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 110.29 | 0.01
Thermal | 04HVER | S1 | 24SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 113.28 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 113.27 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.57 | P42:345:OKGE:SB_FTTH7385 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 101.23 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 101.22 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.79 | 80254: 500050 BSALES 4 138 500820 TECHE 4 138 1 500460 JULTAP 4 138 500820 TECHE 4 138 1 500580 MORBHAN4 138 500820 TECHE 4 138 1 500660 PATOUT 4 138 500820 TECHE 4 138 1 501823 G3TECHE 24.0 500820 TECHE 4 138 1 501824 G4TECHE 13.8 500820 TECHE 4 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01104 | 105.37 | P42:345:OKGE:SB_HURS7309 | External | 105.22 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 113.46 | 104494: 541232 LEX161 5 161 541236 RICHMND5 161 1 541236 RICHMND5 161 541244 ORRICK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.94 | P11:18:EES:DOWAEP:U4 | External | 103.9 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01048 | 116.29 | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00509 | 129.5 | 84385: 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541273 KELHYS 2 69.0 541275 SEDPLT 2 69.0 1 | External | 129.51 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.19 | P13:138:EES:ND:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01158 | 104.09 | 92289: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.56 | P11:115:XEL:RIV COMBINE CYCLE | External | 101.45 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01068 | 115.91 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1 | External | 116.13 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 106.65 | 300103 5NEWMAD 161 301398 5NORANDA2 161 1: 300103 5NEWMAD 161 301398 5NORANDA2 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.21 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 116.09 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.54 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1 | External | 101.45 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.56 | P23:345:OTP:CENTER 3:3215 | External | 101.48 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.16 | P12:345:OKGE:BKRBKR295 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.59 | P11:0:MEC:AUTO-SINGLE:RLHILLSW0:W | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01151 | 104.3 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 104.21 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.18 | P12:HV:EES::3PLANTATION!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.7 | 104649: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.23 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1 | External | 103.9 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.0002 | 102.95 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 102.95 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00395 | 113.85 | P23:161-345:GMO:BLUESPRINGSE_R1-3::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 113.72 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.42 | P12:345:OKGE:BKRBKR295 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 105.33 | 601034 NOBLES 3 345 631138 LAKEFLD3 345 1: 601034 NOBLES 3 345 631138 LAKEFLD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.77 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 105.68 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01038 | 105.34 | 88028: 503912 FULTON 3 115 507453 HOPE 3 115 1 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | External | 105.18 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00015 | 110.19 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 110.19 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.85 | P11:345:MEC-NPPD:COOPER 1 | External | 105.75 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01158 | 104.56 | 65031: 631107 JASPER 5 161 635710 NEANKNY5 161 1 635710 NEANKNY5 161 635711 PLKCTY5 161 1 | External | 104.45 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.73 | P43:161-345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00033 | 118.28 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 118.21 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01042 | 116.94 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 116.79 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00036 | 111.63 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 111.55 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.4 | P11:345:OPPD:NEBCTY1G:LT | External | 110.91 | 0.49
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.12 | 603284 ODELL WIND 7 115 603285 WOAD HILL 7 115 1: 603284 ODELL WIND 7 115 603285 WOAD HILL 7 115 1 | External | 106.06 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.2 | P11:138:AMMO::MERAMEC:2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.35 | 92230: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.21 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01047 | 106.13 | 636230 FRANKLN5 161 636235 WALL LK5 161 1: 636230 FRANKLN5 161 636235 WALL LK5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01039 | 116.49 | P12:115:XEL:CRY-RRK | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.15 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.06 | P13:013-138:AMMO::OSAGE:1 | External | 116.07 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 118.73 | Base Case | External | 118.66 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 115.3 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:APANOSE5:1 | External | 115.34 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.1 | P22:345:OPPD:S3458 NEBCTY2G | External | 106.04 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.11 | 603179 MEC-CT1 115 600047 G261 MEC-CT1 15 1: 603179 MEC-CT1 115 600047 G261 MEC-CT1 15.0 1 | External | 106.06 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.45 | P12:161:AMMO::OVERTON:MOBERLY:1 | External | 101.29 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.9 | P11:345:WERE:JECU3_GEN:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.57 | 635590 FALLOW 3 345 637089 HEARTLD DIV2 345 1: 635590 FALLOW 3 345 637089 HEARTLD DIV2 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01123 | 104.14 | 601034 NOBLES 3 345 631138 LAKEFLD3 345 1: 601034 NOBLES 3 345 631138 LAKEFLD3 345 1 | External | 103.91 | 0.23
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.88 | P13:013-138:AMMO::OSAGE:4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.89 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.58 | 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1: 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01059 | 106.02 | P23:345:XEL:8S23 WLM | External | 105.87 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.49 | P43:345-500:OKGE:SB_FTTH7306 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01103 | 116.36 | P42:345:OKGE:SB_RARD7313 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 239 | 239 | 0.00106 | 100.81 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 100.73 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | P23:345:MEC:LEHIGH 0390 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01043 | 116.04 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.59 | 92300: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00025 | 109.86 | 620314 BIGSTON4 230 620325 BROWNSV4 230 1: 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | External | 109.83 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.61 | 635200 RAUN 3 345 635214 NEAL 4G 24 1: 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | External | 108.42 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1 | External | 105.21 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P11:345:OPPD:NEBCTY1G:LT | External | 106 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00024 | 107.53 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 107.49 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.36 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.06 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 2: 602030 WHT 14 5 161 997625 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997625 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997625 WHT 14 5 13.8 2 602030 WHT 14 5 161 997632 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997632 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997632 WHT 14 5 13.8 2 | External | 110 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.94 | 85478: 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 | External | 105.89 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.42 | 81395: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.32 | 92300: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.87 | P11:345:WERE:JECU2_GEN:: | External | 111.91 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.8 | P11:345:WERE:JECU3_GEN:: | External | 107.68 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01103 | 116.29 | P42:345:OKGE:SB_RARD7311 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01048 | 116.83 | P12:161:MEC:AUTO-SINGLE:WEBSTER5:WRIGHT5:1 | External | 116.39 | 0.44
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01072 | 116.03 | 84130: 510907 PITTSB-7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510925 KIOWA 7 345 1 510907 PITTSB-7 345 514809 JOHNCO 7 345 1 510907 PITTSB-7 345 515045 SEMINOL7 345 1 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01138 | 105.88 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 105.75 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 105.49 | P23:345:OTP:JAMESTN3:3125:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 115.96 | 681525 GRANGRAE 161 699010 NED 161 161 1: 681525 GRANGRAE 161 699010 NED 161 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01165 | 104.24 | 300132 5THMHLB2 161 300207 5MEADVL 161 1: 300132 5THMHLB2 161 300207 5MEADVL 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.85 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 108.44 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.26 | 81725: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 2 | External | 116.05 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14487 | 108.4 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 107.5 | 0.9
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 108.91 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00024 | 107.53 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 107.49 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 113.99 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 113.88 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00348 | 108.14 | 300091 5LATHRP 161 300098 5MOCITY 161 1: 300091 5LATHRP 161 300098 5MOCITY 161 1 | External | 107.97 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.43 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 115.29 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 114.08 | 104639: 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 | External | 113.91 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00265 | 115.65 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.03 | P13:138,18:CLEC::G1-2ACAD::1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01072 | 105.31 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998300 CIMARON1 138 1 514901 CIMARON7 345 998299 CIMARON2 138 1 514901 CIMARON7 345 998308 CIMARON1 138 1 514901 CIMARON7 345 998307 CIMARON2 138 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 116.16 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 116.05 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 105.51 | 300339 5EMERSN 161 300363 5NEWARK 161 1: 300339 5EMERSN 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 115.98 | 300339 5EMERSN 161 300363 5NEWARK 161 1: 300339 5EMERSN 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.53 | P13:23-345:OPPD:NEBCTY2G | External | 108.32 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00033 | 118.36 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 118.29 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 118.48 | 104644: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 118.01 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635431 J529J590COL1 34.5 1 | 1 | 1 | 3e-05 | 18416.61 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 18416.62 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00064 | 114.77 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 114.62 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.22 | P11:18:EES:DOWAEP:U1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00061 | 111.64 | P11:024:DPC:ALMA2:6 | External | 111.63 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.24 | P42:345:OKGE:SB_FTTH7386 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01068 | 116.01 | P12:138:MKEC:BARBER-FLATRIDGE:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00419 | 113.98 | 104640: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 113.88 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.08906 | 104.33 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 103.78 | 0.55
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 105.4 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.53 | P11:345:WERE:JECU3_GEN:: | External | 101.41 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.16 | P42:345:OKGE:SB_FTTH7385 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01153 | 104.24 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.03 | 500020 ACADIA 4 138 501912 G1-2ACAD 18 1: 500020 ACADIA 4 138 501912 G1-2ACAD 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 108.57 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External | 108.56 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0002 | 104.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.93 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00336 | 120.08 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 119.67 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P13:230:EES:STGABE:T1 | External | 115.81 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.69 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 115.54 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00298 | 118.57 | 104640: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 118.61 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 105.46 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.37 | 303023 8XMFRINT4 500 303027 1S4INTHB 18 1: 303023 8XMFRINT4 500 303027 1S4INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00918 | 106.16 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1: 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 101.53 | Base Case | External | 101.54 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00349 | 106.14 | P23:345:AMMO::ZACHARY:3 | External | 106 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P11:16:AEPW:FULTONU1 1 | External | 115.96 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.83 | P12:LV-HV:EES::6CALCASIEU%:1DYNEGY_U2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.51 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External | 108.38 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 107.85 | 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22 1: 615600 GRE-COAL CR4 230 615001 GRE-COAL 41G 22.0 1 | External | 107.84 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.16 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.54 | 661015 COYOTE1G 24 661016 COYOTE 3 345 1: 661015 COYOTE1G 24.0 661016 COYOTE 3 345 1 | External | 101.45 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.47 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1 | External | 101.35 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.27 | P41:345:OKGE:SB_MUGE7385 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01158 | 104.06 | 104117: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.06 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 105 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.38 | P11:18:CLEC::G1-2ACAD:1 | External | 116.07 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 106.64 | 300103 5NEWMAD 161 301397 5NORANDA1 161 1: 300103 5NEWMAD 161 301397 5NORANDA1 161 1 | External | 106.53 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01103 | 116.56 | P42:345:OKGE:SB_RARD7311 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1 | External | 115.86 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 116.01 | P23:345:OTP:JAMESTN3:3125:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00233 | 112.27 | 85485: 640183 GENTLMN3 345 640252 KEYSTON3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 640183 GENTLMN3 345 997408 GGS T1 230 1 640183 GENTLMN3 345 997407 GGS T2 230 2 587850 GEN-2016-106 345 640183 GENTLMN3 345 1 640183 GENTLMN3 345 997415 GGS T1 230 1 640183 GENTLMN3 345 997414 GGS T2 230 2 | External | 112.36 | -0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.41 | 500020 ACADIA 4 138 501912 G1-2ACAD 18 1: 500020 ACADIA 4 138 501912 G1-2ACAD 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.39 | P13:13-13-161:XEL:AUTO-SINGLE:WHT51G:WHT52G:WHT145:1 | External | 110.34 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01018 | 116.4 | P13:161-345:AMMO::ZACHARY:1 | External | 116.25 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01123 | 103.97 | 601050 HELENA 3 345 615646 GRE-CDRMTH13 345 1: 601050 HELENA 3 345 615646 GRE-CDRMTH13 345 1 | External | 103.89 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01131 | 103.89 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P22:345:OPPD:S3458 NEBCTY1G:LT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 104.94 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 104.83 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.3 | P12:LV-HV:EES::4CARROLS%:1EXXONGT1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.14 | P11:345:MEC-OPPD:NEBRASKA CITY 2 | External | 106.1 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.16 | 81395: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 117.5 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 117.41 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.35 | P42:345:NPPD:BKR-GGS-3304 | External | 112.4 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P11:16:AEPW:FULTONU1 1 | External | 105.14 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.85 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01068 | 105.41 | P12:138:MKEC:BARBER-FLATRIDGE:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01047 | 106.13 | P12:161:MEC:AUTO-SINGLE:FRANKLN5:WALLLK5:1 | External | 105.87 | 0.26
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01018 | 116.4 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 116.25 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01178 | 104.09 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998300 CIMARON1 138 1 514901 CIMARON7 345 998299 CIMARON2 138 1 514901 CIMARON7 345 998308 CIMARON1 138 1 514901 CIMARON7 345 998307 CIMARON2 138 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 180.67 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 180.71 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00254 | 112.3 | 105850: 652529 WATERTN3 345 652829 WATERTN-LNX3 345 Z 652537 WHITE 3 345 652829 WATERTN-LNX3 345 1 652293 WHITE 9 13.8 997148 WHT KU1A 115 1 652504 BROOKNG7 115 652538 WHITE 7 115 1 652538 WHITE 7 115 655472 IVANHOE-ER7 115 1 652538 WHITE 7 115 997148 WHT KU1A 115 1 601006 SPLT RK3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 2 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 652537 WHITE 3 345 997148 WHT KU1A 115 1 652293 WHITE 9 13.8 997155 WHT KU1A 115 1 652538 WHITE 7 115 997155 WHT KU1A 115 1 652537 WHITE 3 345 997155 WHT KU1A 115 1 652293 WHITE 9 13.8 997146 WHT KU1A 115 1 652538 WHITE 7 115 997146 WHT KU1A 115 1 652537 WHITE 3 345 997146 WHT KU1A 115 1 | External | 112.36 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.19563 | 105.97 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 104.73 | 1.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.14 | P11:HV:EES::1DOW_AEP_4!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.0003 | 110.14 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 110.08 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.53 | P23:345:OPPD:S3458 NEBCTY2G | External | 108.32 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.04 | 345401 4OSG_1&2TAP 138 345403 4OSAGE_U1&2 138 1: 345401 4OSG_1&2TAP 138 345403 4OSAGE_U1&2 138 1 | External | 116.07 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 115.92 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00056 | 106.12 | 105850: 652529 WATERTN3 345 652829 WATERTN-LNX3 345 Z 652537 WHITE 3 345 652829 WATERTN-LNX3 345 1 652293 WHITE 9 13.8 997148 WHT KU1A 115 1 652504 BROOKNG7 115 652538 WHITE 7 115 1 652538 WHITE 7 115 655472 IVANHOE-ER7 115 1 652538 WHITE 7 115 997148 WHT KU1A 115 1 601006 SPLT RK3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 2 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 652537 WHITE 3 345 997148 WHT KU1A 115 1 652293 WHITE 9 13.8 997155 WHT KU1A 115 1 652538 WHITE 7 115 997155 WHT KU1A 115 1 652537 WHITE 3 345 997155 WHT KU1A 115 1 652293 WHITE 9 13.8 997146 WHT KU1A 115 1 652538 WHITE 7 115 997146 WHT KU1A 115 1 652537 WHITE 3 345 997146 WHT KU1A 115 1 | External | 106.08 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.21 | 82343: 645022 N OMA 2G 13.8 645122 NO2 AUX9 2.40 1 646211 S1211 5 161 645022 N OMA 2G 13.8 1 645023 N OMA 3G 13.8 645123 NO3 AUX9 2.40 1 646211 S1211 5 161 645023 N OMA 3G 13.8 1 645021 N OMA 1G 13.8 645121 NO1 AUX9 2.40 1 647911 S911 8 69.0 645021 N OMA 1G 13.8 1 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 645451 S3451 3 345 645459 S3459 3 345 1 | External | 112.24 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01104 | 116.6 | P42:345:OKGE:SB_HURS7389 | External | 116.14 | 0.46
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.38 | P41:345:AEPW:LEBROCK CB 13220 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.04 | P11:20:AEPW:WILKE1-1 | External | 103.98 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00229 | 131.35 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 131.74 | -0.39
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 145.85 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 145.73 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00918 | 116.75 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1: 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 7e-05 | 108.78 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.74 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00622 | 109.64 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 109.74 | -0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.0001 | 118.95 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 118.89 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01037 | 115.96 | P12:161:DPC-ALTE:AUTO-SINGLE:GRANGRAE:NED161:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0106 | 105.44 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.69 | P11:23.8:CLEC:: G6-1COUGH:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.84 | 92487: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 105.75 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.53 | P22:345:OPPD:S3458 NEBCTY2G | External | 108.32 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.68 | 81725: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 2 | External | 105.5 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.57 | 81735: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515302 FTSMITH7 345 998249 FTSMITH5 161 5 515302 FTSMITH7 345 998248 FTSMITH1 345 1 515302 FTSMITH7 345 998257 FTSMITH5 161 5 515302 FTSMITH7 345 998256 FTSMITH1 345 1 515302 FTSMITH7 345 998254 FTSMITH5 161 5 515302 FTSMITH7 345 998253 FTSMITH1 345 1 | External | 105.42 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 104.89 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 104.79 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01018 | 105.72 | P23:345:AMMO::ZACHARY:3 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | 717.1 | 717.1 | 0.03702 | 100.33 | P12:115:MIDW:BUSHTON-RICE COUNTY | Internal | 100.1 | 0.23
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.38 | 303030 8XFMRINT2 500 303034 1S2INTHB 18 1: 303030 8XFMRINT2 500 303034 1S2INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01066 | 116.27 | P12:161:ALTW-MEC:AUTO-SINGLE:REASNOR5:RISINGSUN5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00407 | 113.36 | 344233 5CALIF UE 161 345411 5OVERTON 2 161 1: 344233 5CALIF UE 161 345411 5OVERTON 2 161 1 | External | 113.23 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.08 | P11:13.8:AMMO:1OSAGE:1&2 | External | 116.07 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.35 | P23:345:AEPW:LEBROCK CB 13250 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 105.1 | 344001 5ADAIR2 161 631112 APANOSE5 161 1: 344001 5ADAIR2 161 631112 APANOSE5 161 1 | External | 105.09 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.14 | P13:138-18:AEPW:STLGENS4_#2 | External | 115.88 | 0.26
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01043 | 105.35 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00229 | 131.33 | 84410: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.85 | 0.48
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18665 | 100.12 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.78 | P23:345:WERE:JEC_345-15:: | External | 111.79 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.01 | 104748: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 106.01 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 110.67 | 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1: 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1 | External | 110.53 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01072 | 105.46 | 84130: 510907 PITTSB-7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510925 KIOWA 7 345 1 510907 PITTSB-7 345 514809 JOHNCO 7 345 1 510907 PITTSB-7 345 515045 SEMINOL7 345 1 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.98 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 123.98 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.6 | P42:345:OKGE:SB_FTTH7386 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P11:HV:EES::FULTONU1 1:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01018 | 116.4 | 344006 5ADAIR3 161 344010 5ZACKARY 161 1: 344006 5ADAIR3 161 344010 5ZACKARY 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.88 | P11:18:EES:DOWAEP:U1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00061 | 109.84 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 109.85 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.95 | P11:23.8:CLEC::G7-2COUGH:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1 | External | 115.86 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01035 | 116.42 | P12:230:XEL:MNV-GRA-PTH | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.14 | P42:345:OKGE:SB_FTTH7385 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1 | External | 105.21 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1 | External | 116.09 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.06 | P13:13-13-161:XEL:AUTO-SINGLE:WHT53G:WHT54G:WHT145:2 | External | 110 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.12 | P11:345:OPPD:NEBCTY1G | External | 106.05 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.86 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | External | 108.7 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01195 | 107.02 | P12:161:ALTW-MEC:AUTO-SINGLE:REASNOR5:RISINGSUN5:1 | External | 106.92 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P22:345:OPPD:S3458 NEBCTY1G | External | 106.01 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.34 | P42:345:OKGE:SB_FTTH7386 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 108.91 | 635200 RAUN 3 345 645451 S3451 3 345 1: 635200 RAUN 3 345 645451 S3451 3 345 1 | External | 108.63 | 0.28
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0028 | 117.3 | 104570: 301342 5BUTLER 161 541208 NEVADA 5 161 1 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 117.03 | 0.27
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.92 | P12:HV:EES::3PLANTATION!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01049 | 106.17 | P13:069:MEC:WRIGHT AB | External | 105.9 | 0.27
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.00025 | 100.72 | 620314 BIGSTON4 230 620325 BROWNSV4 230 1: 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | External | 100.69 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.34 | 104662: 543080 HAWTH 2 69.0 548803 SUB F 69.0 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01104 | 116.33 | P42:345:OKGE:SB_HURS7389 | External | 115.88 | 0.45
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00392 | 114.01 | P12:161:KCPL:AECINORTON-KCPLNORTON-MARSHALLJCT | External | 113.92 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01053 | 116.74 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01062 | 116.32 | 81741: 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998272 SUNNYSD3 138 1 515136 SUNNYSD7 345 998271 SUNNYSD2 138 1 515136 SUNNYSD7 345 998280 SUNNYSD3 138 1 515136 SUNNYSD7 345 998279 SUNNYSD2 138 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 120.21 | Base Case | External | 120.09 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00622 | 109.64 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 109.74 | -0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.66 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 105.56 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.99 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 105.94 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00275 | 127.23 | 300043 7KINGDM 345 300044 7MCCRED 345 1: 300043 7KINGDM 345 300044 7MCCRED 345 1 | External | 127.27 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.98 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 123.98 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.51 | P23:345:AEPW:LEBROCK CB 13220 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00445 | 117.6 | 104570: 301342 5BUTLER 161 541208 NEVADA 5 161 1 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 117.23 | 0.37
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 109.05 | 85478: 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 | External | 108.98 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 143.65 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 143.66 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 110.67 | 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2: 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2 | External | 110.53 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00051 | 106.18 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 106.11 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.92 | P11:230:WERE:JECU1_GEN:: | External | 107.78 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00275 | 127.16 | 300090 5KINGDM 161 300043 7KINGDM 345 1: 300090 5KINGDM 161 300043 7KINGDM 345 1 | External | 127.28 | -0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.83 | P12:HV:EES::3PLANTATION!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.56 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 101.44 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.55 | 300025 1NDWYG1 13.8 300104 5NODWAY 161 1: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 | External | 101.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00204 | 111.75 | P23:345:WERE:JEC_345-16:: | External | 111.79 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 116.04 | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00392 | 114.28 | 300105 5NORTON 161 543064 NORTON-5 161 Z1: 300105 5NORTON 161 543064 NORTON-5 161 Z1 | External | 114.12 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 108.63 | 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1: 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1 | External | 108.52 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01224 | 104.29 | P42:345:OKGE:SB_RARD7311 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.53 | P13:138-18:AEPW:STLGENS4_#2 | External | 105.31 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P12:HV:EES::FULTON!:1 | External | 105.14 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 107.85 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 107.84 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01151 | 104.37 | P23:345:XEL:8S23 WLM | External | 104.24 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01053 | 105.86 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.77 | P22:345:OPPD:S3458 NEBCTY1G:LT | External | 108.39 | 0.38
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17277 | 107.87 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 106.8 | 1.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 6e-05 | 100.45 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | External | 100.34 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01104 | 115.95 | P42:345:OKGE:SB_HURS7309 | External | 115.77 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.37 | P11:13.8:AMMO:1OSAGE:7&8 | External | 116.38 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.46 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2 | External | 101.35 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01055 | 105.61 | P23:345:AMMO::SIOUX:32H | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00399 | 137.77 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External | 137.79 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00251 | 112.19 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 112.23 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 110.27 | Base Case | External | 110.15 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00253 | 112.3 | 82339: 645454 S3454 3 345 650185 WAGENER 3 345 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 648351 S3451T49 13.8 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 648251 S3451T39 13.8 997277 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 648351 S3451T49 13.8 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 648251 S3451T39 13.8 997284 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 648351 S3451T49 13.8 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 648251 S3451T39 13.8 997275 S3451 T3 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 118.48 | 300070 5CLARK 161 541208 NEVADA 5 161 1: 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 118.02 | 0.46
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 108.57 | 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22 1: 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 | External | 108.56 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01042 | 117.22 | 631087 VINTON 5 161 631088 ARNOLD 5 161 1: 631087 VINTON 5 161 631088 ARNOLD 5 161 1 | External | 117.06 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01145 | 104.34 | P12:161:ALTW:AUTO-SINGLE:TIMBRCK5:M-TOWN_W5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.34 | 636620 WALCOTT3 345 636625 IPSCO 3 345 1: 636620 WALCOTT3 345 636625 IPSCO 3 345 1 | External | 101.3 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00399 | 108.72 | P23:345:WERE:JEC_345-20:: | External | 108.61 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00229 | 131.35 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 131.74 | -0.39
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01047 | 116.76 | 636230 FRANKLN5 161 636235 WALL LK5 161 1: 636230 FRANKLN5 161 636235 WALL LK5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01053 | 116.48 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.03 | P13:138:CLEC:ND:G1-2ACAD:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00341 | 105.7 | 344001 5ADAIR2 161 344004 5ADAIR1 161 Z: 344001 5ADAIR2 161 344004 5ADAIR1 161 Z | External | 105.57 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01138 | 104.96 | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1: 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | External | 104.72 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00622 | 109.64 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 109.74 | -0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00242 | 117.8 | P12:138:AMMO::BLAND:OSAGE:6030 | External | 117.85 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.44 | 601003 PR ISLD3 345 600003 PR IS31G 20 2: 601003 PR ISLD3 345 600003 PR IS31G 20.0 2 | External | 101.33 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01025 | 116.32 | 82341: 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17634 | 101.17 | P12:115:MIDW:LYONS-WHEATLANDS | Internal | 100.03 | 1.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00031 | 119.22 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 119.19 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.85 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00035 | 110.99 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 110.92 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0106 | 116.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.6 | P11:18:AEPW:STALL6A | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 180.67 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 180.71 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00562 | 126.61 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 126.04 | 0.57
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01048 | 116.23 | 300339 5EMERSN 161 300363 5NEWARK 161 1: 300339 5EMERSN 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00349 | 106.14 | P13:161-345:AMMO::ZACHARY:1 | External | 106 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00298 | 118.19 | P12:161:GMO:GRAINVALLEY-OAKGROVE-ODESSA | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.21 | 636620 WALCOTT3 345 636625 IPSCO 3 345 1: 636620 WALCOTT3 345 636625 IPSCO 3 345 1 | External | 112.27 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.92 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | External | 111.98 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.84 | 104719: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541253 ST JOE 5 161 541257 COOK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 109.24 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 109.16 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 3e-05 | 113.35 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.35 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.06 | P13:013-138:AMMO::OSAGE:2 | External | 116.07 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.1 | P23:345:OPPD:S3458 NEBCTY2G | External | 106.04 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01104 | 116.51 | P42:345:OKGE:SB_HURS7319 | External | 116.14 | 0.37
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.84 | P12:HV:EES::FULTON!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 105.54 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 105.41 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 118.48 | 84404: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 | External | 118.01 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01056 | 105.23 | P42:345:OKGE:SB_TAGA7381 | External | 105.23 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00251 | 111.86 | 104853: 562711 G15_023_1 345 640510 HOLT.CO3 345 1 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.8 | P13:18-345:OPPD:NEBCTY1G | External | 108.46 | 0.34
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.08 | P12:HV:EES::FULTON!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.18 | P12:345:OKGE:BKRBKR295 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P13:18-345:OPPD:NEBCTY1G | External | 106.01 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.36 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 101.28 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.33 | 82331: 645022 N OMA 2G 13.8 645122 NO2 AUX9 2.40 1 646211 S1211 5 161 645022 N OMA 2G 13.8 1 645023 N OMA 3G 13.8 645123 NO3 AUX9 2.40 1 646211 S1211 5 161 645023 N OMA 3G 13.8 1 645021 N OMA 1G 13.8 645121 NO1 AUX9 2.40 1 647911 S911 8 69.0 645021 N OMA 1G 13.8 1 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 | External | 112.38 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00374 | 100.78 | 82339: 645454 S3454 3 345 650185 WAGENER 3 345 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 648351 S3451T49 13.8 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 648251 S3451T39 13.8 997277 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 648351 S3451T49 13.8 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 648251 S3451T39 13.8 997284 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 648351 S3451T49 13.8 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 648251 S3451T39 13.8 997275 S3451 T3 161 1 | External | 100.59 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01119 | 104.11 | P23:345:OTP:CENTER 3:3245 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00025 | 109.86 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 109.83 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00262 | 116.52 | 104639: 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 | External | 116.52 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00957 | 118.8 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 118.72 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01055 | 116.2 | P23:345:AMMO::SIOUX:32H | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01138 | 105.88 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 105.75 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01068 | 116.27 | P12:138:MKEC:BARBER-FLATRIDGE:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.33 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 115.21 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 103.93 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.82 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 108.99 | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 645451 S3451 3 345 997276 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External | 108.84 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 116.54 | P12:161:MEC:AUTO-SINGLE:WEBSTER5:WRIGHT5:1 | External | 116.1 | 0.44
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00958 | 117.63 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 117.5 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01018 | 116.15 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 116.01 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.23 | P41:345:AEPW:LEBROCK CB 13220 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00235 | 115.8 | P12:138:AMMO::MARIES:OSAGE:1 | External | 115.58 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.14 | 601004 WILMART3 345 601030 MEC-ST 345 1: 601004 WILMART3 345 601030 MEC-ST 345 1 | External | 106.09 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | 621318 CROWN RDG 230 621319 CROWN RDG N 230 1: 621318 CROWN RDG 230 621319 CROWN RDG N 230 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 109.05 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 108.97 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 100.85 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | External | 100.74 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.84 | P11:16:AEPW:FULTONU1 1 | External | 115.7 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.00989 | 106.35 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 106.27 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00224 | 112.13 | 85222: 300101 5MORGAN 161 505498 STOCKTN5 161 1 300118 5STKAEC 161 505498 STOCKTN5 161 1 300816 5COLLINS 161 505498 STOCKTN5 161 1 505498 STOCKTN5 161 505500 STK #1 1 13.8 1 | External | 112.2 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 114.08 | 84380: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 | External | 113.91 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 7e-05 | 108.78 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.74 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00399 | 136.08 | P12:161:AECI:M:HUNTSDL:C_PERCH:1 | External | 136.09 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00227 | 112.2 | 20632: 640065 AXTELL 3 345 640312 PAULINE3 345 1 560062 G15088_T 345 640277 MOORE 3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | External | 112.27 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1 | External | 105.21 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01104 | 116.24 | P42:345:OKGE:SB_HURS7319 | External | 115.87 | 0.37
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.85 | P13:138:EES:ND:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01018 | 116.16 | 344006 5ADAIR3 161 344010 5ZACKARY 161 1: 344006 5ADAIR3 161 344010 5ZACKARY 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1 | External | 115.86 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 109.92 | P13:13-13-161:XEL:AUTO-SINGLE:WHT55G:WHT56G:WHT565:1 | External | 109.87 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00958 | 117.34 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 117.21 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0002 | 108.49 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.43 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.88 | P11:HV:EES::1DOW_AEP_4!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15135 | 105.19 | Base Case | Internal | 104.15 | 1.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01233 | 104.32 | P42:345:OKGE:SB_HURS7389 | External | 104.07 | 0.25
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01046 | 105.36 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.23 | P43:345-500:OKGE:SB_FTTH7306 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 118.19 | 104571: 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 541227 OAKGRV 5 161 541229 ODESSA 5 161 1 | External | 118.22 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 109.08 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | External | 108.99 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17634 | 104.21 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal | 103.07 | 1.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 131.06 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 131.04 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.51 | P11:18:AEPW:LEBROCG1 | External | 105.29 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.41 | P11:138-18:CLEC::ACADIA 4:1(2) | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.06 | P11:23.8:CLEC:: G6-1COUGH:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.14 | P11:18:EES:DOWAEP:U1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00057 | 110.03 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 109.97 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01233 | 104.28 | P42:345:OKGE:SB_HURS7319 | External | 104.06 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.0003 | 111.27 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 111.26 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00399 | 137.77 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External | 137.79 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.95 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 103.95 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00036 | 111.12 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 111.04 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 116.16 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 116.05 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.32 | 303029 8XFMRINT1 500 303032 1S1INTHB 18 1: 303029 8XFMRINT1 500 303032 1S1INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1 | External | 115.86 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 116.54 | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1: 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00041 | 106.25 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 106.18 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.58 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 115.46 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.8 | P23:345:OPPD:S3458 NEBCTY1G | External | 108.46 | 0.34
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01123 | 104.14 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.96 | P12:LV-HV:EES::6CALCASIEU%:1DYNEGY_U2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.77 | P11:345:MEC-OPPD:NEBRASKA CITY 1 | External | 108.39 | 0.38
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.93 | 105883: 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | External | 111.98 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.59 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | External | 105.5 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00022 | 106.76 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 106.79 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.19 | P13:138:EES:ND:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01043 | 115.96 | P12:230:WERE:AUBN-SWIS_230:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.98 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 123.98 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.2 | P12:115:XEL:BDS #2 5 | External | 106.15 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01037 | 105.35 | 681525 GRANGRAE 161 699010 NED 161 161 1: 681525 GRANGRAE 161 699010 NED 161 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00061 | 111.64 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 111.63 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.19 | P23:345:OTP:CENTER 3:3245 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.76 | P11:345:WERE:JECU2_GEN:: | External | 107.68 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.56 | P23:345:OTP:CENTER 3:3215(1) | External | 101.48 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.18 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1: 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00412 | 114.67 | P23:161-345:GMO:BLUESPRINGSE_R4-12::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 114.51 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.09249 | 105.31 | P13:115-230:MIDW:RICE COUNTY | Internal | 104.71 | 0.6
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00025 | 108.2 | P12:230:OTP::BIGSTON4:HANKSON4 | External | 108.16 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.92 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0114 | 104.97 | P13:069:MEC:WRIGHT AB | External | 104.8 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 116.22 | 681525 GRANGRAE 161 699010 NED 161 161 1: 681525 GRANGRAE 161 699010 NED 161 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 122.48 | 104501: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 122.48 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 142.42 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.33 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00212 | 124.36 | 300105 5NORTON 161 543064 NORTON-5 161 Z1: 300105 5NORTON 161 543064 NORTON-5 161 Z1 | External | 124.36 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.24 | P11:18:AEPW:STALL6B | External | 116 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.16 | 81735: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515302 FTSMITH7 345 998249 FTSMITH5 161 5 515302 FTSMITH7 345 998248 FTSMITH1 345 1 515302 FTSMITH7 345 998257 FTSMITH5 161 5 515302 FTSMITH7 345 998256 FTSMITH1 345 1 515302 FTSMITH7 345 998254 FTSMITH5 161 5 515302 FTSMITH7 345 998253 FTSMITH1 345 1 | External | 104.04 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01042 | 117.22 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 117.06 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01045 | 105.15 | 345402 5OSAGE 161 345400 4OSAGE 138 1: 345402 5OSAGE 161 345400 4OSAGE 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.84 | 603271 FARIBALT GEN 115 600050 FEP CT G 18 1: 603271 FARIBALT GEN 115 600050 FEP CT G 18.0 1 | External | 105.77 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01148 | 104.31 | 300076 5FAIRPT 161 300039 7FAIRPT 345 3: 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | External | 104.2 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17634 | 102.63 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal | 101.52 | 1.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01062 | 116.06 | 81741: 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998272 SUNNYSD3 138 1 515136 SUNNYSD7 345 998271 SUNNYSD2 138 1 515136 SUNNYSD7 345 998280 SUNNYSD3 138 1 515136 SUNNYSD7 345 998279 SUNNYSD2 138 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.57 | 92482: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 107.28 | 0.29
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.1 | P13:138:CLEC:ND:G1-2ACAD:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00019 | 138.86 | P23:500:EMI-EES:ABF_FRKLN-A | External | 138.87 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 103.87 | 635369 KOSSUTH 3 345 635441 PLM CRK B1 9 34.5 1: 635369 KOSSUTH 3 345 635441 PLM CRK B1 9 34.5 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.06 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0039 | 118.25 | 300336 2HOLDEN 69 300124 5HOLDEN 161 1: 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | External | 118.14 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01046 | 116.02 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | External | 108.66 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 5e-05 | 108.04 | Base Case | External | 108.06 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.05 | 303023 8XMFRINT4 500 303027 1S4INTHB 18 1: 303023 8XMFRINT4 500 303027 1S4INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.01 | P11:230:WERE:JECU1_GEN:: | External | 112.05 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.02 | P11:13.8:AMMO:1OSAGE:5&6 | External | 116.09 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 105.49 | P23:345:OTP:JAMESTN3:3115:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15997 | 104.52 | P12:115:MKEC:SAINTJOHN-SAINTJOHN(MIDWEST):: | Internal | 103.53 | 0.99
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.66 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1 | External | 100.52 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00402 | 108.84 | P23:345:MEC:CBEC 905 | External | 108.66 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00918 | 106.94 | P23:345:MEC:ATCHISON CO 903 | External | 106.81 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01049 | 105.64 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.66 | 635200 RAUN 3 345 645451 S3451 3 345 1: 635200 RAUN 3 345 645451 S3451 3 345 1 | External | 100.52 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 249.95 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 250.04 | -0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.1 | P11:138-18:CLEC::ACADIA 4:1(2) | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 110.39 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 110.34 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01128 | 105.99 | 631187 IRVINE_5 161 635870 BEACON 5 161 1: 631187 IRVINE_5 161 635870 BEACON 5 161 1 | External | 105.89 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.06 | 345403 4OSAGE_U1&2 138 345396 1OSAGE 1&2 13.8 1: 345403 4OSAGE_U1&2 138 345396 1OSAGE 1&2 13.8 1 | External | 116.07 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.00988 | 107.09 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 107.03 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00328 | 101.51 | 852690: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 560062 G15088_T 345 640277 MOORE 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | External | 101.45 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01042 | 116.94 | 631087 VINTON 5 161 631088 ARNOLD 5 161 1: 631087 VINTON 5 161 631088 ARNOLD 5 161 1 | External | 116.79 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.14487 | 110.48 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 109.57 | 0.91
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 112.41 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 112.48 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.32 | 104665: 542973 HAWTHS5 161 548814 SUB M-161 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 138.44 | Base Case | External | 138.29 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.85 | P13:138:EES:ND:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.39 | P42:345:OKGE:SB_FTTH7385 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.45 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1 | External | 101.37 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.62 | P11:18:AEPW:STALL6B | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P13:230:EES:STGABE:T1 | External | 116.09 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.05 | 303030 8XFMRINT2 500 303034 1S2INTHB 18 1: 303030 8XFMRINT2 500 303034 1S2INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.36 | P13:345-34:MEC:AUTO-SINGLE:IPSCO3:IPSCOSV9:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.61 | P23:345:MEC:RAUN 0210 | External | 108.43 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.11 | 603285 WOAD HILL 7 115 601073 WOAD HILL 3 345 1: 603285 WOAD HILL 7 115 601073 WOAD HILL 3 345 1 | External | 106.06 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00061 | 109.84 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 109.85 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.22 | P11:18:AEPW:LEBROCG2 | External | 104.08 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P13:138:EES:ND:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01038 | 105.38 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17634 | 101.42 | P12:115:MIDW:RICE-LYONS | Internal | 100.31 | 1.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01045 | 115.98 | 345402 5OSAGE 161 345400 4OSAGE 138 1: 345402 5OSAGE 161 345400 4OSAGE 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01104 | 116.21 | P42:345:OKGE:SB_HURS7309 | External | 116.03 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 101.23 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 101.22 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.96 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 131.65 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.73 | P23:345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.69 | P12:LV-HV:EES::6CALCASIEU%:1DYNEGY_U2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01049 | 116.13 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01233 | 104.14 | P42:345:OKGE:SB_HURS7309 | External | 104.03 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.09 | P12:HV:EES::3PLANTATION!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00349 | 106.14 | 344006 5ADAIR3 161 344010 5ZACKARY 161 1: 344006 5ADAIR3 161 344010 5ZACKARY 161 1 | External | 105.99 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.00913 | 106.47 | P23:345:MEC:ATCHISON CO 903 | External | 106.37 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00399 | 136.08 | 300500 5HUNTSDL 161 343004 5PERCHE 161 1: 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | External | 136.09 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00016 | 137.19 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.12 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635432 J529J590 SUB 345 635430 J529J590COL2 34.5 1 | 1 | 1 | 0.00024 | 18416.61 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 18416.62 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01038 | 116.19 | 88028: 503912 FULTON 3 115 507453 HOPE 3 115 1 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | External | 116 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 109.05 | P13:345-34:MEC:AUTO-SINGLE:IPSCO3:IPSCOSV9:1 | External | 108.97 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.75 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 115.83 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01068 | 116.18 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01161 | 104.4 | 300098 5MOCITY 161 344558 5MAURER LK 161 1: 300098 5MOCITY 161 344558 5MAURER LK 161 1 | External | 104.19 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.02 | 345406 4OSG_5&6TAP 138 345398 1OSAGE 5&6 13.8 1: 345406 4OSG_5&6TAP 138 345398 1OSAGE 5&6 13.8 1 | External | 116.09 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00384 | 107.85 | 104564: 300117 5SEDALA 161 541217 WINDSR 5 161 1 300071 5CLINTN 161 541217 WINDSR 5 161 1 | External | 107.67 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01158 | 104.56 | P12:161:ALTW-MEC:AUTO-SINGLE:JASPER5:NEANKNY5:1 | External | 104.45 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 109.92 | 602031 WHT 56 5 161 3WXFMR WHT 56 5 1: 602031 WHT 56 5 161 997623 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997623 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997623 WHT 56 5 13.8 1 602031 WHT 56 5 161 997630 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997630 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997630 WHT 56 5 13.8 1 602031 WHT 56 5 161 997624 WHT 56 5 13.8 1 600037 WHT 56G 13.8 997624 WHT 56 5 13.8 1 600036 WHT 55G 13.8 997624 WHT 56 5 13.8 1 | External | 109.87 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 5e-05 | 110.72 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 110.8 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 106.38 | 344012 7HPW-N 345 344013 7HPW-S 345 1: 344012 7HPW-N 345 344013 7HPW-S 345 1 | External | 106.32 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.77 | P11:345:OPPD:NEBCTY1G:LT | External | 108.39 | 0.38
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.49 | P11:18:AEPW:STALL6A | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.54 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1: 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1 | External | 101.41 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.24 | P11:18:AEPW:LEBROCG1 | External | 104.09 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 111.18 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 111.13 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.66 | P22:345:OPPD:S3451-RAUN | External | 100.52 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.49 | 637091 CONTRAIL W 161 637092 J611 COL 34.5 1: 637091 CONTRAIL W 161 637092 J611 COL 34.5 1 | External | 101.34 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.29 | 104719: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541253 ST JOE 5 161 541257 COOK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01059 | 116.29 | P23:345:XEL:8S23 WLM | External | 116.12 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 106.39 | 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2: 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2 | External | 106.27 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01049 | 116.51 | P13:069:MEC:WRIGHT AB | External | 116.2 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.08 | P23:345:AEPW:LEBROCK CB 13250 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 100.18 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External | 100.07 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01059 | 116.57 | P23:345:XEL:8S23 WLM | External | 116.4 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.25 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1 | External | 105.21 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.61 | P13:013-138:AMMO::OSAGE:4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.59 | P12:345:OKGE:BKRBKR295 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1 | External | 116.13 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.8 | P13:500:EES:ND:1PERRYV_C2:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01044 | 116.8 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 116.62 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00131 | 101.33 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 101.34 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.02 | 303023 8XMFRINT4 500 303027 1S4INTHB 18 1: 303023 8XMFRINT4 500 303027 1S4INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.14542 | 109.04 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | External | 108.93 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 145.85 | P11:024:DPC:ALMA2:6 | External | 145.73 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17277 | 105.51 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 104.48 | 1.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 118.75 | 601039 NROC 3 345 613060 BYRON 3 345 1: 601039 NROC 3 345 613060 BYRON 3 345 1 | External | 118.5 | 0.25
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01104 | 104.6 | 82341: 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External | 104.49 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00431 | 114.16 | 84408: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 114 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00957 | 118.5 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 118.43 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01138 | 104.96 | P12:161:MEC:AUTO-SINGLE:WEBSTER5:WRIGHT5:1 | External | 104.72 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01042 | 106.63 | 631087 VINTON 5 161 631088 ARNOLD 5 161 1: 631087 VINTON 5 161 631088 ARNOLD 5 161 1 | External | 106.5 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01039 | 105.6 | P12:115:XEL:CRY-RRK | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 110.29 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 110.37 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.19563 | 103.51 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 102.3 | 1.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00022 | 106 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 106.03 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 114.44 | 615307 GRE-PL VLLY5 161 615032 GRE-PVS 52G 16 1: 615307 GRE-PL VLLY5 161 615032 GRE-PVS 52G 16.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.28 | P11:138:AMMO::MERAMEC:2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.49 | P11:18:AEPW:LEBROCG2 | External | 105.25 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.28 | P23:345:OTP:JAMESTN3:3125:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 106.64 | 300103 5NEWMAD 161 301399 5NORANDA3 161 1: 300103 5NEWMAD 161 301399 5NORANDA3 161 1 | External | 106.53 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.01 | P13:013-138:AMMO::OSAGE:4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.82 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.71 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.19 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00401 | 108.4 | P11:345:MEC-OPPD:NEBRASKA CITY 2 | External | 108.18 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01131 | 104.89 | 631087 VINTON 5 161 631088 ARNOLD 5 161 1: 631087 VINTON 5 161 631088 ARNOLD 5 161 1 | External | 104.78 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01047 | 116.48 | P12:161:MEC:AUTO-SINGLE:FRANKLN5:WALLLK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.38 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 123.39 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 111.47 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 111.4 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 114.36 | 84406: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 120.94 | -6.58
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0103 | 116.01 | P23:345:OTP:JAMESTN3:3115:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 119.61 | 104529: 541205 BLSPE 5 161 541211 BLSPS 5 161 1 541206 PRALEE 5 161 541211 BLSPS 5 161 1 541205 BLSPE 5 161 541226 GRAINVL5 161 1 | External | 119.65 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.14 | 601030 MEC-ST 345 600046 G261 MEC-ST 19.5 1: 601030 MEC-ST 345 600046 G261 MEC-ST 19.5 1 | External | 106.08 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 108.49 | 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1: 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1 | External | 108.38 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.16 | 104665: 542973 HAWTHS5 161 548814 SUB M-161 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.65 | P43:345-500:OKGE:SB_FTTH7306 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01141 | 105.19 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 105.09 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.1 | 104719: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541253 ST JOE 5 161 541257 COOK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01103 | 105.52 | P42:345:OKGE:SB_RARD7313 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00256 | 116.35 | 300540 2NORTON 69 300105 5NORTON 161 1: 300540 2NORTON 69.0 300105 5NORTON 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 111.57 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 111.51 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.56 | P23:345:OTP:CENTER 3:3225(1) | External | 101.48 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01072 | 116.14 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998300 CIMARON1 138 1 514901 CIMARON7 345 998299 CIMARON2 138 1 514901 CIMARON7 345 998308 CIMARON1 138 1 514901 CIMARON7 345 998307 CIMARON2 138 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 114.69 | 615307 GRE-PL VLLY5 161 615032 GRE-PVS 52G 16 1: 615307 GRE-PL VLLY5 161 615032 GRE-PVS 52G 16.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 106.35 | 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1: 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1 | External | 106.28 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.45 | 345221 5MOBERLY 161 345409 5OVERTON 161 1: 345221 5MOBERLY 161 345409 5OVERTON 161 1 | External | 101.29 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00431 | 114.16 | 104649: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 114 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.92 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.38 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 123.39 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 108.97 | P23:345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.22 | P11:18:AEPW:STALL6A | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 138.75 | Base Case | External | 138.6 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.17 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00262 | 116.46 | 104637: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 | External | 116.46 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 106.19 | P12:161:MEC:AUTO-SINGLE:WEBSTER5:WRIGHT5:1 | External | 105.81 | 0.38
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.39 | P11:18:AEPW:LEBROCG1 | External | 116.11 | 0.28
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 116.14 | 81735: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515302 FTSMITH7 345 998249 FTSMITH5 161 5 515302 FTSMITH7 345 998248 FTSMITH1 345 1 515302 FTSMITH7 345 998257 FTSMITH5 161 5 515302 FTSMITH7 345 998256 FTSMITH1 345 1 515302 FTSMITH7 345 998254 FTSMITH5 161 5 515302 FTSMITH7 345 998253 FTSMITH1 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00256 | 117.51 | 300088 5HUBEN 161 300042 7HUBEN 345 1: 300088 5HUBEN 161 300042 7HUBEN 345 1 | External | 117.52 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.59 | 81395: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.12 | P13:23-345:OPPD:NEBCTY2G | External | 110.97 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.57 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 107.28 | 0.29
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.85 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 108.44 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 106.11 | 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1: 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1 | External | 106 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 131.99 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 131.87 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.08 | P11:13.8:AMMO:1OSAGE:3&4 | External | 116.07 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.25 | P13:138-18:AEPW:STLGENS4_#2 | External | 104.11 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 3e-05 | 113.2 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.2 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 1e-05 | 155.48 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9: 601002 ADAMS 3 345 997679 ADAMS 3 161 9 631046 ADAMS 5 161 997679 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997679 ADAMS 3 161 9 601002 ADAMS 3 345 997686 ADAMS 3 161 9 631046 ADAMS 5 161 997686 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997686 ADAMS 3 161 9 601002 ADAMS 3 345 997682 ADAMS 3 161 9 631046 ADAMS 5 161 997682 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997682 ADAMS 3 161 9 | External | 155.43 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01103 | 116.1 | P42:345:OKGE:SB_RARD7313 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.11 | P11:18:CLEC::G1-2ACAD:1 | External | 115.8 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 113.96 | 104637: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 | External | 113.79 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.86 | P23:345:MEC:CBEC 908 | External | 108.44 | 0.42
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.37 | P13:138,18:CLEC::G1-2ACAD::1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00044 | 119.92 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 119.86 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.04 | 345404 4OSG_3&4TAP 138 345405 4OSAGE_U3&4 138 1: 345404 4OSG_3&4TAP 138 345405 4OSAGE_U3&4 138 1 | External | 116.07 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00386 | 108.32 | 104280: 532851 AUBURN 6 230 532852 JEC 6 230 1 532852 JEC 6 230 532861 EMANHAT6 230 1 532852 JEC 6 230 532651 JEC U1 26.0 1 532852 JEC 6 230 997953 JEC TX-13 230 1 532852 JEC 6 230 997952 JEC TX-26 230 1 532852 JEC 6 230 997959 JEC TX-13 230 1 532852 JEC 6 230 997958 JEC TX-26 230 1 532852 JEC 6 230 997955 JEC TX-13 230 1 532852 JEC 6 230 997954 JEC TX-26 230 1 | External | 108.19 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 4e-05 | 117.33 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.33 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 119.06 | 345409 5OVERTON 161 346117 2OVERTON 69 1: 345409 5OVERTON 161 346117 2OVERTON 69.0 1 | External | 119.11 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00246 | 118.93 | P13:161-345:AMMO::MONTGOMERY:1 | External | 118.96 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.73 | P44:345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 478 | 478 | 0.00031 | 106.13 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 106.11 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.07 | 104662: 543080 HAWTH 2 69.0 548803 SUB F 69.0 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 603020 MAPLE R7 115 997618 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00065 | 125.61 | 93772: 652435 FARGO 4 230 997175 FA KV1A 115 1 652436 FARGO 7 115 997175 FA KV1A 115 1 652434 FARGOSVC 13.2 997175 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997174 FA KV2A 115 2 652436 FARGO 7 115 997174 FA KV2A 115 2 652434 FARGOSVC 13.2 997174 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997182 FA KV1A 115 1 652436 FARGO 7 115 997182 FA KV1A 115 1 652434 FARGOSVC 13.2 997182 FA KV1A 115 1 652435 FARGO 4 230 997181 FA KV2A 115 2 652436 FARGO 7 115 997181 FA KV2A 115 2 652434 FARGOSVC 13.2 997181 FA KV2A 115 2 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 | External | 125.61 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01047 | 116.76 | P12:161:MEC:AUTO-SINGLE:FRANKLN5:WALLLK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01072 | 115.88 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998300 CIMARON1 138 1 514901 CIMARON7 345 998299 CIMARON2 138 1 514901 CIMARON7 345 998308 CIMARON1 138 1 514901 CIMARON7 345 998307 CIMARON2 138 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.35 | 92338: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.21 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.61 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | External | 108.42 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.4 | P13:013-138:AMMO::OSAGE:4 | External | 116.38 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00349 | 106.14 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 106 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 113.56 | 104618: 541232 LEX161 5 161 541236 RICHMND5 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541236 RICHMND5 161 541244 ORRICK 5 161 1 | External | 113.42 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00264 | 117.37 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01025 | 116.07 | 82341: 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | 635100 RLHILLS3 345 635103 RLHILLS B2 9 34.5 1: 635100 RLHILLS3 345 635103 RLHILLS B2 9 34.5 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.22 | P23:345:AEPW:LEBROCK CB 13250 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.09 | P11:18:AEPW:LEBROCG2 | External | 115.84 | 0.25
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.1 | 500020 ACADIA 4 138 501912 G1-2ACAD 18 1: 500020 ACADIA 4 138 501912 G1-2ACAD 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.48 | 104662: 543080 HAWTH 2 69.0 548803 SUB F 69.0 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00373 | 100.66 | P14:345:OPPD-MEC:S3451 REAC-1 | External | 100.52 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.41 | P11:18:CLEC::G1-2ACAD:1 | External | 105.14 | 0.27
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01103 | 105.69 | P42:345:OKGE:SB_RARD7311 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 143.65 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 143.66 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00255 | 112.22 | 635200 RAUN 3 345 645451 S3451 3 345 1: 635200 RAUN 3 345 645451 S3451 3 345 1 | External | 112.07 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0106 | 116.27 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00424 | 113.39 | 104651: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 113.27 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.41 | P13:138:CLEC:ND:G1-2ACAD:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.34 | P12:LV-HV:EES::4CARROLS%:1EXXONGT1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01018 | 105.72 | P13:161-345:AMMO::ZACHARY:1 | External | 105.59 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00022 | 106 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 106.03 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 100.62 | P23:345:MEC:ROLLING HILLS 906 | External | 100.51 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.1 | P13:23-345:OPPD:NEBCTY2G | External | 106.04 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.74 | 82335: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 107.61 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01138 | 104.89 | P12:161:MEC:AUTO-SINGLE:FRANKLN5:WALLLK5:1 | External | 104.72 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00269 | 116.06 | 104564: 300117 5SEDALA 161 541217 WINDSR 5 161 1 300071 5CLINTN 161 541217 WINDSR 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00037 | 133.23 | 105830: 616002 GRE-JOHNJCT7 115 616003 GRE-GRACEV 7 115 1 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 616001 GRE-WALDEN 7 115 620218 MOROTP 7 115 1 620218 MOROTP 7 115 652555 MORRIS 7 115 1 620170 EFERGUS7 115 658102 GRANTCO7 115 1 652555 MORRIS 7 115 658102 GRANTCO7 115 1 658102 GRANTCO7 115 658104 ELBOWLK7 115 1 652555 MORRIS 7 115 652318 MORRIS 9 41.6 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652554 MORRIS 4 230 652555 MORRIS 7 115 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 | External | 133.17 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.85 | P11:345:OPPD:NEBCTY1G | External | 108.51 | 0.34
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.51 | P11:18:AEPW:STALL6B | External | 116.27 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 110.29 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 110.37 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.39 | 81735: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515302 FTSMITH7 345 998249 FTSMITH5 161 5 515302 FTSMITH7 345 998248 FTSMITH1 345 1 515302 FTSMITH7 345 998257 FTSMITH5 161 5 515302 FTSMITH7 345 998256 FTSMITH1 345 1 515302 FTSMITH7 345 998254 FTSMITH5 161 5 515302 FTSMITH7 345 998253 FTSMITH1 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01018 | 116.4 | P23:345:AMMO::ZACHARY:3 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.84 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 108.66 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01044 | 117.05 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 116.87 | 0.18
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.14 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | External | 106.09 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01047 | 116.48 | 636230 FRANKLN5 161 636235 WALL LK5 161 1: 636230 FRANKLN5 161 636235 WALL LK5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.00626 | 110.29 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 110.37 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 103.63 | Base Case | External | 103.48 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00044 | 112.95 | P12:115:XEL:AUTO-SINGLE:CRYSTAL7:RIVFLSN7:1 | External | 112.91 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.4 | 345407 4OSG_7&8TAP 138 345399 1OSAGE 7&8 13.8 1: 345407 4OSG_7&8TAP 138 345399 1OSAGE 7&8 13.8 1 | External | 116.38 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16976 | 101.2 | P12:115:WERE:RENO-WMCP_115:: | Internal | 100.14 | 1.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.69 | 92300: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00918 | 117.36 | P23:345:MEC:ATCHISON CO 903 | External | 117.22 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00504 | 129.1 | 104628: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 300082 5GEORGE 161 541209 SEDALIA5 161 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541271 SEDN 2 69.0 541273 KELHYS 2 69.0 1 | External | 129.09 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01072 | 116.3 | 84130: 510907 PITTSB-7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510925 KIOWA 7 345 1 510907 PITTSB-7 345 514809 JOHNCO 7 345 1 510907 PITTSB-7 345 515045 SEMINOL7 345 1 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.37 | 500020 ACADIA 4 138 501912 G1-2ACAD 18 1: 500020 ACADIA 4 138 501912 G1-2ACAD 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00022 | 106.76 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 106.79 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P11:HV:EES::FULTONU1 1:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 105.57 | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00035 | 111.51 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 111.43 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.29 | P11:18:AEPW:STALL6A | External | 104.17 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01018 | 116.15 | P13:161-345:AMMO::ZACHARY:1 | External | 116.01 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1 | External | 116.13 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00056 | 109.55 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 109.49 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00431 | 114.97 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 114.68 | 0.29
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.92 | P13:138:EES:ND:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01043 | 115.79 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01048 | 115.93 | P12:161:MPW-MEC-ITC-CIPCO::NEWPORT5:MPWSPLIT:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00262 | 115.81 | 84304: 541232 LEX161 5 161 541236 RICHMND5 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541236 RICHMND5 161 541244 ORRICK 5 161 1 | External | 115.83 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.6 | P13:500:EES:ND:1PERRYV_C2:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.32 | P13:161-34:MEC:AUTO-SINGLE:ADAMSWF5:ADAMSWF9:1 | External | 101.2 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01049 | 116.8 | P13:069:MEC:WRIGHT AB | External | 116.49 | 0.31
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 131.99 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 131.87 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.31 | 303023 8XMFRINT4 500 303027 1S4INTHB 18 1: 303023 8XMFRINT4 500 303027 1S4INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.24 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01133 | 104.02 | 635700 SYCAMOR3 345 3WXFMR DAG9T2 2: 635700 SYCAMOR3 345 997478 DAG9T2 161 2 635701 SYCAMOR5 161 997478 DAG9T2 161 2 635707 SYCA2XT9 13.8 997478 DAG9T2 161 2 635700 SYCAMOR3 345 997485 DAG9T2 161 2 635701 SYCAMOR5 161 997485 DAG9T2 161 2 635707 SYCA2XT9 13.8 997485 DAG9T2 161 2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.83 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1: 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.82 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.71 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.16976 | 103.21 | P12:115:WERE:RENO-WMCP_115:: | Internal | 102.13 | 1.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.00913 | 104.93 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1: 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00384 | 100.41 | P23:345:MEC:ATCHISON CO 903 | External | 100.27 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.48 | P23:345:AEPW:LEBROCK CB 13250 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.35 | 104501: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.21 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.38 | P23:345:AEPW:LEBROCK CB 13220 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.19 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01133 | 104.12 | 635700 SYCAMOR3 345 3WXFMR DAG9T1 1: 635700 SYCAMOR3 345 997479 DAG9T1 161 1 635701 SYCAMOR5 161 997479 DAG9T1 161 1 635706 SYCA1XT9 13.8 997479 DAG9T1 161 1 635700 SYCAMOR3 345 997486 DAG9T1 161 1 635701 SYCAMOR5 161 997486 DAG9T1 161 1 635706 SYCA1XT9 13.8 997486 DAG9T1 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 4e-05 | 117.95 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.93 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 114.44 | 615307 GRE-PL VLLY5 161 615031 GRE-PVS 51G 16 1: 615307 GRE-PL VLLY5 161 615031 GRE-PVS 51G 16.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 109 | 82339: 645454 S3454 3 345 650185 WAGENER 3 345 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 648351 S3451T49 13.8 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 648251 S3451T39 13.8 997277 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 648351 S3451T49 13.8 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 648251 S3451T39 13.8 997284 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 648351 S3451T49 13.8 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 648251 S3451T39 13.8 997275 S3451 T3 161 1 | External | 108.77 | 0.23
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.09 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1: 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01141 | 105.19 | P13:345-161:MEC:AUTO-SINGLE:SEPOLK3:SEPOLK5:1 | External | 105.09 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.06 | 345405 4OSAGE_U3&4 138 345397 1OSAGE 3&4 13.8 1: 345405 4OSAGE_U3&4 138 345397 1OSAGE 3&4 13.8 1 | External | 116.07 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00412 | 114.67 | 104529: 541205 BLSPE 5 161 541211 BLSPS 5 161 1 541206 PRALEE 5 161 541211 BLSPS 5 161 1 541205 BLSPE 5 161 541226 GRAINVL5 161 1 | External | 114.51 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01035 | 105.61 | P12:230:XEL:MNV-GRA-PTH | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01054 | 105.76 | P42:345:OKGE:SB_FTTH7386 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 115.3 | 631110 WAPELLO5 161 631112 APANOSE5 161 1: 631110 WAPELLO5 161 631112 APANOSE5 161 1 | External | 115.34 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00298 | 118.57 | 84399: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 118.61 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00424 | 114.24 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 104.27 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.24 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01018 | 116.15 | P23:345:AMMO::ZACHARY:3 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.05 | 303029 8XFMRINT1 500 303032 1S1INTHB 18 1: 303029 8XFMRINT1 500 303032 1S1INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P12:HV:EES::FULTON!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 122.48 | 92230: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 122.48 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01157 | 104.02 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.03 | 334391 4CARROLS% 138 334392 1EXXONGT1! 18 1: 334391 4CARROLS% 138 334392 1EXXONGT1! 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 249.95 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 250.04 | -0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01165 | 104.24 | 300068 5CHILLI 161 300207 5MEADVL 161 1: 300068 5CHILLI 161 300207 5MEADVL 161 1 | External | 104.13 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 115.87 | P13:500:EES:ND:1PERRYV_C2:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 105.97 | 92473: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 105.96 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01158 | 104.09 | 104151: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00242 | 118.06 | 345400 4OSAGE 138 345404 4OSG_3&4TAP 138 Z: 345400 4OSAGE 138 345404 4OSG_3&4TAP 138 Z | External | 117.93 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01145 | 104.51 | P12:161:ALTW:AUTO-SINGLE:M-TOWN_W5:STRY_CO5:1 | External | 104.39 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.03 | P11:138-18:CLEC::ACADIA 4:1(2) | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.22 | P11:18:EES:DOWAEP:U2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.74 | 105018: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 107.61 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 114.08 | 104626: 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 110.62 | 92482: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 110.41 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01062 | 105.49 | 81741: 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998272 SUNNYSD3 138 1 515136 SUNNYSD7 345 998271 SUNNYSD2 138 1 515136 SUNNYSD7 345 998280 SUNNYSD3 138 1 515136 SUNNYSD7 345 998279 SUNNYSD2 138 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01044 | 106.32 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 106.16 | 0.16
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 114.36 | 104647: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 120.94 | -6.58
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P23:345:OPPD:S3458 NEBCTY1G | External | 106.01 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.35 | P11:18:AEPW:LEBROCG2 | External | 116.11 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00229 | 131.33 | 104651: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.85 | 0.48
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.21 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:IPSCO3:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01055 | 116.46 | P23:345:AMMO::SIOUX:32H | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.22 | P42:345:AEPW:LEBROCK CB 13250 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01054 | 115.94 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN | External | 115.81 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00031 | 119.22 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 119.19 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1 | External | 103.9 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.0105 | 104.27 | 82344: 635000 CBLUFFS3 345 645456 S3456 3 345 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 645030 SCBSD G 4.20 645033 SARPY 3G 13.8 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 645035 SARPY 5G 13.8 997266 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997266 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997273 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997273 SARPY4&5 GSU 13.8 1 645035 SARPY 5G 13.8 997264 SARPY4&5 GSU 13.8 1 645034 SARPY 4G 13.8 997264 SARPY4&5 GSU 13.8 1 | External | 104.17 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00429 | 115.22 | 300098 5MOCITY 161 344558 5MAURER LK 161 1: 300098 5MOCITY 161 344558 5MAURER LK 161 1 | External | 114.92 | 0.3
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 112.79 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External | 112.77 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00041 | 104.74 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 104.72 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01018 | 105.72 | 344006 5ADAIR3 161 344010 5ZACKARY 161 1: 344006 5ADAIR3 161 344010 5ZACKARY 161 1 | External | 105.6 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00016 | 139.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.74 | 0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00446 | 117.88 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 117.23 | 0.65
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.28 | P11:023:NPPD:GENTLM1G:1:757 | External | 112.33 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00228 | 131.7 | 84408: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.23 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 114.7 | 615307 GRE-PL VLLY5 161 615031 GRE-PVS 51G 16 1: 615307 GRE-PL VLLY5 161 615031 GRE-PVS 51G 16.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00044 | 119.92 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 119.86 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 116.02 | P13:013-138:AMMO::OSAGE:3 | External | 116.09 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.95 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | External | 108.36 | 0.59
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.92 | P13:138:EES:ND:1ACADIA_C25!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.05 | P11:138:AMMO::MERAMEC:2 | External | 103.92 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00061 | 249.95 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 250.04 | -0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104 | P12:LV-HV:EES::4CARROLS%:1EXXONGT1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 118.48 | 84403: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 118.01 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.23 | P23:345:AEPW:LEBROCK CB 13220 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01048 | 116.83 | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1: 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.17634 | 102.99 | P12:115:MIDW:RICE-LYONS | Internal | 101.85 | 1.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 6e-05 | 105.4 | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1: 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | External | 105.42 | -0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01056 | 116.09 | P42:345:OKGE:SB_TAGA7381 | External | 116.07 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.58 | P13:345-34:MEC:AUTO-SINGLE:RLHILLS3:RLHILLSB9:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 113.87 | Base Case | External | 113.91 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01035 | 116.15 | P12:230:XEL:MNV-GRA-PTH | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00389 | 105.79 | 344558 5MAURER LK 161 543060 CAROLTN5 161 1: 344558 5MAURER LK 161 543060 CAROLTN5 161 1 | External | 105.64 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.54 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.55 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.12 | P11:18:AEPW:LEBROCG1 | External | 115.85 | 0.27
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00262 | 115.81 | 104618: 541232 LEX161 5 161 541236 RICHMND5 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541236 RICHMND5 161 541244 ORRICK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01046 | 115.75 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01025 | 105.62 | 82341: 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 646206 S1206 5 161 997272 S3456 T4 161 1 648256 S3456T49 13.8 997272 S3456 T4 161 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 648256 S3456T49 13.8 997279 S3456 T4 161 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | External | 105.49 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.37 | P13:138:CLEC:ND:G1-2ACAD:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.32 | 303030 8XFMRINT2 500 303034 1S2INTHB 18 1: 303030 8XFMRINT2 500 303034 1S2INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.15135 | 107.05 | Base Case | Internal | 105.99 | 1.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01127 | 104.14 | 88028: 503912 FULTON 3 115 507453 HOPE 3 115 1 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | External | 104.03 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00334 | 119.88 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 103.7 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 103.73 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 109.08 | 636620 WALCOTT3 345 636625 IPSCO 3 345 1: 636620 WALCOTT3 345 636625 IPSCO 3 345 1 | External | 108.99 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00212 | 124.36 | P12:161:KCPL:AECINORTON-KCPLNORTON-MARSHALLJCT | External | 124.42 | -0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00328 | 101.51 | 20632: 640065 AXTELL 3 345 640312 PAULINE3 345 1 560062 G15088_T 345 640277 MOORE 3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | External | 101.45 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01104 | 105.63 | P42:345:OKGE:SB_HURS7319 | External | 105.3 | 0.33
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00393 | 123.38 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 123.39 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 105.4 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.03 | P12:LV-HV:EES::4CARROLS%:1EXXONGT1!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01037 | 116.22 | P12:161:DPC-ALTE:AUTO-SINGLE:GRANGRAE:NED161:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00918 | 117.03 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1: 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.17 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1 | External | 116.13 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.16 | 92300: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 548814 SUB M-161 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | P23:345:MEC:LUNDGREN 911 OR 912 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01039 | 116.22 | P12:115:XEL:CRY-RRK | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00562 | 126.61 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 126.04 | 0.57
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.41 | P13:138,18:CLEC::G1-2ACAD::1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.84 | P11:HV:EES::FULTONU1 1:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | 280 | 308 | 0.09249 | 103.77 | P13:115-230:MIDW:RICE COUNTY | Internal | 103.16 | 0.61
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00022 | 106.76 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 106.79 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P23:345:OPPD:S3458 NEBCTY1G:LT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.3 | P11:18:AEPW:STALL6B | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1 | External | 103.9 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01056 | 115.82 | P42:345:OKGE:SB_TAGA7381 | External | 115.81 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01123 | 103.99 | 601050 HELENA 3 345 615647 GRE-CDRMTH23 345 2: 601050 HELENA 3 345 615647 GRE-CDRMTH23 345 2 | External | 103.84 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00227 | 112.2 | 852690: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 560062 G15088_T 345 640277 MOORE 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | External | 112.27 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00044 | 113.07 | P12:115:XEL:AUTO-SINGLE:WILOWRV7:THREELAKES7:1 | External | 112.97 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.08906 | 105.87 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 105.32 | 0.55
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.37 | P11:138-18:CLEC::ACADIA 4:1(2) | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 111.18 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 111.13 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00389 | 107.64 | 300098 5MOCITY 161 344558 5MAURER LK 161 1: 300098 5MOCITY 161 344558 5MAURER LK 161 1 | External | 107.43 | 0.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00408 | 114.08 | 84398: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 | External | 113.91 | 0.17
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 111.39 | P11:345:OPPD:NEBCTY1G | External | 111.02 | 0.37
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00265 | 116.63 | 84579: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | External | 116.61 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01154 | 104.07 | 104570: 301342 5BUTLER 161 541208 NEVADA 5 161 1 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00958 | 106.99 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 106.88 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337600 3REED% 115 337602 3DUMAS% 115 1 | 106 | 106 | 0.00018 | 105.81 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.77 | 0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 116.28 | P23:345:OTP:JAMESTN3:3115:V2020 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.12 | P41:345:AEPW:LEBROCK CB 13220 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.0003 | 110.14 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 110.08 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 116.16 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 116.05 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1: 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 107.75 | P23:345:WERE:JEC_345-19:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.42 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | 280 | 308 | 0.18665 | 102.46 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal | 101.25 | 1.21
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.11 | P13:138:EES:ND:1ACADIA_C24!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.04 | P11:18:CLEC::G1-2ACAD:1 | External | 103.85 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.41 | P13:138-18:AEPW:STLGENS4_#2 | External | 116.15 | 0.26
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 111.16 | Base Case | External | 111.04 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01018 | 105.72 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 105.59 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 119.61 | P23:161-345:GMO:BLUESPRINGSE_R4-12::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 119.65 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.11 | 601073 WOAD HILL 3 345 601074 CRANDAL 3 345 1: 601073 WOAD HILL 3 345 601074 CRANDAL 3 345 1 | External | 106.06 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.32 | P12:161:ALTW:AUTO-SINGLE:PLAZA5:TIMBRCK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 103.7 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 103.73 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01139 | 104.39 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.38 | 303029 8XFMRINT1 500 303032 1S1INTHB 18 1: 303029 8XFMRINT1 500 303032 1S1INTHB 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00253 | 112.08 | 105856: 648516 GRPR11 9 34.5 645065 GRPR11 W 0.69 1 648523 GRPR21 9 34.5 645067 GRPR21 W 0.69 1 648519 GRPR12 9 34.5 645066 GRPR12 W 0.69 1 648513 GRPR1 3 345 648520 GRPR2 3 345 1 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 648513 GRPR1 3 345 997246 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997245 GRPR1 TFMR 2 34.5 1 648526 GRPR22 9 34.5 645068 GRPR22 W 0.69 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z 652532 GR PRAIRIE 3 345 579457 G16-075XFMR1 34.5 1 648514 GRPR11X9 34.5 648516 GRPR11 9 34.5 Z1 648514 GRPR11X9 34.5 997246 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997246 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997244 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997245 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997244 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997243 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997243 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997253 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997252 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997253 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997253 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997251 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997252 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997251 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997250 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997250 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997244 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997243 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997244 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997244 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997242 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997243 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997242 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997241 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997241 GRPR2 TFMR 2 34.5 1 | External | 112.02 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 133.49 | 105811: 620263 FORMN 7 115 652438 FORMAN 7 115 1 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1 652438 FORMAN 7 115 652462 ELLIOTT7 115 1 652438 FORMAN 7 115 659172 LUDDEN -CP7 115 1 652438 FORMAN 7 115 997172 FO KY1A 69.0 1 652439 FORMAN 8 69.0 655630 COGSWELL-CP8 69.0 1 652327 FORMAN 9 41.8 652439 FORMAN 8 69.0 1 652439 FORMAN 8 69.0 997172 FO KY1A 69.0 1 652393 FORMAN9 12.5 997172 FO KY1A 69.0 1 620262 GWINNER7 115 620263 FORMN 7 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 652438 FORMAN 7 115 997179 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997179 FO KY1A 69.0 1 652393 FORMAN9 12.5 997179 FO KY1A 69.0 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 652438 FORMAN 7 115 997170 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997170 FO KY1A 69.0 1 652393 FORMAN9 12.5 997170 FO KY1A 69.0 1 | External | 133.64 | -0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.08 | P11:HV:EES::FULTONU1 1:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01125 | 103.91 | 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1: 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00262 | 116.52 | 84398: 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541262 LIBERTY2 69.0 541263 SIBLEY 2 69.0 1 | External | 116.52 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01104 | 105.73 | P42:345:OKGE:SB_HURS7389 | External | 105.32 | 0.41
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00957 | 108.03 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 107.96 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.96 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1 | External | 103.9 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01159 | 104.06 | P42:345:OKGE:SB_TAGA7381 | External | 104.04 | 0.02
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00072 | 101.23 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 101.22 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 106.19 | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1: 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 104.27 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 104.31 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01054 | 116.53 | 81725: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 2 | External | 116.31 | 0.22
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 114.88 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 114.92 | -0.04
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.0005 | 105.84 | 104890: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 105.77 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00022 | 106 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 106.03 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0056 | 126.4 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External | 125.94 | 0.46
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00918 | 117.64 | P23:345:MEC:ATCHISON CO 903 | External | 117.5 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01049 | 116.37 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.06 | P12:LV-HV:EES::6CALCASIEU%:1DYNEGY_U2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 105.69 | 104665: 542973 HAWTHS5 161 548814 SUB M-161 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00131 | 104.25 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 104.14 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01156 | 104.14 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.77 | P23:345:OPPD:S3458 NEBCTY1G:LT | External | 108.39 | 0.38
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 103.94 | P11:18:EES:DOWAEP:U2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0002 | 101.54 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.48 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 7e-05 | 118.75 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1 | External | 118.5 | 0.25
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.004 | 108.8 | P22:345:OPPD:S3458 NEBCTY1G | External | 108.46 | 0.34
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.21 | 81725: 515224 MUSKOGE7 345 515302 FTSMITH7 345 1 515224 MUSKOGE7 345 515235 PECANCK7 345 2 | External | 104.09 | 0.12
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00845 | 113.4 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 113.39 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.00025 | 100.72 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 100.69 | 0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.12 | P23:345:AEPW:LEBROCK CB 13220 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 5e-05 | 110.72 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 110.8 | -0.08
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 106.11 | 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2: 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2 | External | 106 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00452 | 115.82 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 115.71 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 111.47 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 111.4 | 0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.35 | P11:024:NPPD:GENTLM2G:2:757 | External | 112.4 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00217 | 118.48 | 104645: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 118.01 | 0.47
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00429 | 113.2 | 344558 5MAURER LK 161 543060 CAROLTN5 161 1: 344558 5MAURER LK 161 543060 CAROLTN5 161 1 | External | 113.06 | 0.14
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.91 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.19 | P43:345-500:OKGE:SB_FTTH7306 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.89 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.9 | -0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.93 | P11:138:AMMO::MERAMEC:2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01195 | 107.02 | 631117 REASNOR5 161 635675 RISING SUN 5 161 1: 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | External | 106.92 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01038 | 115.93 | 88028: 503912 FULTON 3 115 507453 HOPE 3 115 1 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | External | 115.74 | 0.19
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 116.1 | P13:138,18:CLEC::G1-2ACAD::1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01045 | 115.72 | 345402 5OSAGE 161 345400 4OSAGE 138 1: 345402 5OSAGE 161 345400 4OSAGE 138 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01042 | 106.63 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 106.5 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00411 | 108.87 | 104853: 562711 G15_023_1 345 640510 HOLT.CO3 345 1 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | External | 108.74 | 0.13
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 105.1 | P12:161:AMMO-ITC::APANOSE:ADAIR:1 | External | 105.09 | 0.01
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01066 | 116.54 | P12:161:ALTW-MEC:AUTO-SINGLE:REASNOR5:RISINGSUN5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | P13:345-34:MEC:AUTO-SINGLE:RLHILLS3:RLHILLSA9:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00424 | 114.24 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00419 | 113.98 | 84399: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 113.88 | 0.1
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01129 | 104.15 | P12:115:XEL:CRY-RRK | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01131 | 104.89 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 104.78 | 0.11
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00389 | 105.88 | P12:161:AMMO-KCPL::MAURERLAKE:CARR:4 | External | 105.73 | 0.15
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00255 | 112.25 | P23:345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01066 | 106.01 | P12:161:ALTW-MEC:AUTO-SINGLE:REASNOR5:RISINGSUN5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.01149 | 104.18 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 248 | 248 | 0.00358 | 101.62 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z: 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 3e-05 | 102.83 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 102.83 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00255 | 112.29 | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 645451 S3451 3 345 997276 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.11 | 603002 WILMART7 115 603179 MEC-CT1 115 1: 603002 WILMART7 115 603179 MEC-CT1 115 1 | External | 106.06 | 0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 115.49 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 115.56 | -0.07
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01048 | 105.46 | P12:161:MPW-MEC-ITC-CIPCO::NEWPORT5:MPWSPLIT:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00048 | 106.09 | P11:345:MEC-OPPD:NEBRASKA CITY 1 | External | 106 | 0.09
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00246 | 118.93 | 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1: 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1 | External | 118.96 | -0.03
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00015 | 110.19 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 110.19 | 0
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.59 | 104665: 542973 HAWTHS5 161 548814 SUB M-161 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00403 | 108.05 | 82342: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 107.81 | 0.24
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 116.3 | 334391 4CARROLS% 138 334392 1EXXONGT1! 18 1: 334391 4CARROLS% 138 334392 1EXXONGT1! 18.0 1 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 104.97 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00252 | 112.34 | 105023: 645025 N OMA 5G 20.0 645 691 5 645024 N OMA 4G 15.0 645124 NO4 AUX9 2.40 1 646211 S1211 5 161 645024 N OMA 4G 15.0 1 645025 N OMA 5G 20.0 645125 NO5 AUX9 4.20 1 646211 S1211 5 161 645025 N OMA 5G 20.0 1 645024 N OMA 4G 15.0 645 691 4 | External | 112.39 | -0.05
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01043 | 116.23 | P12:230:WERE:AUBN-SWIS_230:: | External
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.0001 | 127 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997146 GF KV8A 115 1 652298 GRANITF8 69.0 997145 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997147 GF KV3A 115 1 652551 GRANITF7 115 997146 GF KV8A 115 1 652551 GRANITF7 115 997145 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997147 GF KV3A 115 1 652550 GRANITF4 230 997146 GF KV8A 115 1 619975 GRE-WILLMAR4 230 997522 230/69 69.0 1 652292 GRANITF29 13.8 997153 GF KV8A 115 1 652298 GRANITF8 69.0 997152 GF KY2A 69.0 1 652551 GRANITF7 115 997154 GF KV3A 115 1 652551 GRANITF7 115 997153 GF KV8A 115 1 652551 GRANITF7 115 997152 GF KY2A 69.0 1 652550 GRANITF4 230 997154 GF KV3A 115 1 652550 GRANITF4 230 997153 GF KV8A 115 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 126.94 | 0.06
Thermal | 00NR | S2 | 24WP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 114.88 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 114.92 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00023 | 106.84 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 106.94 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.12 | 601088 BLZNG STR1 3 345 603304 BLZNG STR1 7 115 1: 601088 BLZNG STR1 3 345 603304 BLZNG STR1 7 115 1 | External | 111.04 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.32 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 103.32 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0018 | 121.74 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 121.7 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.14 | 300025 1NDWYG1 13.8 300104 5NODWAY 161 1: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 | External | 109.15 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 103.94 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 103.89 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 100.19 | P12:345:AMMO::CALLAWAY:BLAND:1 | External | 100.19 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0001 | 143.95 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 143.84 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 109.06 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 109.01 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 113.77 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 113.56 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.43 | P13:138-24:AEPW:TURK 4 | External | 100.36 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.69 | P11:22:CLEC::G3MADISN:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.28 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.29 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01314 | 130.19 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 130.05 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.78 | P13:18-161:ALTW:AUTO-SINGLE:MGSST1:M-TOWN5:1 | External | 109.79 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 103.64 | P22:345:MEC:SUB 92 | External | 103.6 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00064 | 124.76 | P23:345:AMIL::SANDBURG:1 | External | 124.61 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.002 | 110.59 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 110.55 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 104.96 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 105 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 135.78 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 135.71 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00045 | 127.79 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 127.8 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 108.58 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 108.43 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.86 | 631166 NUTHTCH5 161 631171 WHISWIL5 161 1: 631166 NUTHTCH5 161 631171 WHISWIL5 161 1 | External | 109.87 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00048 | 126.9 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 126.69 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.8 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 127 | -0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.79 | P23:500:EAI:NBF_SAN SO~1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 140.18 | 613330 RICE 5 161 693755 JADE AVE 161 1: 613330 RICE 5 161 693755 JADE AVE 161 1 | External | 140.16 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.39 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998885 HGT X1 69.0 1 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 338373 1HGT X1 13.8 998885 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.38 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 133.05 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 133.06 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00038 | 114.95 | P23:345:MEC:WALCOTT 944 | External | 114.87 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14537 | 107.67 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 106.7 | 0.97
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.12 | P12:345:AMIL::7AUDRAIN:7SPENCER: Z | External | 107.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.97 | P11:345:AMMO::LABADIE:4 | External | 104.87 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 105.37 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 105.48 | -0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 137.92 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 137.89 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 119.75 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 119.76 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 128.09 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 127.98 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.29 | P42:345:OKGE:SB_BOER7304 | Internal | 102.28 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0012 | 104.87 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.79 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00998 | 118.69 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 118.63 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.47 | 657848 YNG2 4 230 657748 CENTER2G 20 1: 657848 YNG2 4 230 657748 CENTER2G 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00038 | 107.19 | P23:345:MEC:HILLS 9114 | External | 107.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06968 | 121.07 | 7800: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 119.44 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 2e-05 | 118.04 | P12:161:ITCM:AUTOSINGLE:LANSINGW:GENOA:1 | External | 118 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.05 | P12:HV:EES::PIRKEY 4:1 | External | 110.02 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01031 | 114.51 | P23:345:MEC:TIFFIN 944 | External | 114.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.19647 | 100.36 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635641 NORWLK5 161 635653 GRENFLD5 161 1 | 409 | 410 | 0.00399 | 100.58 | P13:161:MEC:SE POLK 9T1 | External | 100.53 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.26 | 336250 69MILE% 230 336252 1NMIL U5! 26 1: 336250 69MILE% 230 336252 1NMIL U5! 26.0 1 | External | 100.17 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01276 | 126.81 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 126.68 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 109.88 | 105871: 659354 DEERC_ST-BEG 18.0 997076 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997076 DEERCRK KU1A 18.0 1 659354 DEERC_ST-BEG 18.0 997083 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997083 DEERCRK KU1A 18.0 1 659354 DEERC_ST-BEG 18.0 997074 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997074 DEERCRK KU1A 18.0 1 | External | 109.8 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 146.74 | P23:345:ITCM:HCKRYCK:FUT3 | External | 146.47 | 0.27
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 116.93 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 131.63 | P12:161:AMMO-ALTW::CARBIDE:VIELE:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 120.76 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 120.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.56 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 141.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.98 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1 | External | 129.98 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.23 | P13:13-115:ALTW:AUTO-SINGLE:SUTHLCT2:M-TOWN7:1 | External | 135.22 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00417 | 105.38 | P23:161-345:GMO:BLUESPRINGSE_R1-3::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 105.25 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 128.03 | P11:161:ITCM:MGS CT2:2C | External | 128.04 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01207 | 127.94 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 127.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 142.68 | P13:69-161:ALTW:AUTO-SINGLE:HIAWATAJ18:HIAWATA5:1 | External | 142.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 131.63 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:CARBIDE5:1 | External | 131.5 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 106.98 | 105871: 659354 DEERC_ST-BEG 18.0 997076 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997076 DEERCRK KU1A 18.0 1 659354 DEERC_ST-BEG 18.0 997083 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997083 DEERCRK KU1A 18.0 1 659354 DEERC_ST-BEG 18.0 997074 DEERCRK KU1A 18.0 1 659353 DEERC_CT-BEG 18.0 997074 DEERCRK KU1A 18.0 1 | External | 106.88 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 109.2 | P23:345:MEC:HILLS 934 | External | 109.15 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00015 | 102.82 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 102.77 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.4 | P11:18:ALTW:AUTO-SINGLE:MGSCT1:1C | External | 101.41 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 100.33 | 63174: 344078 7WILDWD TP 345 344886 7LABADIE3 345 1 344079 7WILDWD 345 345985 4WILDWD 1 138 1 344884 7LABADIE1 345 345046 7MASON 2 345 1 344078 7WILDWD TP 345 345051 7MASON 3 345 1 344078 7WILDWD TP 345 344079 7WILDWD 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00812 | 139.78 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 139.68 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00091 | 126.1 | P12:161:MEC-WAPA:AUTO-SINGLE:FRANKLN5:HAMPTONTAP5:1 | External | 125.99 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00065 | 117.61 | 631083 TRAER 5 161 631086 DYSART 5 161 1: 631083 TRAER 5 161 631086 DYSART 5 161 1 | External | 117.56 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01286 | 127.42 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.69 | P11:22:CLEC:RODEMR1:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.43 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.43 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.39 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 135.46 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.78 | 344885 7LABADIE2 345 344895 1LAB G2 20 1: 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 105.51 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 105.5 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00033 | 132.74 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 132.75 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 128.09 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 127.98 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.5 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 116.42 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00064 | 139.81 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 139.73 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.36 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 108.21 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.88 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 135.01 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00119 | 128.51 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 128.45 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00035 | 120.19 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 119.45 | 0.74
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00389 | 103.1 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 103.02 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.39 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.38 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00021 | 111.5 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 111.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00015 | 143.8 | P13:69-161:ALTW:AUTO-SINGLE:VINTON8:VINTON5:1 | External | 143.78 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.7 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 105.52 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00565 | 105.83 | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | External | 105.7 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00125 | 120.86 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 120.79 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.0003 | 115.76 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External | 115.83 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01027 | 115.29 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 115.26 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00058 | 101.4 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 101.35 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00233 | 111.56 | P23:345:MEC:MADISON CO 901 | External | 111.39 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 124.11 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 124.01 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00056 | 139.1 | P12:115:ITCM:STON PT7-PRAR CK7:IA-EC | External | 139.02 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.0016 | 109.27 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 109.21 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01034 | 122.89 | P23:345:ALTW:MITCHLCO:1150 | External | 122.77 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 122 | 631037 MPWSPLIT 161 631108 DENMARK5 161 1: 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | External | 121.99 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 100.31 | 636001 WEBSTER5 161 637035 J524 161 1: 636001 WEBSTER5 161 637035 J524 161 1 | External | 100.32 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00018 | 118.31 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 118.19 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01067 | 119.83 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 119.48 | 0.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00037 | 212.03 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 211.98 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.8 | P23:500:EAI:NBF_SAN SO~2 | External | 110.71 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | 1061261: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.76 | P13:138-24:AEPW:TURK 4 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00037 | 212.02 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 211.98 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00547 | 115.19 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 115.01 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 142.06 | Base Case | External | 142.45 | -0.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00093 | 107.85 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.75 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.41 | 601088 BLZNG STR1 3 345 603304 BLZNG STR1 7 115 1: 601088 BLZNG STR1 3 345 603304 BLZNG STR1 7 115 1 | External | 108.33 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00034 | 105.94 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 105.89 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 103.86 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 103.86 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 118.98 | P23:345:ATC:NORTHMADISON:6037-S | External | 118.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 117.01 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:APANOSE5:1 | External | 116.98 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00441 | 104.94 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 100.19 | 344154 7BLAND 345 344224 7CALAWY 1 345 1: 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 100.19 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00196 | 123.81 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 123.8 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06916 | 109 | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.7 | P43:345:SPS:TUCO:NR20_19L | Internal | 106.67 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00531 | 107.37 | 84385: 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541273 KELHYS 2 69.0 541275 SEDPLT 2 69.0 1 | External | 107.3 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 125.26 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 125.22 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 108.48 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 108.38 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 109.25 | P22:345:XEL:ADAMS 3 N1:MN | External | 109.14 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 145.9 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 145.57 | 0.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.42 | P11:345:AMMO::LABADIE:4 | External | 124.32 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 118.53 | 658047 ALEXMRES3 345 3WXFMR ALEXMRES3 9: 658047 ALEXMRES3 345 997101 ALEXMRES3 115 9 658050 ALEXMRES7 115 997101 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997101 ALEXMRES3 115 9 658047 ALEXMRES3 345 997108 ALEXMRES3 115 9 658050 ALEXMRES7 115 997108 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997108 ALEXMRES3 115 9 658047 ALEXMRES3 345 997099 ALEXMRES3 115 9 658050 ALEXMRES7 115 997099 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997099 ALEXMRES3 115 9 | External | 118.53 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00118 | 111.5 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 111.48 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.09296 | 102.61 | P13:115-230:MIDW:RICE COUNTY | Internal | 101.93 | 0.68
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 108.45 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 107.84 | 0.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05861 | 102.5 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 101.1 | 1.4
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 137.85 | Base Case | External | 137.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.24 | 620223 HOOT LK7 115 620324 HOOTLK3G 13.8 1: 620223 HOOT LK7 115 620324 HOOTLK3G 13.8 1 | External | 113.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.15 | P11:HV:EES::PIRKEY 1:1 | External | 125.02 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 122 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:DENMARK5:1 | External | 121.99 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 153.57 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 153.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00113 | 111.63 | P12:345:OPPD-MEC:S3451-RAUN | External | 111.56 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 118.24 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 118.25 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 103.06 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 102.96 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 105.12 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 105.11 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.56 | P11:024:DPC:ALMA2:6 | External | 141.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.17683 | 102.54 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal | 101.39 | 1.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0011 | 150.9 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 150.75 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.91 | P11:345:MEC:GDMEC ST | External | 134.9 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00484 | 107.46 | P23:345:WERE:N345_345-110:: | External | 107.26 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.66 | P23:345:AEPW:WELSH CB 10630 NBTB | External | 116.62 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.18 | P11:18:ALTW:AUTO-SINGLE:MGSCT1:1C | External | 126.19 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00089 | 137.66 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 137.55 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0109 | 110.72 | P23:345:XEL:8S23 WLM | External | 110.71 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.68 | P11:16:EES-EAI:MAGNET:1 | Internal | 106.11 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 126.03 | 631017 PRAR CK7 115 629066 PR CRK4G 18 1: 631017 PRAR CK7 115 629066 PR CRK4G 18.0 1 | External | 125.99 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 121.32 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 121.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.47 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.48 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 146.37 | P22:345:XEL:ADAMS 3 N1:MN | External | 146.26 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 110.19 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 110.17 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 100.44 | 0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 132.6 | Base Case | External | 132.59 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 109.61 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 109.59 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00418 | 106.44 | 84375: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541235 DUNCAN 5 161 541250 SIBLEYPL 161 1 | External | 106.33 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 151.15 | P12:115:ALTW:AUTO-SINGLE:STONPT7:6ST7:1 | External | 151.14 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 140.22 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 140.2 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01281 | 129.75 | P23:345:ALTW:MITCHLCO:1140 | External | 129.54 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 130.33 | 631037 MPWSPLIT 161 631108 DENMARK5 161 1: 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | External | 130.3 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620263 FORMN 7 115 997497 230/115 115 1 | 112 | 132 | 0.0006 | 101.02 | 620327 HANKSON4 230 620329 WAHPETN4 230 1: 620327 HANKSON4 230 620329 WAHPETN4 230 1 | External | 100.99 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0002 | 132.18 | 620314 BIGSTON4 230 620325 BROWNSV4 230 1: 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | External | 132.08 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00047 | 139.7 | 602042 LAW CRK5 161 3WXFMR 82578T7IC002 5: 602042 LAW CRK5 161 997619 82578T7IC002 115 5 603197 LAW CRK7 115 997619 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997619 82578T7IC002 115 5 602042 LAW CRK5 161 997626 82578T7IC002 115 5 603197 LAW CRK7 115 997626 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997626 82578T7IC002 115 5 602042 LAW CRK5 161 997620 82578T7IC002 115 5 603197 LAW CRK7 115 997620 82578T7IC002 115 5 605768 LAWRENCE CK 13.8 997620 82578T7IC002 115 5 | External | 139.7 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 100.48 | 635200 RAUN 3 345 635214 NEAL 4G 24 1: 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | External | 100.45 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.8 | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 101.33 | 0.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00399 | 111.23 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 110.98 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00298 | 100.34 | 81778: 509852 T.NO.--7 345 512865 GREC TAP5 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | External | 100.24 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00152 | 128.78 | P13:161-69:MEC-WAPA:AUTO-SINGLE:WEBSTER5:WEBSTER8:1 | External | 128.69 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 143.01 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 142.96 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 0.00018 | 115.48 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:DENMARK5:1 | External | 115.48 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.41 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 118.38 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.6 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 116.47 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00133 | 109.67 | P23:345:AMIL::HERLEMAN:1 | External | 109.66 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.00837 | 117.75 | P23:345:MEC:GRIMES 901 | External | 117.67 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00127 | 103.65 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 103.57 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 107.78 | P11:345:MEC:GDMEC ST | External | 107.75 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 114.37 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 114.37 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.52 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.33 | P12:EHV:EES::WELSH 7:1 | External | 110.29 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.3 | P22:345:AMMO::LABADIE:1 | External | 124.33 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 119.9 | P23:345:ALTW:MITCHLCO:1140 | External | 119.69 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 131.69 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 130.7 | 0.99
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 125.84 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 125.83 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00027 | 107.12 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 107.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 122 | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1: 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | External | 121.97 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.28 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 2: 602030 WHT 14 5 161 997625 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997625 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997625 WHT 14 5 13.8 2 602030 WHT 14 5 161 997632 WHT 14 5 13.8 2 600034 WHT 53G 13.8 997632 WHT 14 5 13.8 2 600035 WHT 54G 13.8 997632 WHT 14 5 13.8 2 | External | 132.3 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00208 | 105.97 | P23:161-345:GMO:SIBLEY_R3-8::SIBLEY-KETCHEM-SIBLEYT11 | External | 105.84 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.36 | P13:138-24:AEPW:PIRKEY 4 | Internal | 104.83 | 1.53
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00014 | 100.07 | 300126 5MOBTAP 161 345221 5MOBERLY 161 Z1: 300126 5MOBTAP 161 345221 5MOBERLY 161 Z1 | External | 100.12 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01182 | 131.73 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 131.53 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00024 | 102.17 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 102.15 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 109.19 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 109.17 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.79 | P23:500:EES-LAGN:ABF_HTBG-B | Internal | 106.21 | 1.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.12 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | Internal | 105.6 | 1.52
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 124.23 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 124.19 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00528 | 119.21 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 119.1 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00059 | 113.77 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 113.87 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00029 | 103.76 | P23:345:AMMO::ZACHARY:2 | External | 103.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 106.82 | P22:345:AMMO::RUSHISLAND:1 | External | 106.71 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00125 | 120.86 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 120.79 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01331 | 128.95 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 128.7 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00027 | 141.94 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 141.9 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 123.25 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 123.24 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00143 | 115.18 | 636235 WALL LK5 161 636236 WALL LK8 69 1: 636235 WALL LK5 161 636236 WALL LK8 69.0 1 | External | 115.09 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 111.26 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 111.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0007 | 156.57 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 156.41 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00078 | 137.33 | P23:345:AMIL::SANDBURG:3 | External | 137.16 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0024 | 102.85 | 69825: 635631 BOONVIL5 161 635632 EARLHAM5 161 1 635632 EARLHAM5 161 635633 ADAIR 5 161 1 635632 EARLHAM5 161 635833 EARLHAM8 69.0 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | External | 102.76 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 108.72 | P23:345:MEC:LOUISA 954 | External | 108.69 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.5 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 116.42 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 114.41 | P23:345:MEC:HILLS 984 | External | 114.33 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01159 | 116.31 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 116.25 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01043 | 113.4 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 113.33 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 114.73 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External | 114.73 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00132 | 112.35 | 636050 WRIGHT 5 161 636051 WRIGHT 8 69 1: 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | External | 112.26 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01622 | 128.07 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 127.88 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.15 | P11:24:AEPW:PIRKEY 1 | External | 125.02 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 100.77 | P12:345:AMMO::BLAND:FRANKS:3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01329 | 124.45 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 124.33 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 102.92 | P13:161-69:ITCM:HAYWD#15 T1:MN | External | 102.81 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.5 | P12:EHV:EES::8COTNWOOD2!:8HARTBRG%:1 | Internal | 105.95 | 1.55
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0001 | 139.8 | P23:345:MEC:OAK GROVE 904 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01318 | 124.32 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00027 | 134.66 | P23:345-161:XEL:ADAMS_I:681_S | External | 134.64 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.59 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | Internal | 105.1 | 1.49
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00013 | 140.14 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 140.1 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 257 | 257 | 0.00239 | 104.46 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 104.39 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 123.71 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 123.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 117.44 | P23:345:XEL:8S23 WLM | External | 117.37 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00054 | 127.28 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 127.21 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.97 | P11:20:AMMO:1LAB G1:1 | External | 104.79 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0027 | 122.71 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | External | 122.69 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.29 | P13:138-24:AEPW:TURK 4 | External | 107.21 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00118 | 103.53 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External | 103.48 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 | 350 | 0.03367 | 123.52 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 123.05 | 0.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 109.33 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 109.31 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.18 | P13:138-24:AEPW:PIRKEY 4 | External | 100.09 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.16 | P11:18:ITCM:EMERYGT1:1 | External | 101.17 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 115.02 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 114.96 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 100.54 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 100.45 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00059 | 113.89 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 113.99 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00118 | 103.22 | P12:345:OPPD-MEC:S3451-RAUN | External | 103.16 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00141 | 119.24 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.15 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00391 | 108.27 | P23:345:AMMO::SPENCERCREEK:V3 | External | 108.16 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01274 | 128.67 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 128.51 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0002 | 129.91 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 129.71 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 132.42 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 132.33 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00117 | 120.94 | P12:230:OTP::HANKSON4:OAKES 4 | External | 120.83 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:345:AMMO::LABADIE:3 | External | 107.17 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.00192 | 114.87 | P23:345:MEC:SYCAMORE 905 | External | 114.71 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00033 | 100.75 | P12:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 100.7 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00099 | 100.14 | 103887: 301999 2PARKMDWS 69.0 512703 PARKMEDTP 69.0 1 512703 PARKMEDTP 69.0 512870 COLNSGR2 69.0 1 512703 PARKMEDTP 69.0 512871 SKIATTP2 69.0 1 300994 2GREEN 69.0 512874 GREENTP2 69.0 1 512872 SKIATOK2 69.0 512873 SKIATCTY2 69.0 1 512871 SKIATTP2 69.0 512872 SKIATOK2 69.0 1 512876 OSAGEK2 69.0 512877 CLEVDSTK2 69.0 1 512875 PRUEK2 69.0 512876 OSAGEK2 69.0 1 512871 SKIATTP2 69.0 512874 GREENTP2 69.0 1 512874 GREENTP2 69.0 512875 PRUEK2 69.0 1 300927 2CLEVLND 69.0 512876 OSAGEK2 69.0 1 | External | 100.11 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 103.57 | P23:345:MEC:GDMEC 908 | External | 103.54 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.48 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z: 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | External | 116.43 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00113 | 111.64 | P43:161-345:OPPD:S3451-RAUN&T4 | External | 111.56 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0003 | 103.13 | P23:345:MEC:LOUISA 964 | External | 103.1 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.07 | P42:345:OKGE:SB_BOER7384 | Internal | 101.9 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.91 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | External | 134.91 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 108.14 | 105835: 652520 OAHE 7 115 652559 OAHE 1G 13.8 1 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652489 PIERRE 7 115 652600 ASH TAP 115 1 652520 OAHE 7 115 652600 ASH TAP 115 1 652600 ASH TAP 115 658120 GARFLD 7 115 1 652476 EAGLEBT7 115 652520 OAHE 7 115 1 652491 IRVSIMM7 115 652520 OAHE 7 115 1 652520 OAHE 7 115 997156 OA NO. 5 115 1 652520 OAHE 7 115 997155 OA NO. 6 115 1 652589 OAHE 9 13.8 997156 OA NO. 5 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652520 OAHE 7 115 997163 OA NO. 5 115 1 652520 OAHE 7 115 997162 OA NO. 6 115 1 652589 OAHE 9 13.8 997163 OA NO. 5 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 652520 OAHE 7 115 997154 OA NO. 5 115 1 652520 OAHE 7 115 997153 OA NO. 6 115 1 652589 OAHE 9 13.8 997154 OA NO. 5 115 1 | External | 108.04 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00126 | 114.65 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 114.04 | 0.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 73.1 | 73.1 | 0.20789 | 118.14 | 80545: 530686 RICE 6 230 530688 BUFLOCRK6 230 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 112.3 | 5.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07488 | 125.08 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 123.75 | 1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00424 | 106.22 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 106.12 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 127.62 | P23:345:ALTW:MITCHLCO:1130 | External | 127.53 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00022 | 152.9 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 152.89 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.14 | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | External | 112.22 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00203 | 108.87 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 108.81 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 114.27 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 114.23 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.002 | 112.67 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 111.87 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.79 | P12:500:EES:STL500:OUACHI:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.4 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 152.35 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.5 | P11:22:CLEC:RODEMR1:1 | External | 116.48 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.47 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 135.58 | -0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00054 | 123.66 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 123.61 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.32 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 135.33 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.7 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 106.65 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 119.11 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 119.09 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.29 | P43:345:SPS:TUCO:NR20_19L | Internal | 102.28 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03453 | 108.47 | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 107.77 | 0.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.37 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 112.38 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01185 | 125.85 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 125.88 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00033 | 132.83 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 132.84 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 115.58 | 104644: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 115.61 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.44 | P12:EHV:EES::8SANS SOUCI%:1 | External | 109.37 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00065 | 135.82 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 135.74 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 100 | P23:345:MEC:WALCOTT 914 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 124.82 | P11:024:DPC:ALMA2:6 | External | 124.82 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 153.49 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 153.47 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00396 | 107.53 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 107.22 | 0.31
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00115 | 116.63 | P12:161:ALTW-MEC:AUTO-SINGLE:BNEJCT5:FT.DODG5:1 | External | 116.49 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 124.7 | 631075 CARBIDE5 161 630006 CARBIDE8 69 1: 631075 CARBIDE5 161 630006 CARBIDE8 69.0 1 | External | 124.59 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 119.66 | 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1: 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1 | External | 119.58 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 111.02 | P11:HV:EES::PIRKEY 1:1 | External | 110.94 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 100.98 | 635056 ADAMS 5 161 635057 ADAMS B1 9 34.5 1: 635056 ADAMS 5 161 635057 ADAMS B1 9 34.5 1 | External | 100.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 126.45 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 126.31 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00111 | 119.71 | P22:345:XEL:ADAMS 3 N1:MN | External | 119.44 | 0.27
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 128.74 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 128.66 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 116.57 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 116.58 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00062 | 149.56 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 149.49 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 137.98 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 137.93 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.56 | P23:EHV:EES::8STERLING2%:9 | External | 100.48 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00027 | 105.59 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 104.79 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.86 | P11:HV:EES::1GOXY U1!:1 | External | 116.85 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.13 | P23:345:MEC:OAK GROVE 904 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 121.48 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 121.45 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 101.64 | 345231 5MONTGMRY 161 345941 5WARENTN 161 1: 345231 5MONTGMRY 161 345941 5WARENTN 161 1 | External | 100.82 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00041 | 110.61 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 110.43 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 110.22 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 110.13 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 116.33 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 116.28 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 139.19 | P11:18:ALTW:AUTO-SINGLE:PRCRK4G:4 | External | 139.15 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01207 | 137.98 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 137.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 145.23 | P23:345:ALTW:MITCHLCO:1140 | External | 144.85 | 0.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107 | 103758: 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | Internal | 105.54 | 1.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0016 | 110.13 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 110.04 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00024 | 135.43 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 135.33 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00028 | 104.97 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.97 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 145.09 | P12:161:DPC:RCE-HAR5 | External | 145.04 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 131.52 | P12:161:XEL:JEF-WHT | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00046 | 141 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 140.93 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 105.92 | Base Case | External | 105.9 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01151 | 118.75 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 118.66 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 104.96 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 105 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.37 | 605492 WBYRON 8 69 613070 BYRON 5 161 1: 605492 WBYRON 8 69.0 613070 BYRON 5 161 1 | External | 132.34 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 122.44 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 122.44 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.42 | P11:20:AMMO:1LAB G1:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 106.51 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC | External | 106.43 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.5 | P22:345:OPPD:S3458 NEBCTY1G:LT | External | 129.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.48 | P23:345:XEL:8S50 HMP | External | 101.5 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.1 | P12:EHV:EES::WELSH 7:1 | External | 108.06 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 123.37 | P22:345:AMMO::LABADIE:2 | External | 123.39 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.71 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 126.94 | -0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.23 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.07 | P11:230-22-18:EES:HOOKER_E | External | 104.92 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 131.91 | 104649: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.98 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 115.44 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External | 115.35 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00048 | 356.52 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 356.4 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.57 | 337413 8STERLING2% 500 337434 8OUACHITA% 500 1: 337413 8STERLING2% 500 337434 8OUACHITA% 500 1 | External | 100.48 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.14 | 92482: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 129.14 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01079 | 111.19 | P23:345-161:XEL:ADAMS_I:680_S | External | 111.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00321 | 100.8 | P12:EHV:EES::8MT_OLIVE%:LAYFLD8%:1 | External | 100.77 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.43 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 112.44 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 102.1 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 102.1 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00074 | 104.4 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 104.4 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.69 | P13:13-13-161:XEL:AUTO-SINGLE:WHT51G:WHT52G:WHT145:1 | External | 132.64 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 103.4 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 103.39 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 111.46 | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | External | 111.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 105.4 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 105.37 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 115.02 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 114.96 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00069 | 100.9 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 100.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.67 | P11:230-22-18:EES:HOOKER_E | Internal | 106.99 | 1.68
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00027 | 105.7 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 104.9 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.47 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 110.44 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 103.64 | P23:345:MEC:HILLS 934 | External | 103.6 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00177 | 100.92 | P23:345:ALTW:MITCHLCO:1130 | External | 100.84 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.93 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 125.87 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00443 | 106.11 | P23:345:AMMO::MONTGOMERY:V43 | External | 106.06 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00067 | 124.44 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 124.35 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 119.12 | P22:345:MEC:SUB 92 | External | 119.04 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 3e-05 | 100.19 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.18 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01377 | 127.96 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 127.86 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 134.08 | P23:345:ALTW:MITCHLCO:1130 | External | 133.91 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00089 | 137.66 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 137.55 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.2 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | External | 100.12 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 107.28 | P23:345:ATC:NORTHMADISON:6037-S | External | 107.17 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 101.56 | P12:161:AMMO::WARRENTON:MONTGOMERY:3 | External | 100.67 | 0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 135.61 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 135.63 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00214 | 117.53 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 117.39 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.23 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 117.24 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 110.84 | 105823: 652515 HURON 7 115 660009 BTAP WP7 115 1 660003 HURONWP7 115 660009 BTAP WP7 115 1 660009 BTAP WP7 115 660040 DAKOTACCESS7 115 1 652515 HURON 7 115 652528 WOONSKT7 115 1 652515 HURON 7 115 655481 REDFELD-ER7 115 1 652515 HURON 7 115 660003 HURONWP7 115 1 652284 HURON 8 69.0 652515 HURON 7 115 1 652515 HURON 7 115 997158 HU KV1A 115 1 652515 HURON 7 115 997157 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 1 652507 FTTHOMP4 230 652514 HURON 4 230 2 652514 HURON 4 230 652530 WATERTN4 230 2 652514 HURON 4 230 652614 CARPENTER 4 230 1 652514 HURON 4 230 659205 BROADLND-BE4 230 1 652514 HURON 4 230 997158 HU KV1A 115 1 652514 HURON 4 230 997157 HU KV1B 115 2 652528 WOONSKT7 115 659123 STORLA__-BE7 115 1 652528 WOONSKT7 115 655355 WOONSKT-ER8 69.0 2 652284 HURON 8 69.0 655063 SW341-ER8 69.0 1 652284 HURON 8 69.0 655066 SW352-ER8 69.0 1 652284 HURON 8 69.0 655067 SW353-ER8 69.0 1 652282 HURON429 13.3 997157 HU KV1B 115 2 652281 HURON419 13.3 997158 HU KV1A 115 1 652515 HURON 7 115 997165 HU KV1A 115 1 652515 HURON 7 115 997164 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 2 652514 HURON 4 230 997165 HU KV1A 115 1 652514 HURON 4 230 997164 HU KV1B 115 2 652282 HURON429 13.3 997164 HU KV1B 115 2 652281 HURON419 13.3 997165 HU KV1A 115 1 652515 HURON 7 115 997156 HU KV1A 115 1 652515 HURON 7 115 997155 HU KV1B 115 2 652514 HURON 4 230 997156 HU KV1A 115 1 652514 HURON 4 230 997155 HU KV1B 115 2 652282 HURON429 13.3 997155 HU KV1B 115 2 652281 HURON419 13.3 997156 HU KV1A 115 1 | External | 111.01 | -0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 110.82 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 110.79 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00206 | 105.82 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 105.78 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 119.49 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 119.44 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 121.98 | 344290 5CARBID T 161 631075 CARBIDE5 161 1: 344290 5CARBID T 161 631075 CARBIDE5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00131 | 105.49 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 106.51 | P12:345:MEC:TIFFIN 9T1 SPS | External | 106.43 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00214 | 117.53 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 117.39 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00015 | 127.33 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 127.25 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01076 | 119.26 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 119.19 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00109 | 111.68 | P12:161:MEC-WAPA:AUTO-SINGLE:FRANKLN5:HAMPTONTAP5:1 | External | 111.57 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 115.78 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 115.66 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.96 | P12:HV:EES::TURK 4%:1(1) | External | 116.91 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 101.38 | 657848 YNG2 4 230 657748 CENTER2G 20 1: 657848 YNG2 4 230 657748 CENTER2G 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01056 | 116.11 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 116.05 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.0003 | 101.31 | P12:EHV:EES::8BIG_CAJUN2%:8WEBRE%:1 | External | 101.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.86 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 110.8 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01207 | 137.98 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 137.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 185.9 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 185.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 109.2 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 109.15 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00561 | 127.08 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 126.86 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.77 | P11:22:CLEC:RODEMR1:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 122.91 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 122.79 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00299 | 100.58 | 81775: 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 512650 GRDA1 7 345 512750 TONECE7 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512688 GRDA17-1 22.8 512650 GRDA1 7 345 1 512650 GRDA1 7 345 998343 GRDAUTO1 161 1 512650 GRDA1 7 345 998351 GRDAUTO1 161 1 512650 GRDA1 7 345 998348 GRDAUTO1 161 1 | External | 100.5 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345221 5MOBERLY 161 345409 5OVERTON 161 1 | 204 | 242 | 0.00126 | 103.07 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 102.69 | 0.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00774 | 111.63 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 111.5 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01207 | 134.46 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 134.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00101 | 116.41 | P12:161:CBPC-MEC:SHEFFIELD-HAMPTONTAP-FRANKLIN:1 | External | 116.27 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00035 | 115.04 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 115.02 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03511 | 102.52 | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | Internal | 102.3 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 135.78 | P13:115-161:ALTW:AUTO-SINGLE:STONPT7:STONPT5:1 | External | 135.71 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.43 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.43 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.002 | 104.56 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 104.43 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 105.18 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 104.94 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.74 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 116.68 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.00036 | 103.93 | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | External | 103.93 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | P11:22:AEPW:FLINTCR1 | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.03 | P11:HV:EES::PIRKEY 1:1 | External | 124.9 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 109.37 | P21:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 109.32 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05992 | 103.76 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 102.34 | 1.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01313 | 127.8 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 127.69 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 141.7 | P23:345:ALTW:MITCHLCO:1160 | External | 141.63 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00032 | 150.09 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 149.92 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00192 | 115.08 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 115.15 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 137.92 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 137.89 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.0016 | 109.27 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 109.21 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 105.63 | 104120: 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External | 105.52 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05862 | 101.62 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 100.27 | 1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 141.74 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 141.66 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00211 | 111.2 | P12:161:ALTW:AUTO-SINGLE:MTVERN5:WYOMING5:1 | External | 111.16 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.4 | 631081 M-TOWN 5 161 629216 MGS ST1 18 1: 631081 M-TOWN 5 161 629216 MGS ST1 18.0 1 | External | 126.41 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.76 | P11:345:AMMO::RUSHISLAND:U2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:24:AEPW:TURKCOAL | External | 107.18 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.97 | P11:345:AMMO::LABADIE:3 | External | 104.79 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.91 | P11:24:AEPW:PIRKEY 1 | External | 108.8 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 133.3 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 133.29 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.5 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 118.41 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.12 | P42:345:OKGE:SB_BOER7383 | Internal | 102.02 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00031 | 118.7 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 118.58 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00232 | 115.68 | P23:345:MEC:OAK GROVE 904 | External | 115.59 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06916 | 108.85 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal | 107.24 | 1.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00045 | 119.56 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 119.43 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01097 | 110.82 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 110.77 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 180.76 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 180.77 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 119.75 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 119.76 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00027 | 104.04 | 300060 5BIGSPG 161 300067 5CHAMOI 161 1: 300060 5BIGSPG 161 300067 5CHAMOI 161 1 | External | 103.14 | 0.9
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.22 | P12:345:MEC:TIFFIN 9T1 SPS | External | 116.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.31 | P12:HV:EES::FLINTCR5:1 | External | 100.24 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 153.42 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 153.34 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01032 | 115.49 | P22:345:XEL:ADAMS 3 N1:MN | External | 115.38 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01253 | 127.47 | P14:345:GMO-OPPD:S3458 REACTOR | External | 127.31 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.11 | P23:345:GRE:CHL 304JB22 | External | 116.05 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.31 | P11:13:ALTW:AUTO-SINGLE:SUTHLCT1:1C | External | 135.3 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.6 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z: 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 116.57 | P13:345-34-115:OTP:AUTO-SINGLE:ALEXMRES3:ALEXMRES9:ALEXMRES7:9 | External | 116.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0012 | 104.87 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.79 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0024 | 115.34 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External | 115.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.42 | 635200 RAUN 3 345 635214 NEAL 4G 24 1: 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | External | 103.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00073 | 123.2 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 123.2 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 137.36 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 137.3 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.17 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 118.24 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.89 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 127.13 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00231 | 143.31 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 143.17 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.64 | 501801 G1DOLHIL 24 500250 DOLHILL7 345 1: 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 | Internal | 107.01 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00082 | 136.18 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 136.07 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00196 | 100.84 | P12:345:AMMO::LOOSECREEK:MARIOSADELTA:1 | External | 100.75 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 128.09 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 128.04 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00057 | 109.34 | 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1: 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1 | External | 109.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00849 | 134.35 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 134.2 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.26 | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997758 EASTOWNE11 161 11 541400 EASTOWN7 345 997765 EASTOWNE11 161 11 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | External | 109.15 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 141.39 | P23:345:ALTW:MITCHLCO:1150 | External | 141.27 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 121.78 | Base Case | External | 121.78 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.31 | 630771 SUTHL CT1 13.5 631004 M-TOWN 7 115 1: 630771 SUTHL CT1 13.5 631004 M-TOWN 7 115 1 | External | 135.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 149.76 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:SQUARED7:1 | External | 149.74 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.38 | 92415: 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541165 S.HARP#1 13.8 541341 S.HARP 5 161 1 541167 S.HARP#3 13.8 541341 S.HARP 5 161 1 541166 S.HARP#2 13.8 541341 S.HARP 5 161 1 | External | 102.33 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 109.19 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 109.17 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00396 | 105.52 | 300249 2FAIRPT 69 300076 5FAIRPT 161 2: 300249 2FAIRPT 69.0 300076 5FAIRPT 161 2 | External | 105.41 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06918 | 106.72 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | Internal | 105.31 | 1.41
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01308 | 129.01 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 128.76 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05904 | 104.58 | 7800: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | Internal | 103.19 | 1.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.28 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z: 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | External | 110.21 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 103.4 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 103.34 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 130.83 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 130.72 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 115.39 | P23:345:XEL:8S23 WLM | External | 115.3 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00565 | 105.69 | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.33 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 101.27 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.64 | P11:16:EES-EAI:MAGNET:1 | External | 100.54 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 120.88 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 120.84 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00391 | 106.08 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 105.92 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.95 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | Internal | 107.37 | 1.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0001 | 134.93 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 135.06 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.0003 | 115.88 | 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1: 300044 7MCCRED 345 345088 7MCCREDIE 345 Z1 | External | 115.95 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01377 | 128.78 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 128.62 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00047 | 141.13 | 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1: 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 | External | 141.1 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01034 | 122.71 | P23:345:ALTW:MITCHLCO:1140 | External | 122.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00045 | 127.79 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 127.8 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.33 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 117.28 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00141 | 131.18 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 130.29 | 0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.48 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 100.33 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.8 | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00117 | 118.84 | 620327 HANKSON4 230 620363 FORMAN 4 230 1: 620327 HANKSON4 230 620363 FORMAN 4 230 1 | External | 118.72 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00203 | 108.86 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 108.8 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 127.58 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 127.46 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00131 | 111.16 | P13:161-69:ITCM:HAYWD#15 T1:MN | External | 111.06 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00208 | 105.97 | 104518: 541201 SIBLEY 7 345 997774 SIBLEY11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 997781 SIBLEY11 161 11 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | External | 105.84 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00115 | 108.15 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.64 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | External | 123.64 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01096 | 111.86 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 111.77 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 113.33 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | External | 113.31 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.22 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 116.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 110.78 | 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1: 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1 | External | 110.7 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00092 | 139.29 | P23:345:AMIL::HERLEMAN:3 | External | 139.19 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 121.02 | Base Case | External | 121 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06949 | 117.4 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 115.84 | 1.56
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.8 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.81 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 143.01 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 142.96 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00056 | 136.84 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 136.66 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01334 | 131.59 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 131.45 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0002 | 130.07 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 129.82 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00583 | 115.8 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 115.73 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 128.11 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 128.02 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01326 | 123.98 | P23:345-161:XEL:ADAMS_I:681_S | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01225 | 129.9 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 129.85 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00171 | 134.55 | P12:161:CBPC:HOPE-WEBSTER:1 | External | 134.44 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.42 | P11:345:AMMO::LABADIE:3 | External | 124.29 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.1 | P22:345:AEP-CLEC::DOLHILL7:BUS | Internal | 106.68 | 1.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00424 | 105.51 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 105.43 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00306 | 104.31 | 84316: 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541235 DUNCAN 5 161 541250 SIBLEYPL 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 541151 SIBLEY#3 22.0 541250 SIBLEYPL 161 1 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 2 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 3 541250 SIBLEYPL 161 541346 RTCHFLD5 161 1 | External | 104.21 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 5e-05 | 145.46 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 145.34 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05861 | 102.34 | 82900: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 101.05 | 1.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00204 | 109.43 | P13:161:MEC:NORWALK 9T1 | External | 109.32 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00305 | 102.57 | P12:345:AMMO::BLAND:FRANKS:3 | External | 102.51 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 109.64 | P12:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 109.58 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15838 | 136.7 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 135.6 | 1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 132.26 | 84410: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 132.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00097 | 118.66 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 118.64 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 105.71 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 105.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00143 | 108.16 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 108.08 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 114.05 | 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1: 637067 DIAM TR WIND 345 637065 J530 COL 34.5 1 | External | 113.99 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18191 | 153 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 151.77 | 1.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00774 | 117.47 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 117.37 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00998 | 112.95 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 112.87 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00117 | 118.84 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1 | External | 118.72 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997576 345-161 161 2 | 500 | 500 | 0.00041 | 109.42 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00161 | 111.44 | 300097 5MARYVL 161 300104 5NODWAY 161 1: 300097 5MARYVL 161 300104 5NODWAY 161 1 | External | 111.25 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 129.25 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 129.11 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.67 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 103.67 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 121.02 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 120.97 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.59 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1 | External | 115.51 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00011 | 109.29 | 93779: 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 588210 GEN-2016-130 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659105 LELAND_O-BE3 345 659111 LELAND_2-BEG 20.0 1 659105 LELAND_O-BE3 345 997099 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997098 LOS KV2A 230 1 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 997106 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997105 LOS KV2A 230 1 659105 LELAND_O-BE3 345 997097 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997096 LOS KV2A 230 1 | External | 109.21 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 136.63 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 136.49 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00152 | 128.78 | 636001 WEBSTER5 161 656369 WEBSTER8 69 1: 636001 WEBSTER5 161 656369 WEBSTER8 69.0 1 | External | 128.69 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.23 | 344884 7LABADIE1 345 344894 1LAB G1 20 1: 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 136.08 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 135.94 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.26 | 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1: 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.26 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 122.64 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 122.63 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 109.62 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 109.6 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0006 | 123.71 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 123.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 111.26 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 111.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.67 | 501813 G3MADISN 22 500770 RODEMR 6 230 1: 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | Internal | 106.13 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0021 | 101.31 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 101.24 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.14 | P13:138-24:AEPW:TURK 4 | External | 125.04 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 105.16 | Base Case | Internal | 104.12 | 1.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00421 | 105.11 | P24:345:GRDA:GRDA CB400T | External | 105.08 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00183 | 122.28 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 122.23 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00024 | 101.5 | 300591 2BIG CK 69 300059 5BIG CK 161 1: 300591 2BIG CK 69.0 300059 5BIG CK 161 1 | External | 100.68 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00128 | 102.88 | 631008 WELSBRG5 161 656301 WELSBRG G 69 1: 631008 WELSBRG5 161 656301 WELSBRG G 69.0 1 | External | 102.79 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00161 | 128.65 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 128.52 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.28 | P13:13-13-161:XEL:AUTO-SINGLE:WHT53G:WHT54G:WHT145:2 | External | 132.3 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 147.34 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 147.24 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00097 | 107.91 | P23:345:MEC:OAK GROVE 901 | External | 107.83 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.1 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 105.09 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.71 | P23:345:MEC:TIFFIN 944 | External | 121.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00131 | 105.49 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 106.55 | P11:138:AMMO::SIOUX:1 | External | 106.43 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00068 | 130.02 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 129.94 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.04 | P11:24:AEPW:TURKCOAL | External | 124.95 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06949 | 117.43 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 115.76 | 1.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 2e-05 | 118.04 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 118 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.49 | 337413 8STERLING2% 500 337434 8OUACHITA% 500 1: 337413 8STERLING2% 500 337434 8OUACHITA% 500 1 | External | 116.48 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.17 | P12:HV:EES::FLINTCR5:1 | External | 105.09 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01446 | 124.74 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.39 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 111.32 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0009 | 127.02 | P12:161:UMZ:# 5519 #: IN . PROPER N-1 (LINE) FOR 636230-656207-1 | External | 126.91 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.78 | P13:138-24:AEPW:PIRKEY 4 | External | 124.7 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 102.04 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 101.97 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.38 | P11:26:EES:NINEMI:1(1) | External | 109.31 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 120.25 | P23:345:ALTW:MITCHLCO:1150 | External | 120.05 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0028 | 109.14 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | External | 109.05 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.28 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 153.06 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.67 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 115.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.47 | P21:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.46 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.34 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.34 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 123.99 | P11:138:AMMO::SIOUX:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.99 | P12:345:AMIL::7AUDRAIN:7SPENCER: Z | External | 125.04 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18191 | 149.26 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 148.16 | 1.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 314 | 314 | 0.00102 | 109.81 | P23:345:MEC:OAK GROVE 901 | External | 109.75 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.71 | P11:13:OTP:AUTO-SINGLE:HOOTLK3G:3 | External | 115.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00027 | 142.35 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 142.28 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.22 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 124.2 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0002 | 132.77 | 620314 BIGSTON4 230 620325 BROWNSV4 230 1: 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | External | 132.64 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.7 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1 | External | 113.61 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 156.59 | P23:345:ALTW:MITCHLCO:1160 | External | 156.39 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.12 | P11:HV:EES::TURKCOAL:1 | External | 125.01 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.57 | 631155 CRYSTLK5 161 631220 CLKREACT5 161 1: 631155 CRYSTLK5 161 631220 CLKREACT5 161 1 | External | 125.58 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.00027 | 106.56 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 106.33 | 0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00443 | 107.14 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 106.97 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 140.74 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 140.72 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00577 | 115.06 | 84363: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 542969 STILWEL5 161 542994 HICKMAN5 161 1 542969 STILWEL5 161 543050 ANTIOCH5 161 1 542969 STILWEL5 161 543053 REDEL 5 161 1 542969 STILWEL5 161 543057 BUCYRUS5 161 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 542969 STILWEL5 161 997752 STILWELL11 161 11 542969 STILWEL5 161 997751 STILWELL22 161 22 542969 STILWEL5 161 997759 STILWELL11 161 11 542969 STILWEL5 161 997758 STILWELL22 161 22 542969 STILWEL5 161 997755 STILWELL11 161 11 542969 STILWEL5 161 997754 STILWELL22 161 22 | External | 114.91 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.69 | P42:345:OKGE:SB_BOER7384 | Internal | 106.48 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.04 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 103.03 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00059 | 113.89 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 113.99 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 124.89 | P23:345:MEC:LOUISA 954 | External | 124.85 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 151.51 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:M-TOWN5:1 | External | 151.43 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00191 | 100.32 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 100.3 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.61 | P11:0:GRE:AUTO-SINGLE:WAPSIGEN:W | External | 135.73 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 118.96 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 118.9 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00336 | 114.15 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 114.07 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.88 | P11:345:MEC:GDMEC ST | External | 103.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06968 | 121.07 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6 | Internal | 119.44 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00177 | 102.46 | P23:345:ALTW:MITCHLCO:1160 | External | 102.4 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01088 | 118.36 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 118.25 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00135 | 101.86 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External | 101.75 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00098 | 116.32 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 116.28 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 132.27 | Base Case | External | 132.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00198 | 124.25 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 124.12 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 103.66 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 103.6 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.12 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1: 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | External | 109.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.91 | P23:345:XEL:8N17 SHC | External | 114.91 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00267 | 119.26 | P22:345:MEC:SUB 92 | External | 119.21 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.71 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Internal | 106.14 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.69 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | External | 110.59 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.13 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 100.07 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.14 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 112.22 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00547 | 119.2 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 119.01 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 136.27 | P12:345:AMIL-MEC::OAKGROVE:SANDBURG:1 | External | 136.12 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.97 | P11:20:AMMO:1LAB G2:2 | External | 104.87 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01151 | 113 | P23:345:MEC:KOSSUTH 904 | External | 112.88 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00204 | 110.42 | P22:345:AMMO::LABADIE:3 | External | 110.39 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 128.25 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 128.26 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.46 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00112 | 103.81 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 103.75 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.5 | P11:24:AEPW:PIRKEY 1 | External | 110.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.39 | P23:345:MEC:CBEC 905 | External | 111.32 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 138.3 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 138.21 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.89 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 127.13 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 111.13 | P13:69-161:ALTW:AUTO-SINGLE:PARNEL8:PARNEL5:1 | External | 111.1 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.12 | 501813 G3MADISN 22 500770 RODEMR 6 230 1: 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 109.09 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 107.04 | P12:161:ALTW:AUTO-SINGLE:MTVERN5:WYOMING5:1 | External | 106.99 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 105.14 | 92234: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 | External | 105.05 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 130.5 | 105813: 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 652509 FTRANDL4 230 652526 UTICAJC4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 652509 FTRANDL4 230 652510 FTRANDL7 115 1 652509 FTRANDL4 230 652510 FTRANDL7 115 2 652509 FTRANDL4 230 652547 FTRDL34G 13.8 1 652509 FTRANDL4 230 652548 FTRDL56G 13.8 1 652509 FTRANDL4 230 652549 FTRDL78G 13.8 1 652501 ARMOUR 7 115 652510 FTRANDL7 115 1 652501 ARMOUR 7 115 652518 MTVERN 7 115 1 652246 ARMOUR 9 34.5 652501 ARMOUR 7 115 1 652249 ARMOUR 8 69.0 652501 ARMOUR 7 115 1 640349 SPENCER7 115 652510 FTRANDL7 115 1 652475 BONESTL7 115 652510 FTRANDL7 115 1 652510 FTRANDL7 115 655490 WHTSWAN-ER7 115 1 652510 FTRANDL7 115 652546 FTRDL12G 13.8 1 652475 BONESTL7 115 652478 GREGORY7 115 1 652525 TYNDALL7 115 655490 WHTSWAN-ER7 115 1 652525 TYNDALL7 115 660006 YKNTJCT7 115 1 652525 TYNDALL7 115 652286 TYNDALL8 69.0 1 | External | 130.45 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 108.58 | 344001 5ADAIR2 161 631112 APANOSE5 161 1: 344001 5ADAIR2 161 631112 APANOSE5 161 1 | External | 108.54 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01067 | 116.59 | P23:345:MEC:LOUISA 964 | External | 116.55 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 140.53 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 140.49 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00144 | 103.34 | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | External | 103.43 | -0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0018 | 121.75 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 121.69 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.26 | 620314 BIGSTON4 230 3WXFMR BSP 230 1: 620314 BIGSTON4 230 997504 BSP 230 115 1 620316 BIGSTON9 13.8 997504 BSP 230 115 1 620314 BIGSTON4 230 997512 BSP 230 115 1 620316 BIGSTON9 13.8 997512 BSP 230 115 1 620314 BIGSTON4 230 997505 BSP 230 115 1 620316 BIGSTON9 13.8 997505 BSP 230 115 1 | External | 111.18 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00113 | 111.64 | P42:345:OPPD-MEC:S3451-RAUN&T4 | External | 111.56 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00466 | 108.17 | 104570: 301342 5BUTLER 161 541208 NEVADA 5 161 1 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 108.11 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.14 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1: 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1 | External | 109.13 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 149.77 | P12:115:ITCM:STON PT7-PRAR CK7:IA-EC | External | 149.75 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.17 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 118.24 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 107.81 | P23:345:MEC:OAK GROVE 901 | External | 107.76 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.19 | P11:13:GRE:AUTO-SINGLE:GRE-PVS53G:3 | External | 135.32 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00034 | 115.32 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 115.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.7 | P22:345:OPPD:S3458 NEBCTY1G | External | 117.71 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.54 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 117.55 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 177.73 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 177.72 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 114.05 | 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2: 637067 DIAM TR WIND 345 637066 J530 COL2 34.5 2 | External | 113.99 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.76 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 117.76 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.52 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 110.5 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 105.71 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 105.53 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.35 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.4 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 110.37 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.74 | P23:345:MEC:CBEC 905 | External | 108.65 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.89 | P23:500:EAI:NBF_SAN SOUC | External | 123.86 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01091 | 116.84 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 116.68 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00011 | 106.33 | 93779: 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z 560074 G16-017-TAP 345 659424 LO.LS-FT-BE3 345 1 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 588210 GEN-2016-130 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659105 LELAND_O-BE3 345 659111 LELAND_2-BEG 20.0 1 659105 LELAND_O-BE3 345 997099 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997098 LOS KV2A 230 1 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 997106 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997105 LOS KV2A 230 1 659105 LELAND_O-BE3 345 997097 LOS KU1A 230 1 659105 LELAND_O-BE3 345 997096 LOS KV2A 230 1 | External | 106.23 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00321 | 110.53 | 300090 5KINGDM 161 300043 7KINGDM 345 1: 300090 5KINGDM 161 300043 7KINGDM 345 1 | External | 110.45 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00117 | 120.42 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1 | External | 120.3 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 134.66 | P11:HV:EES::PIRKEY 1:1 | External | 134.6 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00206 | 112.55 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 112.48 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00148 | 126.56 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 126.27 | 0.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01022 | 113.63 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 113.6 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 102.51 | 300041 7FRANKS 345 344327 7LOOSECRK 345 1: 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | External | 101.68 | 0.83
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0043 | 106.61 | 345408 7OVERTON 345 345409 5OVERTON 161 1: 345408 7OVERTON 345 345409 5OVERTON 161 1 | External | 106.48 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00224 | 101.72 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 101.88 | -0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06907 | 117.5 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 115.86 | 1.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 111.46 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | External | 111.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.8 | P11:16:EES-EAI:MAGNET:1 | External | 104.73 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.09 | P11:22:CLEC::G3MADISN:1 | Internal | 106.45 | 1.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 137.36 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 137.3 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 4e-05 | 101.26 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 101.28 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00159 | 101.46 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 101.47 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.58 | P23:345:MEC:TIFFIN 944 | External | 117.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.12 | 657713 TRFALLS7 115 3WXFMR TRF 1: 657713 TRFALLS7 115 997125 TRF 69.0 1 657910 TRFALLS8 69.0 997125 TRF 69.0 1 657767 TRFALLS9 13.2 997125 TRF 69.0 1 657713 TRFALLS7 115 997132 TRF 69.0 1 657910 TRFALLS8 69.0 997132 TRF 69.0 1 657767 TRFALLS9 13.2 997132 TRF 69.0 1 657713 TRFALLS7 115 997123 TRF 69.0 1 657910 TRFALLS8 69.0 997123 TRF 69.0 1 657767 TRFALLS9 13.2 997123 TRF 69.0 1 | External | 111.1 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.17 | P13:161-22:AEPW:FLINTCR5 | External | 105.09 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.5 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 118.41 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.58 | P12:345:MEC:TIFFIN 9T1 SPS | External | 117.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 114.73 | P11:34:ALTW:AUTO-SINGLE:G798_WF9:1 | External | 114.72 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.83 | 631155 CRYSTLK5 161 631220 CLKREACT5 161 1: 631155 CRYSTLK5 161 631220 CLKREACT5 161 1 | External | 100.84 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.54 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 117.55 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00158 | 152.69 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 152.39 | 0.3
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.59 | P11:18:ALTW:AUTO-SINGLE:MGSST1:1S | External | 101.6 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 125.34 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 125.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.95 | P11:HV:EES::TURKCOAL:1 | External | 116.9 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.18 | P12:HV:EES::TURK 4%:1(1) | Internal | 105.7 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01207 | 137.98 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 137.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 103.94 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 103.89 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.37 | 300001 1THLG1 20 300120 5THMHILB1 161 1: 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 107.28 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00235 | 110.03 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 109.91 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0035 | 102.13 | 104177: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 102.04 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.0016 | 120.56 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 120.53 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01093 | 117.96 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 117.89 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00541 | 116.28 | P22:345:AMMO::OVERTON:1 | External | 116.34 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 111.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External | 111.11 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.39 | 92432: 541154 RGREEN#3 13.2 541279 RGREEN 2 69.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.32 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.59 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | External | 114.48 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.1 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | External | 135.11 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00083 | 104.63 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 104.59 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.96 | 81778: 509852 T.NO.--7 345 512865 GREC TAP5 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | Internal | 105.42 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00014 | 110.21 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 110.13 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00032 | 102.37 | P23:345:ALTW:MITCHLCO:1150 | External | 102.21 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00032 | 102.05 | P23:345:ALTW:MITCHLCO:1140 | External | 101.88 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0022 | 106.16 | 635635 MADISON3 345 635640 NORWLK3 345 1: 635635 MADISON3 345 635640 NORWLK3 345 1 | External | 106.13 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.42 | P11:20:AMMO:1LAB G2:2 | External | 124.32 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 115.25 | P12:115:OTP:AUTO-SINGLE:GRE-GRACEV7:DUMONT7:1 | External | 115.22 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.1 | P12:EHV:EES::WELSH 7:1(1) | External | 108.05 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00436 | 121.26 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External | 121.17 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01116 | 112.96 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 112.89 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00097 | 112.31 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 112.29 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 102.44 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | External | 102.4 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00321 | 100.8 | P12:500:EES:ND:8MT_OLIVE%:LAYFLD8:1 | External | 100.77 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00134 | 129.89 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 129.65 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07022 | 114.99 | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Internal | 113.39 | 1.6
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.91 | P11:HV:EES::PIRKEY 1:1 | External | 108.8 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 114.83 | Base Case | External | 114.82 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.00109 | 111.6 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 111.56 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00091 | 128.18 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 128.09 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00216 | 103.96 | P13:161-34:CIPCO:GU CTR T1:IA-SW | External | 103.87 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01079 | 111.19 | P23:345-161:XEL:ADAMS_I:681_S | External | 111.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01022 | 120.69 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 120.62 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00102 | 116.24 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 116.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.78 | 631081 M-TOWN 5 161 629216 MGS ST1 18 1: 631081 M-TOWN 5 161 629216 MGS ST1 18.0 1 | External | 109.79 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 125.34 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 125.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00547 | 119.09 | P22:345:AMMO::OVERTON:1 | External | 119.06 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 108.71 | Base Case | External | 108.74 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 152.03 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00257 | 116.87 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 117.04 | -0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 115.94 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 115.9 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 103.68 | 672621 SHAND 4 230 672321 SHAND 1G 18 1: 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | External | 103.73 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00231 | 143.45 | P23:345:MEC:KOSSUTH 904 | External | 143.27 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.92 | P12:HV:EES::PIRKEY 4:1 | External | 116.85 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 133.3 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 133.29 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 108.41 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 108.4 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 114.7 | P23:345:ALTW:MITCHLCO:1140 | External | 114.68 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0103 | 114.41 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 114.33 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0114 | 121.43 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 121.26 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.26 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 114.18 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 114.15 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00672 | 108.57 | P12:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 108.53 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 131.62 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External | 131.5 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 107.92 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.86 | 601087 STEEP BK LK3 345 601088 BLZNG STR1 3 345 1: 601087 STEEP BK LK3 345 601088 BLZNG STR1 3 345 1 | External | 127.1 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0009 | 127.02 | 105985: 656191 HAMPTON5 161 656207 HAMPTONTAP5 161 1 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 636230 FRANKLN5 161 656207 HAMPTONTAP5 161 1 | External | 126.91 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 116.76 | P23:345:ALTW:MITCHLCO:1130 | External | 116.64 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00089 | 127.25 | P12:161:CBPC-MEC:SHEFFIELD-HAMPTONTAP-FRANKLIN:1 | External | 127.12 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00289 | 101.47 | P12:138:AMMO::BLAND:OSAGE:6030 | External | 101.39 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01116 | 111.42 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 111.39 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.95 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | Internal | 104.88 | 2.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 115.17 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.04 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00018 | 144.35 | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | External | 144.35 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00044 | 102.22 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 102.02 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.7 | P23:345:OPPD:S3458 NEBCTY1G | External | 117.71 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.28 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.27 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 144.18 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 144.16 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 116.98 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 116.9 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00069 | 121.74 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 121.63 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00035 | 115.04 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 115.02 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0018 | 121.73 | P23:345:ATC:NORTHMADISON:6033-S | External | 121.67 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 121.5 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 121.45 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00035 | 119.61 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 118.84 | 0.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 109.06 | P23:345:AMIL::HERLEMAN:1 | External | 109.04 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00144 | 126.52 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External | 126.41 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 114.39 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 114.36 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00672 | 108.57 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 108.53 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00183 | 122.28 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 122.23 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.83 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | External | 100.84 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00145 | 106.21 | 631046 ADAMS 5 161 631154 BARTON5 161 1: 631046 ADAMS 5 161 631154 BARTON5 161 1 | External | 106.17 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.79 | 337413 8STERLING2% 500 337434 8OUACHITA% 500 1: 337413 8STERLING2% 500 337434 8OUACHITA% 500 1 | External | 104.73 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00133 | 109.74 | P23:345:AMIL::HERLEMAN:3 | External | 109.61 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00062 | 149.58 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 149.51 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00226 | 111.28 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 111.27 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 137.38 | P23:345:ATC:NORTHMADISON:6037-S | External | 137.31 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00054 | 144.64 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 144.57 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 130.35 | P23:345:ATC:NORTHMADISON:6037-S | External | 130.26 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00024 | 185.9 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 185.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00045 | 119.43 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 119.3 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | P11:HV:EES::FLINTCR1:1 | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00576 | 115.18 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 115.04 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00312 | 100.33 | P22:345:AMMO::LABADIE:3 | External | 100.22 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 139.94 | P23:345-161:XEL:ADAMS_I:680_S | External | 139.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 146.15 | P12:161:DPC:AUTO-SINGLE:WABACO5:ALMA5:1 | External | 146.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00155 | 103.86 | P12:161:CBPC:HOPE-WEBSTER:1 | External | 103.75 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00054 | 101.24 | P23:345:XEL:8S50 HMP | External | 101.25 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.49 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | External | 116.48 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00054 | 122.46 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 121.86 | 0.6
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00214 | 117.65 | P23:345:MEC:KOSSUTH 904 | External | 117.48 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 4e-05 | 110.72 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.72 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 120.65 | P23:345:ALTW:MITCHLCO:1160 | External | 120.36 | 0.29
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00021 | 112.05 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 112.06 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00776 | 115.46 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 115.44 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00039 | 126.76 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 126.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 114.77 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 114.73 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00109 | 141.19 | P12:161:CBPC-MEC:SHEFFIELD-HAMPTONTAP-FRANKLIN:1 | External | 141.04 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01082 | 116.92 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 116.83 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00225 | 100.53 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 100.18 | 0.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00016 | 110.71 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 110.69 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 105.14 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.05 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 140.23 | P12:161:ALTW:AUTO-SINGLE:VINTON5:ARNOLD5:1 | External | 140.15 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 103.11 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 103.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 110.83 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 110.8 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.86 | P23:345:ALTW:MITCHLCO:1150 | External | 153.61 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.48 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 106.47 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.13 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 109.12 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00024 | 135.43 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 135.33 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 140.61 | P23:345:ALTW:MITCHLCO:1130 | External | 140.5 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.23 | 104522: 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 101.36 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 120.96 | P12:161:MEC:AUTO-SINGLE:SB185:SB1125:1 | External | 120.85 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0006 | 143.23 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 143.17 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 115.59 | 84404: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 | External | 115.61 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.64 | P11:HV:EES::1GOXY U1!:1 | Internal | 106.99 | 1.65
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01088 | 114.98 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 114.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 118.61 | P23:345:ALTW:MITCHLCO:1130 | External | 118.44 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 138.86 | 631017 PRAR CK7 115 629066 PR CRK4G 18 1: 631017 PRAR CK7 115 629066 PR CRK4G 18.0 1 | External | 138.81 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 139.32 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 139.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00021 | 107.1 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:DENMARK5:1 | External | 107.1 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00548 | 119.45 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 119.25 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 109.37 | P12:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 109.32 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01088 | 123.41 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.31 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00048 | 356.52 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 356.4 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 120.44 | Base Case | External | 120.43 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00321 | 100.8 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | External | 100.77 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00058 | 101.4 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 101.35 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.08 | 80247: 500250 DOLHILL7 345 507760 SW SHV 7 345 1 500260 DOLHILL6 230 500250 DOLHILL7 345 1 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 500140 CARROLL6 230 500260 DOLHILL6 230 1 500255 REDBAYOU_6 230 500260 DOLHILL6 230 1 | Internal | 106.65 | 1.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.99 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External | 125.04 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 118.09 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 118.09 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06908 | 109.25 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | Internal | 107.77 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 119.66 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 119.58 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 110.11 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 110.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 135.13 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 135.15 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.31 | 848401: 541256 IND PRK5 161 541401 EASTOWN5 161 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | External | 109.16 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00063 | 118.7 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 118.71 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 105.18 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 104.94 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 100.88 | P23:345:ITCM:SALEM 3 2835:IA-NE | External | 100.84 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.22 | P12:345:MEC:TIFFIN-ARNOLD | External | 116.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00062 | 149.56 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 149.49 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 103.46 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.46 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.16 | P23:345:GRE:CHL 304JB21 | External | 116.09 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997576 345-161 161 2 | 500 | 500 | 0.00041 | 111.94 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 111.92 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 115.96 | P13:345:XEL:BLL TR 9 | External | 115.88 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00175 | 103.91 | P22:345:XEL:ADAMS 3 N1:MN | External | 103.76 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 131.38 | P13:161-69:ITCM:CARBIDE5 T1:IA-EC | External | 131.28 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01076 | 113.56 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 113.47 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0002 | 132.18 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 132.08 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.51 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT | External | 110.46 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 100.32 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.29 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 103.73 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 103.77 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00074 | 112.62 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 112.24 | 0.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.46 | P23:345:GRE:CHL 304JB22 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 107.95 | 105823: 652515 HURON 7 115 660009 BTAP WP7 115 1 660003 HURONWP7 115 660009 BTAP WP7 115 1 660009 BTAP WP7 115 660040 DAKOTACCESS7 115 1 652515 HURON 7 115 652528 WOONSKT7 115 1 652515 HURON 7 115 655481 REDFELD-ER7 115 1 652515 HURON 7 115 660003 HURONWP7 115 1 652284 HURON 8 69.0 652515 HURON 7 115 1 652515 HURON 7 115 997158 HU KV1A 115 1 652515 HURON 7 115 997157 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 1 652507 FTTHOMP4 230 652514 HURON 4 230 2 652514 HURON 4 230 652530 WATERTN4 230 2 652514 HURON 4 230 652614 CARPENTER 4 230 1 652514 HURON 4 230 659205 BROADLND-BE4 230 1 652514 HURON 4 230 997158 HU KV1A 115 1 652514 HURON 4 230 997157 HU KV1B 115 2 652528 WOONSKT7 115 659123 STORLA__-BE7 115 1 652528 WOONSKT7 115 655355 WOONSKT-ER8 69.0 2 652284 HURON 8 69.0 655063 SW341-ER8 69.0 1 652284 HURON 8 69.0 655066 SW352-ER8 69.0 1 652284 HURON 8 69.0 655067 SW353-ER8 69.0 1 652282 HURON429 13.3 997157 HU KV1B 115 2 652281 HURON419 13.3 997158 HU KV1A 115 1 652515 HURON 7 115 997165 HU KV1A 115 1 652515 HURON 7 115 997164 HU KV1B 115 2 589324 G17-094-TAP 230 652514 HURON 4 230 2 652514 HURON 4 230 997165 HU KV1A 115 1 652514 HURON 4 230 997164 HU KV1B 115 2 652282 HURON429 13.3 997164 HU KV1B 115 2 652281 HURON419 13.3 997165 HU KV1A 115 1 652515 HURON 7 115 997156 HU KV1A 115 1 652515 HURON 7 115 997155 HU KV1B 115 2 652514 HURON 4 230 997156 HU KV1A 115 1 652514 HURON 4 230 997155 HU KV1B 115 2 652282 HURON429 13.3 997155 HU KV1B 115 2 652281 HURON419 13.3 997156 HU KV1A 115 1 | External | 108.1 | -0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06909 | 116.33 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 114.76 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00041 | 110.61 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 110.43 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.16061 | 101.11 | P12:115:MKEC:SAINTJOHN-SAINTJOHN(MIDWEST):: | Internal | 100.12 | 0.99
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00994 | 117.31 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 117.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00113 | 111.64 | P45:345:OPPD:S3451-RAUN&T4 | External | 111.56 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 127.34 | P23:345:MEC:HILLS 9114 | External | 127.24 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01034 | 122.76 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 122.66 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00034 | 112.36 | P23:345:MEC:LOUISA 924 | External | 112.3 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.55 | P23:345:OPPD:S3458 NEBCTY1G | External | 129.55 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.44 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 109.37 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.75 | 344011 7HUGHES 345 344012 7HPW-N 345 1: 344011 7HUGHES 345 344012 7HPW-N 345 1 | External | 103.72 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.38 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 100.28 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00145 | 101.58 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 101.51 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00547 | 119.2 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 119.01 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.67 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 110.65 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 125.98 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 126.23 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.86 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 127.1 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00295 | 102.44 | 104212: 542972 HAWTH 7 345 997748 HAWTHORN22 161 22 542972 HAWTH 7 345 997749 HAWTHORN20 161 20 542972 HAWTH 7 345 997755 HAWTHORN22 161 22 542972 HAWTH 7 345 997756 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | External | 102.38 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.64 | P11:345-24:CLEC::DOLHILL7:1 | Internal | 107.01 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00849 | 134.35 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 134.2 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06916 | 109 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal | 106.72 | 2.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.7 | P23:EHV:EES::8STERLING2%:9 | Internal | 106.14 | 1.56
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.1 | P23:345:AMMO::ZACHARY:2 | External | 105.09 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00082 | 145.34 | 69843: 348948 5SANDBURG 161 348949 MERCER5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 145.22 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00224 | 101.72 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 101.88 | -0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.55 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.56 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 109.53 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 109.51 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.74 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.75 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 118.09 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1 | External | 118.09 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00044 | 126.36 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 126.34 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.79 | P13:345,24:CLEC::G1DOLHILL::1 | External | 100.66 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.43 | P12:HV:EES::TURK 4%:1(1) | External | 100.36 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.59 | P11:18:ALTW:AUTO-SINGLE:MGSCT2:2C | External | 109.61 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 560 | 700 | 0.00328 | 106.32 | P23:345:MEC:SYCAMORE 905 | External | 106.28 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00062 | 165.09 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 165.01 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00063 | 124.07 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 123.96 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.36 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1: 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Internal | 104.88 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.0012 | 104.87 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 104.79 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 111.08 | P11:230-22-18:EES:HOOKER_E | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.27 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 112.27 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01334 | 131.59 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 131.45 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.05 | P22:345:AMMO::LABADIE:4 | External | 106.94 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.01 | P13:13-161:ALTW:AUTO-SINGLE:SUTHLCT3:M-TOWN5:1 | External | 117.01 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 8e-05 | 108.39 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 108.29 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.59 | 80247: 500250 DOLHILL7 345 507760 SW SHV 7 345 1 500260 DOLHILL6 230 500250 DOLHILL7 345 1 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 500140 CARROLL6 230 500260 DOLHILL6 230 1 500255 REDBAYOU_6 230 500260 DOLHILL6 230 1 | External | 100.55 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 9e-05 | 105.29 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External | 105.3 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 2e-05 | 101.4 | P12:HV:EES::6WILLOW_GL%:6PECUE:1 | External | 101.4 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00994 | 117.1 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 117.08 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.5 | P11:HV:EES::PIRKEY 1:1 | External | 110.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01056 | 110.52 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 110.49 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.5 | P11:24:CLEC::G1DOLHIL:1 | External | 116.51 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.52 | 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23 1: 338188 8SANS SOUCI% 500 338388 1PLUM PT U1 23.0 1 | External | 123.51 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.69 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 122.66 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00162 | 121.45 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 121.34 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00118 | 103.24 | P23:345:OPPD:S3451-RAUN&T4 | External | 103.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.0038 | 112.5 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.3 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 126.03 | P13:18-115:ALTW:AUTO-SINGLE:PRCRK4G:PRARCK7:1 | External | 125.99 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 4e-05 | 101.26 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.28 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00419 | 104.77 | P12:345:AMMO::AUDRAIN:SPS:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00215 | 112.04 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 111.99 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 117.81 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 117.76 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.43 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2 | External | 134.56 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.76 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 117.76 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05904 | 104.58 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6 | Internal | 103.19 | 1.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.93 | P11:HV:EES::1GYP_U4 G1:1 | External | 116.93 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06909 | 116.33 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 114.76 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00158 | 162.89 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 161.95 | 0.94
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 137.75 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 137.7 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01184 | 125.25 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 125.18 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303029 8XFMRINT1 500 303031 1G1INTHB 18.0 1 | 180 | 180 | 0.00059 | 103.7 | P11:HV:EES::G1 ACAD!:1 | External | 103.69 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 102.44 | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | External | 102.4 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 107.98 | P23:345:AMMO::SPENCERCREEK:V3 | External | 107.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15365 | 102.26 | 104269: 532782 BUFFALO7 345 532783 KINGMAN7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532782 BUFFALO7 345 539801 THISTLE7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 532782 BUFFALO7 345 587500 GEN-2016-073 345 1 | Internal | 101.24 | 1.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0109 | 117.73 | P23:345:XEL:8S22 WLM | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00453 | 108.16 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1: 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | External | 108.04 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01313 | 127.79 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 127.69 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 118.92 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 118.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 116.1 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 116.11 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15838 | 137.03 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 136.02 | 1.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 114.79 | P23:345:ALTW:MITCHLCO:1150 | External | 114.73 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00436 | 119.24 | P12:161:AECI:M:HUNTSDL:C_PERCH:1 | External | 119.15 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00192 | 115.08 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 115.15 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01295 | 125.79 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 125.56 | 0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.42 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | External | 103.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.58 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 117.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.54 | 501813 G3MADISN 22 500770 RODEMR 6 230 1: 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 110.52 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00054 | 118.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 130.68 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 130.57 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.3 | 1045301: 541400 EASTOWN7 345 997758 EASTOWNE11 161 11 541400 EASTOWN7 345 997765 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01079 | 111.07 | P23:345-161:XEL:ADAMS_I:680_S | External | 111.05 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0028 | 111.06 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External | 110.97 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18191 | 153.36 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 152.24 | 1.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.85 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 109.79 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.15 | P11:18:ITCM:EMERYGT1:1 | External | 109.17 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00203 | 108.86 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 108.8 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00028 | 175.76 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 175.74 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 140.34 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 140.33 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 112.41 | P23:345:MEC:SUB 56 934 OR 937 | External | 112.37 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.29 | 105460: 525824 TUCO_TR1 1 13.2 998064 UPDATE LATER 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 525824 TUCO_TR1 1 13.2 998071 UPDATE LATER 230 1 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 | Internal | 102.28 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01097 | 110.57 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 110.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | 106126: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 129.78 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 129.74 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01067 | 114.37 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 113.92 | 0.45
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01182 | 118.36 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 118.33 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 3e-05 | 100.19 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 100.18 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00073 | 125.13 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 125.05 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00048 | 116.54 | 82321: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 116.55 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.59 | 336250 69MILE% 230 336252 1NMIL U5! 26 1: 336250 69MILE% 230 336252 1NMIL U5! 26.0 1 | External | 110.56 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00489 | 105.91 | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | External | 105.71 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 137.61 | Base Case | External | 137.74 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.36 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.37 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00147 | 140.61 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 140.48 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.79 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 129.74 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 108.93 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 108.82 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 110.23 | P23:345:GRE:CHL 304JB22 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 130.14 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 129.95 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.22 | P13:13-13-161:XEL:AUTO-SINGLE:WHT55G:WHT56G:WHT565:1 | External | 132.16 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00217 | 109.99 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 109.9 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.77 | P11:34:ALTW:AUTO-SINGLE:G798_WF9:1 | External | 117.77 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00028 | 107.89 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.9 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00126 | 135.32 | P12:161:ALTW-MEC:AUTO-SINGLE:BNEJCT5:FT.DODG5:1 | External | 135.16 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00126 | 128.21 | P42:345:OPPD-MEC:S3451-RAUN&T4 | External | 128.13 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.71 | P23:345:MEC:TIFFIN 954 | External | 121.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01225 | 138.25 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 138.16 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 145.67 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 145.61 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00034 | 105.94 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 105.89 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00055 | 105.34 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 105.3 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01097 | 116.93 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 116.89 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.81 | P11:24:CLEC::G1DOLHIL:1 | External | 123.81 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.57 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | External | 100.48 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0018 | 121.75 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 121.69 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 110.86 | 105835: 652520 OAHE 7 115 652559 OAHE 1G 13.8 1 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652489 PIERRE 7 115 652600 ASH TAP 115 1 652520 OAHE 7 115 652600 ASH TAP 115 1 652600 ASH TAP 115 658120 GARFLD 7 115 1 652476 EAGLEBT7 115 652520 OAHE 7 115 1 652491 IRVSIMM7 115 652520 OAHE 7 115 1 652520 OAHE 7 115 997156 OA NO. 5 115 1 652520 OAHE 7 115 997155 OA NO. 6 115 1 652589 OAHE 9 13.8 997156 OA NO. 5 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652520 OAHE 7 115 997163 OA NO. 5 115 1 652520 OAHE 7 115 997162 OA NO. 6 115 1 652589 OAHE 9 13.8 997163 OA NO. 5 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 652520 OAHE 7 115 997154 OA NO. 5 115 1 652520 OAHE 7 115 997153 OA NO. 6 115 1 652589 OAHE 9 13.8 997154 OA NO. 5 115 1 | External | 110.78 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00216 | 102.2 | P23:345:AMMO::ZACHARY:2 | External | 102.12 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01198 | 128.11 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 127.96 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 2e-05 | 101.4 | 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1: 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1 | External | 101.4 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00062 | 101.05 | P12:69:GRDA:PAWNEEGR-CLEVDSTK | External | 101.03 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.17 | 335190 6NELSON% 230 335206 1NELSON_G6! 20 1: 335190 6NELSON% 230 335206 1NELSON_G6! 20.0 1 | External | 100.1 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 102.54 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 102.54 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0108 | 110.33 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 110.27 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.6 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.61 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 135.73 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.51 | P12:EHV:EES::WELSH 7:1(1) | External | 116.46 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00038 | 101.61 | P23:345:MEC:HILLS 9114 | External | 101.56 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01253 | 127.47 | P22:345:GMO-OPPD:S3458-HOLT | External | 127.31 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.44 | 85486: 640184 GENTLMN4 230 640286 N.PLATT4 230 1 640184 GENTLMN4 230 640286 N.PLATT4 230 2 640184 GENTLMN4 230 640286 N.PLATT4 230 3 640184 GENTLMN4 230 640302 OGALALA4 230 1 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640184 GENTLMN4 230 997408 GGS T1 230 1 640184 GENTLMN4 230 997407 GGS T2 230 2 640184 GENTLMN4 230 997415 GGS T1 230 1 640184 GENTLMN4 230 997414 GGS T2 230 2 | External | 130.44 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 143.52 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 143.47 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 100.19 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 100.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 106.18 | P13:34-161:MEC:AUTO-SINGLE:WALLLK9:WALLLK5:2 | External | 106.19 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 122.05 | P12:115:OTP:AUTO-SINGLE:GRE-JOHNJCT7:GRE-GRACEV7:1 | External | 122.01 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.4 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | Internal | 104.92 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00044 | 126.36 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 126.34 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 100.55 | P12:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 100.5 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 2e-05 | 116.57 | 658047 ALEXMRES3 345 3WXFMR ALEXMRES3 9: 658047 ALEXMRES3 345 997101 ALEXMRES3 115 9 658050 ALEXMRES7 115 997101 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997101 ALEXMRES3 115 9 658047 ALEXMRES3 345 997108 ALEXMRES3 115 9 658050 ALEXMRES7 115 997108 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997108 ALEXMRES3 115 9 658047 ALEXMRES3 345 997099 ALEXMRES3 115 9 658050 ALEXMRES7 115 997099 ALEXMRES3 115 9 658048 ALEXMRES9 34.5 997099 ALEXMRES3 115 9 | External | 116.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.16 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 108.14 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15917 | 132.72 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 131.64 | 1.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.85 | P23:345:MEC:CBEC 908 | External | 103.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 102.39 | P12:345:AMMO::LOOSECREEK:FRANKS:1 | External | 101.57 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00201 | 110.42 | 681532 WABACO 5 161 681537 ROCHSTR5 161 1: 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | External | 110.36 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00672 | 108.57 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 108.53 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00073 | 100.29 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 100.28 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 111.16 | P11:HV:EES::1GYP_U4 G1:1 | External | 111.12 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.49 | P23:HV-EHV:EES::8STERLING2%:4 | External | 116.48 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0011 | 113.7 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 113.66 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00177 | 102.43 | P23:345:ALTW:MITCHLCO:1150 | External | 102.33 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00064 | 153.42 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 153.34 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 560 | 700 | 0.00328 | 108.96 | P23:345:MEC:SYCAMORE 905 | External | 108.92 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00021 | 130.29 | P12:230:OTP::BIGSTON4:HANKSON4 | External | 130.18 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00055 | 130.47 | 105856: 648516 GRPR11 9 34.5 645065 GRPR11 W 0.69 1 648523 GRPR21 9 34.5 645067 GRPR21 W 0.69 1 648519 GRPR12 9 34.5 645066 GRPR12 W 0.69 1 648513 GRPR1 3 345 648520 GRPR2 3 345 1 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 648513 GRPR1 3 345 997246 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997245 GRPR1 TFMR 2 34.5 1 648526 GRPR22 9 34.5 645068 GRPR22 W 0.69 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z 652532 GR PRAIRIE 3 345 579457 G16-075XFMR1 34.5 1 648514 GRPR11X9 34.5 648516 GRPR11 9 34.5 Z1 648514 GRPR11X9 34.5 997246 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997246 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997244 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997245 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997244 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997243 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997243 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997253 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997252 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997253 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997253 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997251 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997252 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997251 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997250 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997250 GRPR2 TFMR 2 34.5 1 648513 GRPR1 3 345 997244 GRPR1 TFMR 1 34.5 1 648513 GRPR1 3 345 997243 GRPR1 TFMR 2 34.5 1 648514 GRPR11X9 34.5 997244 GRPR1 TFMR 1 34.5 1 648515 GRPR11Y9 13.8 997244 GRPR1 TFMR 1 34.5 1 648522 GRPR21Y9 13.8 997242 GRPR2 TFMR 1 34.5 1 648518 GRPR12Y9 13.8 997243 GRPR1 TFMR 2 34.5 1 648520 GRPR2 3 345 997242 GRPR2 TFMR 1 34.5 1 648520 GRPR2 3 345 997241 GRPR2 TFMR 2 34.5 1 648525 GRPR22Y9 13.8 997241 GRPR2 TFMR 2 34.5 1 | External | 130.42 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 146.62 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 146.6 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00055 | 131.52 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00035 | 119.74 | 300099 5MONTCT 161 300523 5WLMSBG 161 1: 300099 5MONTCT 161 300523 5WLMSBG 161 1 | External | 118.97 | 0.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.7 | 104499: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 106.65 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00038 | 105.6 | P23:345:MEC:WALCOTT 944 | External | 105.52 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.46 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00583 | 104.33 | P23:345:MEC:WALCOTT 914 | External | 104.29 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01075 | 116.65 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT | External | 116.6 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 110.54 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 110.36 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05862 | 101.62 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 100.27 | 1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05862 | 101.62 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 100.27 | 1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.26 | P21:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.26 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.89 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 123.86 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01088 | 118.36 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 118.25 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.62 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 117.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00024 | 122.98 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 122.89 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 117.94 | P23:345:ALTW:MITCHLCO:1160 | External | 117.84 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 150.53 | P12:161:DPC:AUTO-SINGLE:WABACO5:ROCHSTR5:1 | External | 150.46 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 144.98 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 144.85 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 127.82 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 127.76 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00102 | 126.28 | P23:345:MEC:OAK GROVE 901 | External | 126.21 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 158.76 | 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1: 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1 | External | 158.76 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 140.18 | P13:161-34:ALTW-WPS:AUTO-SINGLE:RICE5:G551_TAP:1 | External | 140.16 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.1 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 105.09 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.38 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 116.33 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00064 | 128.02 | 301422 2LEE 69 631216 WEVER5 161 1: 301422 2LEE 69.0 631216 WEVER5 161 1 | External | 128.04 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00028 | 173.26 | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1: 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | External | 173.23 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.1 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 135.22 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.8 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 104.84 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 2e-05 | 120.47 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 120.45 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.013 | 127.84 | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.64 | P11:EHV:EES::1TRACTBEL C1:1 | External | 100.54 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00436 | 119.24 | 300500 5HUNTSDL 161 343004 5PERCHE 161 1: 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | External | 119.15 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00032 | 150.09 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 149.92 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.28 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.27 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00295 | 102.44 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 | External | 102.38 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 144.55 | P23:345:ALTW:MITCHLCO:1130 | External | 144.55 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00238 | 100.75 | 104706: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 997775 P HILL 11 161 11 541200 PHILL 7 345 997782 P HILL 11 161 11 541200 PHILL 7 345 997778 P HILL 11 161 11 | External | 100.64 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.8 | P23:500:EAI:NBF_SAN SOUC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01075 | 110.5 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 110.44 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00078 | 130.56 | P12:161:MPW-MEC::SO.SUB 5:SB 18 5:1 | External | 130.44 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 120.94 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 120.85 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 105.18 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 104.94 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00011 | 104.43 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 104.42 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00419 | 105.25 | P23:345:AMMO::SPENCERCREEK:V3 | External | 105.12 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 105.14 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 105.05 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06103 | 111.92 | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | Internal | 110.57 | 1.35
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.01229 | 101.82 | 635680 BONDRNT3 345 635690 GDMEC 3 345 1: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 | External | 101.72 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00153 | 127.16 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 127.08 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.29 | P12:345:OKGE-SPS:BKRBKR430 | Internal | 102.28 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00776 | 124.82 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 124.76 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 136.27 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | External | 136.12 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.1 | 344884 7LABADIE1 345 344894 1LAB G1 20 1: 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | External | 107 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00666 | 103.72 | P23:345:MEC:OAK GROVE 901 | External | 103.68 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00189 | 111.29 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 111.32 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.47 | P11:115:XEL:AUTO-SINGLE:FIBROMN7:1 | External | 118.38 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.91 | P11:24:AEPW:TURKCOAL | External | 110.85 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00198 | 105.97 | P13:345-161:MEC:AUTO-SINGLE:NORWLK3:NORWLK5:1 | External | 105.94 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00153 | 104.07 | P12:161:MEC-WAPA:AUTO-SINGLE:WEBSTER5:HOPE5:1 | External | 103.97 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.84 | P11:22:CLEC:RODEMR1:1 | External | 123.81 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 124.82 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 124.82 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.92 | P13:138-24:AEPW:TURK 4 | External | 108.85 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 149.81 | 630139 ADAMS 8 69 631046 ADAMS 5 161 1: 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | External | 149.76 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 2e-05 | 120.47 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 120.45 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.89 | P23:500:EAI:NBF_SAN SO~1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00128 | 110.4 | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00129 | 112.41 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 112.17 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01022 | 120.69 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 120.62 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 105.07 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 105.06 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00863 | 111.89 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 111.88 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0002 | 120.58 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 120.52 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00054 | 132.64 | P23:345:MEC:OAK GROVE 904 | External | 132.68 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.27 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.28 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00115 | 108.15 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.68 | P11:23:EES-EAI:PLUM17:1 | External | 115.62 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.46 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 110.4 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00012 | 103.83 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 103.8 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 115.44 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 115.33 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06907 | 117.3 | 82900: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 115.77 | 1.53
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.07 | P23:500:EAI:NBF_SAN SOUC | External | 109.97 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.57 | P12:500:EES:STL500:OUACHI:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00238 | 117.34 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 117.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00161 | 128.03 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 127.92 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00058 | 135.07 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 135.05 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 120.76 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 120.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 123.87 | P23:345:XEL:8S23 WLM | External | 123.99 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00054 | 122.1 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.3 | P11:22:AEPW:FLINTCR1 | External | 105.25 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | External | 103.67 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 4e-05 | 136.67 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.69 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 146.15 | 681532 WABACO 5 161 681543 ALMA 5 161 1: 681532 WABACO 5 161 681543 ALMA 5 161 1 | External | 146.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 120.69 | 300003 1THLG3 24 300049 7THOMHL 345 1: 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 120.59 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 143.51 | P22:345:XEL:ADAMS 3 N1:MN | External | 143.35 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.58 | P12:345:MEC:TIFFIN-ARNOLD | External | 117.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00266 | 108.14 | 300105 5NORTON 161 543064 NORTON-5 161 Z1: 300105 5NORTON 161 543064 NORTON-5 161 Z1 | External | 108.04 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01102 | 112.25 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 112.19 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.4 | P11:18:ALTW:AUTO-SINGLE:MGSCT2:2C | External | 101.41 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00095 | 100.32 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.29 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.32 | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External | 109.18 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01321 | 127.03 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 126.89 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.001 | 139.82 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 139.68 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.94 | 603271 FARIBALT GEN 115 600050 FEP CT G 18 1: 603271 FARIBALT GEN 115 600050 FEP CT G 18.0 1 | External | 127.18 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.88 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 116.93 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00064 | 139.81 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 139.73 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 101.74 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.67 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.72 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 108.63 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 109.64 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 109.58 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00129 | 114.04 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 114.11 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 102.04 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.97 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0014 | 132.74 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 132.46 | 0.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 144.34 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 144.27 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:20:AMMO:1LAB G1:1 | External | 107.16 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00025 | 144.67 | P23:500:EMI-EES:ABF_FRKLN-A | External | 144.64 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603103 SCOTTCO7 115 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00283 | 113.56 | P23:345:XEL:8M57 SCO | External | 113.41 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00151 | 100.15 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 100.08 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.12 | P11:24:AEPW:TURKCOAL | External | 125.01 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00017 | 108.42 | P12:161:AMMO-AECI::SOUTHRIVER:ADAIR:1 | External | 108.39 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.66 | P23:345:MEC:LOUISA 954 | External | 109.58 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 130.23 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 130.19 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0041 | 109.11 | 300336 2HOLDEN 69 300124 5HOLDEN 161 1: 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | External | 108.99 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00073 | 125.13 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 125.05 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00216 | 102.2 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 102.12 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00436 | 121.26 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External | 121.17 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.32 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 135.33 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.07 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 109.97 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00592 | 107.89 | P23:345:MEC:HILLS 9114 | External | 107.86 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00339 | 100.11 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 100.03 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 144.18 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 144.16 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 102.5 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 102.47 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.0002 | 129.91 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 129.71 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 114.7 | 87486 J748GENTIE 345 87485 J748MAINTRX2 34.5 1: 87486 J748GENTIE 345 87485 J748MAINTRX2 34.5 1 | External | 114.7 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 136.09 | P23:345:ALTW:MITCHLCO:1160 | External | 135.72 | 0.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00032 | 142.95 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 142.89 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 138.58 | P23:345:MEC:OAK GROVE 904 | External | 138.37 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.83 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 124.73 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.77 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 106.77 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00037 | 212.02 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 211.98 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 116.27 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External | 116.13 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.37 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | External | 132.34 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00153 | 113.46 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 113.54 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00218 | 111.13 | P13:161-69:CIPCO:ANITA T1:IA-SW | External | 111.04 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.85 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | External | 103.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.74 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998884 HGT X2 69.0 1 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 338374 1HGT X2 13.8 998884 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 120.74 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00559 | 114.89 | 104177: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 114.78 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01077 | 115.69 | P23:345:AMMO::SPENCERCREEK:V3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00015 | 103.29 | P12:161:MEC-CFU:BLACK HAWK-UNION-BUTLER | External | 103.25 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.06 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 117.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00118 | 119.99 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 119.83 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00953 | 111.33 | P23:345:MEC:ATCHISON CO 903 | External | 111.27 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 235.56 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 235.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.00096 | 103.85 | P23:500:EMI:ABF_MCKNT-C | External | 103.85 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 132.69 | 602030 WHT 14 5 161 3WXFMR WHT 14 5 1: 602030 WHT 14 5 161 997624 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997624 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997624 WHT 14 5 13.8 1 602030 WHT 14 5 161 997631 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997631 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997631 WHT 14 5 13.8 1 602030 WHT 14 5 161 997626 WHT 14 5 13.8 1 600033 WHT 52G 13.8 997626 WHT 14 5 13.8 1 600032 WHT 51G 13.8 997626 WHT 14 5 13.8 1 | External | 132.64 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.21 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 135.29 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0002 | 170.14 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 170.1 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 113.29 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 113.23 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 2e-05 | 148.68 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 148.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00339 | 105.73 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 105.65 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00074 | 104.16 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 104.09 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 111.13 | P13:34-161:ALTW:AUTO-SINGLE:PARNEL9:PARNEL5:1 | External | 111.1 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07729 | 131.45 | P12:230:WERE:CIRC-GRTBND_230:: | Internal | 129.76 | 1.69
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.79 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | External | 104.73 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00167 | 101.92 | P23:345-161:XEL:ADAMS_I:681_S | External | 101.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00223 | 116.56 | 631100 LIBERTY5 161 631101 DUNDEE 5 161 1: 631100 LIBERTY5 161 631101 DUNDEE 5 161 1 | External | 116.51 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00201 | 100.39 | P12:161:MEC:AUTO-SINGLE:UNIONTP5:BUTLER5:1 | External | 100.34 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 114.81 | P23:345:ALTW:MITCHLCO:1160 | External | 114.82 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 153.49 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 153.47 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 118.11 | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 117.37 | 0.74
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 115.64 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 115.6 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0102 | 122.74 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 122.67 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06965 | 116.65 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 115.12 | 1.53
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 106.04 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 106.01 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00863 | 120.09 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 120.04 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0005 | 116.83 | 631024 E CALMS7 115 631095 E CALMS5 161 1: 631024 E CALMS7 115 631095 E CALMS5 161 1 | External | 116.76 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.24 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 135.36 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.26 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 116.28 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.95 | P12:HV:EES::JTEC 5:1 | External | 104.85 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00285 | 121.08 | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 120.95 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 152.05 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 152.03 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01313 | 127.8 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 127.69 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 101.88 | P23:345:AMMO::BLAND:V23 | External | 101.08 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 117.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External | 117.58 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 125.7 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 125.95 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 140.07 | P23:345:MEC:KOSSUTH 904 | External | 140.03 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 132.05 | Base Case | External | 132.06 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 123.99 | P12:EHV:EES::WELSH 7:1(1) | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00153 | 128.09 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 128.18 | -0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00542 | 121.3 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 121.18 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00082 | 145.84 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 145.71 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0014 | 141.62 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 140.7 | 0.92
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03019 | 101.19 | 83524: 523095 HITCHLAND 6 230 523155 OCHILTREE 6 230 1 523093 HITCHLAND 3 115 523195 HANSFORD 3 115 1 | Internal | 100.99 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05738 | 105.1 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 103.6 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07076 | 119.24 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 117.52 | 1.72
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01027 | 122.57 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 122.48 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 135.06 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 134.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.46 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 103.22 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA | External | 103.18 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.7 | 336250 69MILE% 230 336252 1NMIL U5! 26 1: 336250 69MILE% 230 336252 1NMIL U5! 26.0 1 | External | 123.7 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.59 | 657747 ASH1 9 34.5 657701 BARNES 4 230 1: 657747 ASH1 9 34.5 657701 BARNES 4 230 1 | External | 115.51 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00021 | 104.27 | 300626 2CHAMOI 69 300067 5CHAMOI 161 1: 300626 2CHAMOI 69.0 300067 5CHAMOI 161 1 | External | 104.3 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.43 | 92486: 546694 QUINDB 2 69.0 546697 QGEN1 1 13.8 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 546695 QUINDC 2 69.0 546700 QCT2 1 13.8 1 546652 QUIND 5 161 546701 QCT3 1 13.8 1 546652 QUIND 5 161 546698 QGEN2 1 15.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.42 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.79 | P11:345-24:CLEC::DOLHILL7:1 | External | 100.66 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 139.94 | P23:345-161:XEL:ADAMS_I:681_S | External | 139.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01413 | 126.81 | P23:345:MEC:KOSSUTH 904 | External | 126.59 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 126.45 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 126.31 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01309 | 129.54 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 128.75 | 0.79
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 118.53 | P13:345-34-115:OTP:AUTO-SINGLE:ALEXMRES3:ALEXMRES9:ALEXMRES7:9 | External | 118.53 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00396 | 105.52 | 300249 2FAIRPT 69 300076 5FAIRPT 161 1: 300249 2FAIRPT 69.0 300076 5FAIRPT 161 1 | External | 105.41 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01075 | 109.98 | P23:345:AEPW:WILKES CB 1U70 NBTB | External | 109.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 106.98 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK | External | 106.88 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00067 | 125.88 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External | 125.71 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00061 | 122.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 122.63 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00035 | 109.87 | P12:345:MEC:WALCOTT-SUB 56 + SUB 56 9T1 | External | 109.81 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.71 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | External | 116.67 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.8 | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 101.33 | 0.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 125.34 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 125.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00069 | 162.93 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 162.87 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.44 | P13:23-345:OPPD:NEBCTY2G | External | 129.44 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00158 | 135.03 | P23:345:MEC:SYCAMORE 905 | External | 134.81 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06984 | 107.36 | 42991: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 102.38 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 102.38 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 132.98 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 132.97 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 1e-05 | 100.93 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External | 100.9 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.15 | P13:34-161:ALTW:AUTO-SINGLE:H096_WF9:KARMA5:1 | External | 109.15 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 118.36 | P23:345:MEC:ROLLING HILLS 906 | External | 118.35 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.48 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 106.47 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00063 | 124.07 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 123.96 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00174 | 133.56 | P12:161:MEC-WAPA:AUTO-SINGLE:WEBSTER5:HOPE5:1 | External | 133.46 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00055 | 130.48 | 105850: 652529 WATERTN3 345 652829 WATERTN-LNX3 345 Z 652537 WHITE 3 345 652829 WATERTN-LNX3 345 1 652293 WHITE 9 13.8 997148 WHT KU1A 115 1 652504 BROOKNG7 115 652538 WHITE 7 115 1 652538 WHITE 7 115 655472 IVANHOE-ER7 115 1 652538 WHITE 7 115 997148 WHT KU1A 115 1 601006 SPLT RK3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 1 601031 BRKNGCO3 345 652537 WHITE 3 345 2 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 652537 WHITE 3 345 997148 WHT KU1A 115 1 652293 WHITE 9 13.8 997155 WHT KU1A 115 1 652538 WHITE 7 115 997155 WHT KU1A 115 1 652537 WHITE 3 345 997155 WHT KU1A 115 1 652293 WHITE 9 13.8 997146 WHT KU1A 115 1 652538 WHITE 7 115 997146 WHT KU1A 115 1 652537 WHITE 3 345 997146 WHT KU1A 115 1 | External | 130.43 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 105.37 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 105.48 | -0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.004 | 108.33 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | External | 108.28 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01182 | 127.53 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 127.45 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 154.16 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4 | External | 154.15 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 9e-05 | 110.45 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 110.41 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 144.37 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 144.36 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15917 | 136.05 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 135.07 | 0.98
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 112.41 | P12:345:MEC:WALCOTT-SUB 56 + SUB 56 9T1 | External | 112.37 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.71 | 337413 8STERLING2% 500 337434 8OUACHITA% 500 1: 337413 8STERLING2% 500 337434 8OUACHITA% 500 1 | Internal | 106.14 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 117.07 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 117.02 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05903 | 101.72 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 100.41 | 1.31
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.00064 | 139.81 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 139.73 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 112.02 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 111.97 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.42 | P11:13:OTP:AUTO-SINGLE:HOOTLK3G:3 | External | 113.33 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05815 | 101.48 | P12:69:MIDW:WALNUT CREEK-HANSTON | Internal | 100.2 | 1.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.68 | P11:EHV:EES::1TRACTBEL C1:1 | Internal | 106.11 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 135.1 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External | 135.09 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 109.29 | P11:24:CLEC::G1DOLHIL:1 | Internal | 107.92 | 1.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00065 | 117.61 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 117.56 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 101.74 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.67 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.67 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1 | External | 114.57 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.3 | P12:345:XEL-GRE:AUTO-SINGLE:LKFLDXL3:GRE-LKFDGEN3:Z | External | 130.29 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00215 | 111.44 | 631069 ANTA TP5 161 631070 ANITA 5 161 1: 631069 ANTA TP5 161 631070 ANITA 5 161 1 | External | 111.42 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.78 | 344884 7LABADIE1 345 344894 1LAB G1 20 1: 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.46 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01106 | 125.67 | P23:345:MEC:ATCHISON CO 903 | External | 125.59 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 117.59 | 616003 GRE-GRACEV 7 115 616064 GRE-GRACEV 9 41.6 1: 616003 GRE-GRACEV 7 115 616064 GRE-GRACEV 9 41.6 1 | External | 117.57 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.25 | P22:345:AMMO::LABADIE:1 | External | 110.25 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00654 | 120.67 | P23:345:MEC:LOUISA 924 | External | 120.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00242 | 119.9 | P23:345:MEC:LOUISA 924 | External | 119.84 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00064 | 118.73 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 118.75 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00134 | 129.89 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 129.65 | 0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00267 | 116.62 | P23:345:MEC:WALCOTT 914 | External | 116.55 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 114.7 | 87486 J748GENTIE 345 87484 J748MAINTRX1 34.5 1: 87486 J748GENTIE 345 87484 J748MAINTRX1 34.5 1 | External | 114.7 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 118.45 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 118.39 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.38 | P11:18:ALTW:AUTO-SINGLE:MGSST1:1S | External | 126.39 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00267 | 119.26 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 119.21 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00176 | 117.05 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 116.94 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.42 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 105.38 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00065 | 140.13 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 140.06 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 133.48 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.5 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 116.22 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 116.19 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 227 | 227 | 0.00199 | 104.94 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 104.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00399 | 108.53 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 108.34 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00062 | 149.58 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 149.51 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00196 | 123.81 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 123.8 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.76 | P12:HV:EES::TURK 4%:1(1) | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.9 | P23:500:EAI:NBF_SAN SO~2 | External | 123.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.0337 | 100.93 | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | Internal | 100.71 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00072 | 134.58 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External | 134.54 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01086 | 110.88 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 110.85 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 102.03 | P23:345:MEC:KOSSUTH 904 | External | 101.94 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.06 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 117.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00092 | 127.37 | 631048 EMERY 5 161 656201 SHEFFLD5 161 1: 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 127.29 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.46 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 116.36 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00421 | 105.22 | 81778: 509852 T.NO.--7 345 512865 GREC TAP5 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | External | 105.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 139.32 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 139.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.42 | P11:HV:EES::TURKCOAL:1 | External | 100.33 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00265 | 119.05 | P23:345:MEC:HILLS 9114 | External | 118.99 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 5e-05 | 105.71 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 105.71 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00013 | 167.9 | P12:161:ALTW:AUTO-SINGLE:PARNEL5:WILLIAMSBRG5:1 | External | 167.85 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.45 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1 | External | 134.57 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.49 | 501801 G1DOLHIL 24 500250 DOLHILL7 345 1: 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00436 | 106.2 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 106.07 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00144 | 103.58 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 103.62 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00517 | 107.29 | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01032 | 119.14 | P22:345:XEL:ADAMS 3 N1:MN | External | 118.94 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0104 | 115.78 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 115.66 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06926 | 109.95 | P12:115:MKEC:MEDICINELODGE-BARBER:: | Internal | 108.44 | 1.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303030 8XFMRINT2 500 303033 1G2INTHB 18.0 1 | 180 | 180 | 0.00067 | 103.7 | P11:HV:EES::G1 ACAD!:1 | External | 103.69 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.06525 | 114.71 | P12:230:WERE:CIRC-GRTBND_230:: | Internal | 113.01 | 1.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00029 | 129.77 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 129.68 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00034 | 100.41 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 100.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 114.38 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 114.36 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00109 | 141.37 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 141.27 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 111.02 | P11:24:AEPW:PIRKEY 1 | External | 110.94 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.36 | 92405: 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 541158 GRNWD#4 13.2 997780 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997781 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997781 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997780 GREENWOOD 1 13.2 1 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 541158 GRNWD#4 13.2 997787 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997788 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997788 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997787 GREENWOOD 1 13.2 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 102.31 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 125.26 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 125.22 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 103.64 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 103.6 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.61 | P22:345:AEP-CLEC::DOLHILL7:BUS | External | 100.56 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.77 | 629993 G798_WF9 34.5 631185 G798_WF7 161 1: 629993 G798_WF9 34.5 631185 G798_WF7 161 1 | External | 117.77 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00056 | 135.61 | P23:345:MEC:KOSSUTH 904 | External | 135.51 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 121.18 | P23:345:MEC:LOUISA 954 | External | 121.16 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.99 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 115.94 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00306 | 104.31 | 104711: 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 541215 HLLMRK 5 161 541250 SIBLEYPL 161 1 541235 DUNCAN 5 161 541250 SIBLEYPL 161 1 541244 ORRICK 5 161 541250 SIBLEYPL 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 541151 SIBLEY#3 22.0 541250 SIBLEYPL 161 1 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 2 541263 SIBLEY 2 69.0 541250 SIBLEYPL 161 3 541250 SIBLEYPL 161 541346 RTCHFLD5 161 1 | External | 104.21 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.62 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 117.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00489 | 105.91 | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | External | 105.71 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 113.45 | Base Case | External | 113.37 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00583 | 106.92 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 106.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00054 | 104.52 | P23:345:ALTW:MITCHLCO:1130 | External | 104.46 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00198 | 124.36 | P23:345:MEC:KOSSUTH 904 | External | 124.19 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00383 | 103.41 | 84363: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 542969 STILWEL5 161 542994 HICKMAN5 161 1 542969 STILWEL5 161 543050 ANTIOCH5 161 1 542969 STILWEL5 161 543053 REDEL 5 161 1 542969 STILWEL5 161 543057 BUCYRUS5 161 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 542969 STILWEL5 161 997752 STILWELL11 161 11 542969 STILWEL5 161 997751 STILWELL22 161 22 542969 STILWEL5 161 997759 STILWELL11 161 11 542969 STILWEL5 161 997758 STILWELL22 161 22 542969 STILWEL5 161 997755 STILWELL11 161 11 542969 STILWEL5 161 997754 STILWELL22 161 22 | External | 103.31 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00014 | 121.04 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 121.01 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.18191 | 149.14 | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 147.92 | 1.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.52 | 344012 7HPW-N 345 344013 7HPW-S 345 1: 344012 7HPW-N 345 344013 7HPW-S 345 1 | External | 124.42 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 140.84 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 140.76 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.01 | P23:345:MEC:LOUISA 954 | External | 100.92 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 101.38 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1: 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1 | External | 101.29 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00214 | 107.47 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 107.4 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00201 | 101.89 | P13:13-345-161:MEC:AUTO-SINGLE:BOON1XT9:BOONVIL3:BOONVIL5:1 | External | 101.76 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.77 | P11:18:ALTW:AUTO-SINGLE:MGSST1:1S | External | 109.78 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 149.7 | P13:115-161:ALTW:AUTO-SINGLE:STONPT7:STONPT5:1 | External | 149.62 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 112.22 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 112.21 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00127 | 129.8 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 129.71 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00147 | 127.66 | P13:161-69:ITCM:HAYWD#15 T1:MN | External | 127.55 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.68 | P12:HV:EES::PIRKEY 4:1 | External | 108.6 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00029 | 103.76 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 103.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00027 | 107.01 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 107.01 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00238 | 100.69 | 104539: 541200 PHILL 7 345 997775 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 997782 P HILL 11 161 11 541200 PHILL 7 345 997778 P HILL 11 161 11 | External | 100.6 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 139.32 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 139.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 101.05 | 637091 CONTRAIL W 161 637092 J611 COL 34.5 1: 637091 CONTRAIL W 161 637092 J611 COL 34.5 1 | External | 100.99 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00038 | 132.24 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 132.23 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.0003 | 101.31 | 303005 8BIG_CAJUN2% 500 335500 8WEBRE% 500 1: 303005 8BIG_CAJUN2% 500 335500 8WEBRE% 500 1 | External | 101.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00198 | 105.97 | 635640 NORWLK3 345 635641 NORWLK5 161 1: 635640 NORWLK3 345 635641 NORWLK5 161 1 | External | 105.94 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00144 | 103.34 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 103.43 | -0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.45 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 116.4 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 121.98 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External | 121.89 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 100.93 | P12:161:ALTW:AUTO-SINGLE:GRMND5:MQOKETA5:1 | External | 100.88 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 120.76 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 120.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.58 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 134.58 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.67 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External | 114.57 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 118.11 | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 108.6 | P23:345:ALTW:MITCHLCO:1140 | External | 108.52 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 116.33 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 116.28 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 127.58 | P22:345:MEC:SUB 92 | External | 127.46 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.53 | 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2: 344013 7HPW-S 345 344017 2HPW-PAD-S 34.5 2 | External | 124.43 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00397 | 109.09 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 109.02 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 108.84 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 108.81 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0043 | 106.61 | P13:161-345:AMMO::OVERTON:1 | External | 106.48 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00321 | 110.55 | 300043 7KINGDM 345 300044 7MCCRED 345 1: 300043 7KINGDM 345 300044 7MCCRED 345 1 | External | 110.45 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 103.86 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 103.78 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 6e-05 | 105.5 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 105.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00076 | 142.16 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 141.91 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.88 | P11:345:AMMO::RUSHISLAND:U1 | External | 104.71 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.00672 | 108.57 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 108.53 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0109 | 116.92 | P23:345:XEL:8S23 WLM | External | 116.92 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0027 | 122.71 | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 122.69 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00229 | 116.15 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | External | 116.17 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00225 | 109.34 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 109.23 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00194 | 100.34 | P23:345:ALTW:MITCHLCO:1150 | External | 100.21 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00189 | 114.04 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 114 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 118.92 | P22:345:MEC:SUB 92 | External | 118.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 | 187 | 0.03453 | 108.47 | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | Internal | 107.77 | 0.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 126.23 | P12:161:ITCM:DENMARK5-NEWPORT5:IA-SE | External | 126.21 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.16 | P11:18:ITCM:EMERYGT2:1 | External | 109.17 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 123.71 | P22:345:AMMO::LABADIE:3 | External | 123.7 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 138.68 | P12:161:MEC-CFU:BLACK HAWK-UNION-BUTLER | External | 138.61 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 123.65 | P23:345:MEC:LOUISA 924 | External | 123.57 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 148.61 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 148.5 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.47 | P12:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.46 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 8e-05 | 148.47 | 105802: 300097 5MARYVL 161 652560 CRESTON5 161 1 631069 ANTA TP5 161 652560 CRESTON5 161 1 635056 ADAMS 5 161 652560 CRESTON5 161 1 635645 MCKSBRG 5 161 652560 CRESTON5 161 1 652560 CRESTON5 161 997144 CS KY3A 69.0 1 652560 CRESTON5 161 997143 CS KY6A 69.0 1 631069 ANTA TP5 161 631070 ANITA 5 161 1 631069 ANTA TP5 161 652603 EXIRA 5 161 1 630381 SLAKEN 8 69.0 652569 CRESTON8 69.0 1 630385 SLAKES 8 69.0 652569 CRESTON8 69.0 1 630419 ECRESTN8 69.0 652569 CRESTON8 69.0 1 652569 CRESTON8 69.0 997144 CS KY3A 69.0 1 652569 CRESTON8 69.0 997143 CS KY6A 69.0 1 652615 CRESTON29 13.8 997143 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997144 CS KY3A 69.0 1 652560 CRESTON5 161 997151 CS KY3A 69.0 1 652560 CRESTON5 161 997150 CS KY6A 69.0 1 652569 CRESTON8 69.0 997151 CS KY3A 69.0 1 652569 CRESTON8 69.0 997150 CS KY6A 69.0 1 652615 CRESTON29 13.8 997150 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997151 CS KY3A 69.0 1 652560 CRESTON5 161 997142 CS KY3A 69.0 1 652560 CRESTON5 161 997141 CS KY6A 69.0 1 652569 CRESTON8 69.0 997142 CS KY3A 69.0 1 652569 CRESTON8 69.0 997141 CS KY6A 69.0 1 652615 CRESTON29 13.8 997141 CS KY6A 69.0 1 652612 CRESTON 9 13.8 997142 CS KY3A 69.0 1 | External | 147.7 | 0.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 117.6 | P23:345:XEL:8N8 MNN | External | 117.54 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 112.02 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 111.97 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 135.06 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 134.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 125.14 | P12:HV:EES::TURK 4%:1(1) | External | 125.04 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.21 | 631081 M-TOWN 5 161 629215 MGS CT2 18 1: 631081 M-TOWN 5 161 629215 MGS CT2 18.0 1 | External | 101.22 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00039 | 105.86 | P23:345:MEC:LOUISA 954 | External | 105.84 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.41 | P11:24:AEPW:PIRKEY 1 | External | 100.29 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00032 | 104.21 | P23:345:ALTW:MITCHLCO:1160 | External | 104.08 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 118.92 | P23:345:MEC:HILLS 934 | External | 118.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14563 | 127.23 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 126.23 | 1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.002 | 111.27 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 110.57 | 0.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00203 | 108.87 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 108.81 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00031 | 118.73 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 118.66 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00041 | 105 | P23:345:XEL:8S51 HMP | External | 104.97 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00112 | 105.4 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 105.37 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.06 | P11:HV:EES::1GOXY U1!:1 | External | 104.92 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 105.89 | Base Case | External | 105.9 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.29 | P12:HV:EES::TURK 4%:1(1) | External | 107.21 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 134.97 | P23:345:MEC:OAK GROVE 903 | External | 134.84 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.77 | 344887 7LABADIE4 345 344897 1LAB G4 20 1: 344887 7LABADIE4 345 344897 1LAB G4 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.75 | P11:345:OPPD:NEBCTY1G | External | 117.75 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00051 | 126.47 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 126.38 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 136.03 | P23:345-161:XEL:ADAMS_I:680_S | External | 135.98 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01282 | 128.46 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 128.3 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.0022 | 103.41 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00153 | 128.35 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 128.4 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06916 | 108.85 | 104522: 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 107.24 | 1.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 117.81 | 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1: 603185 FIBROMN7 115 615365 GRE-BENSON 7 115 1 | External | 117.71 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 136.27 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1: 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 136.12 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00119 | 105.93 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998347 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998346 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998355 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998354 TAHAUTO2 69.0 2 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 105.99 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00064 | 124.78 | P23:345:AMIL::SANDBURG:3 | External | 124.65 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01043 | 119.26 | P21:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 119.21 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00054 | 134.8 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 134.7 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00023 | 106.15 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 106.25 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.98 | P23:345:GRE:CHL 304JB21 | External | 114.03 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00145 | 101.58 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 101.51 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.86 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.87 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 123.91 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 123.93 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 101.05 | 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1: 635999 IRVINGTON3 345 637077 KOSSUTH WIND 345 1 | External | 101.06 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.76 | P42:345:OKGE:SB_BOER7383 | Internal | 106.61 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.85 | P23:EHV:EES::8STERLING2%:9 | External | 123.83 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 112.51 | P21:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 112.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 102.38 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 102.38 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00047 | 106.89 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 106.82 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | P23:500:EES-LAGN:ABF_HTBG-B | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.51 | P12:EHV:EES::WELSH 7:1 | External | 116.47 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.3 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 112.34 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 103.4 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 103.34 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01076 | 113.56 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 113.47 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 136.07 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 135.99 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0002 | 120.58 | P23:345:AMMO::ZACHARY:2 | External | 120.52 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997576 345-161 161 2 | 500 | 500 | 0.00041 | 109.42 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 137.98 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 137.93 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.18 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External | 126.39 | -0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.38 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 100.28 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00161 | 102.86 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 102.76 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.55 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.56 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 134.66 | P11:24:AEPW:PIRKEY 1 | External | 134.6 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 3e-05 | 100.19 | P23:345:MEC:MONTEZUMA 902 | External | 100.18 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.7 | 105460: 525824 TUCO_TR1 1 13.2 998064 UPDATE LATER 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 525824 TUCO_TR1 1 13.2 998071 UPDATE LATER 230 1 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 | Internal | 106.67 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00075 | 125.9 | P23:345:AMIL::HERLEMAN:1 | External | 125.79 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00166 | 108.09 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 107.98 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15917 | 132.98 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 131.95 | 1.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.86 | P12:161:ALTW:AUTO-SINGLE:NUTHTCH5:WHISWIL5:1 | External | 109.87 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01073 | 110.45 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 110.42 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 8e-05 | 111.15 | 93774: 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 | External | 111.08 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.27 | 657713 TRFALLS7 115 3WXFMR TRF 1: 657713 TRFALLS7 115 997125 TRF 69.0 1 657910 TRFALLS8 69.0 997125 TRF 69.0 1 657767 TRFALLS9 13.2 997125 TRF 69.0 1 657713 TRFALLS7 115 997132 TRF 69.0 1 657910 TRFALLS8 69.0 997132 TRF 69.0 1 657767 TRFALLS9 13.2 997132 TRF 69.0 1 657713 TRFALLS7 115 997123 TRF 69.0 1 657910 TRFALLS8 69.0 997123 TRF 69.0 1 657767 TRFALLS9 13.2 997123 TRF 69.0 1 | External | 108.25 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 102.17 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 102.12 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00153 | 112.64 | 104712: 541253 ST JOE 5 161 541257 COOK 5 161 1 541253 ST JOE 5 161 541258 WOODBIN5 161 1 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 541253 ST JOE 5 161 997777 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997776 ST. JOSEPH33 161 33 541253 ST JOE 5 161 997784 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997783 ST. JOSEPH33 161 33 541253 ST JOE 5 161 997780 ST. JOSEPH22 161 22 541253 ST JOE 5 161 997779 ST. JOSEPH33 161 33 | External | 112.58 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00056 | 139.1 | P12:115:ALTW:AUTO-SINGLE:STONPT7:SQUARED7:1 | External | 139.02 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00011 | 103.68 | P12:HV:EES::5JONESBORO!:JONESBO5!:1 | External | 103.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.54 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1 | External | 115.48 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.81 | 104893: 514902 MCCLAIN4 138 515000 MCLN 2G 18.0 1 514902 MCCLAIN4 138 514999 MCLN 1G 18.0 1 514902 MCCLAIN4 138 514998 MCLN 1S 18.0 1 | Internal | 105.27 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01031 | 114.51 | P12:345:MEC:TIFFIN-ARNOLD | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 113.32 | P23:345:ATC:NORTHMADISON:6037-S | External | 113.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.96 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 121.89 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 117.73 | P23:345:ALTW:MITCHLCO:1150 | External | 117.58 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.19647 | 103.17 | 4007: 539645 DCBEEF3 115 539671 FTDODGE3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 1 539671 FTDODGE3 115 539771 NFTDODG3 115 2 539671 FTDODGE3 115 539783 CRKCK 3 115 1 539670 FTDODGP1 15.0 539671 FTDODGE3 115 1 539671 FTDODGE3 115 997824 FTDODGE3 34.5 1 539645 DCBEEF3 115 539740 EDODGE 3 115 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 539666 GBENDTP3 115 539678 GRTBEND3 115 1 539678 GRTBEND3 115 539681 N-GBEND3 115 1 539678 GRTBEND3 115 539684 OTISSUB3 115 1 539677 GRTBEND1 13.8 539678 GRTBEND3 115 1 539678 GRTBEND3 115 997841 MULGREN6 115 1 539678 GRTBEND3 115 997820 GRTBEND3 34.5 1 539666 GBENDTP3 115 539692 SEWARD 3 115 1 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 539671 FTDODGE3 115 997831 FTDODGE3 34.5 1 539678 GRTBEND3 115 997848 MULGREN6 115 1 539678 GRTBEND3 115 997827 GRTBEND3 34.5 1 539671 FTDODGE3 115 997827 FTDODGE3 34.5 1 539678 GRTBEND3 115 997844 MULGREN6 115 1 539678 GRTBEND3 115 997823 GRTBEND3 34.5 1 | Internal | 101.93 | 1.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01043 | 119.26 | P12:345:MEC:AUTO-SINGLE:HILLS3:TIFFIN3:1 | External | 119.21 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 5e-05 | 134.86 | 82330: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.87 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.84 | P13:138-24:AEPW:PIRKEY 4 | External | 110.76 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00443 | 106.2 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 106.19 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 117.06 | P11:24:AEPW:PIRKEY 1 | External | 117 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 106.81 | P11:345:AMMO::RUSHISLAND:U1 | External | 106.71 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00049 | 109.33 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 108.67 | 0.66
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00479 | 106.83 | P12:345:WERE:N345-AECI_345:: | External | 106.71 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.79 | P23:EHV:EES::8STERLING2%:9 | External | 104.73 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 100.44 | 63174: 344078 7WILDWD TP 345 344886 7LABADIE3 345 1 344079 7WILDWD 345 345985 4WILDWD 1 138 1 344884 7LABADIE1 345 345046 7MASON 2 345 1 344078 7WILDWD TP 345 345051 7MASON 3 345 1 344078 7WILDWD TP 345 344079 7WILDWD 345 Z | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.87 | P11:345:MEC:GDMEC CT1 | External | 100.82 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 121.98 | P12:161:AMMO-ALTW::CARBIDE:VIELE:1 | External | 121.89 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00035 | 191.08 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 191.09 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00183 | 122.28 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 122.23 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01207 | 134.46 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 134.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 25 | 31 | 0.00021 | 111.31 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997058 GLENHAM TR2 115 2 661035 GLENHAM7 115 997058 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997058 GLENHAM TR2 115 2 661038 GLENHAM4 230 997065 GLENHAM TR2 115 2 661035 GLENHAM7 115 997065 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997065 GLENHAM TR2 115 2 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 111.32 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.06 | P13:138-24:AEPW:TURK 4 | External | 124.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 3e-05 | 100.19 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 100.18 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00191 | 100.73 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 100.69 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00148 | 136.38 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 135.48 | 0.9
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 107.96 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 129.03 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 128.03 | 1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.39 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 106.33 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00078 | 130.67 | 633261 KPECKTP5 161 636673 SB 112 5 161 1: 633261 KPECKTP5 161 636673 SB 112 5 161 1 | External | 130.54 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00159 | 120.53 | 620362 OAKES 4 230 620363 FORMAN 4 230 1: 620362 OAKES 4 230 620363 FORMAN 4 230 1 | External | 120.33 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01091 | 112.39 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.94 | P22:345:AMMO::RUSHISLAND:2 | External | 104.77 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00145 | 130.1 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 130.23 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06677 | 117.08 | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | Internal | 115.36 | 1.72
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.32 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 997758 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997765 EASTOWNE11 161 11 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | External | 109.18 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.51 | P23:345:AEPW:WELSH CB 10630 NBTB | External | 110.46 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.09 | 335190 6NELSON% 230 335206 1NELSON_G6! 20 1: 335190 6NELSON% 230 335206 1NELSON_G6! 20.0 1 | Internal | 105.63 | 1.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.92 | P11:HV:EES::1GYP_U4 G1:1 | Internal | 107.27 | 1.65
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01207 | 127.94 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 127.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0005 | 120.24 | P12:161:ALTW:AUTO-SINGLE:DENMARK5:BRLGTN5:2 | External | 120.24 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00201 | 100.55 | P12:161:MEC-CFU:BLACK HAWK-UNION-BUTLER | External | 100.5 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08908 | 145.6 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 144.02 | 1.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.76 | 105009: 515044 SEMINOL4 138 998281 SEMINOL2 138 1 515045 SEMINOL7 345 998281 SEMINOL2 138 1 515757 SEMINO21 14.4 998281 SEMINOL2 138 1 515044 SEMINOL4 138 998282 SEMINOL1 138 1 515045 SEMINOL7 345 998282 SEMINOL1 138 1 515756 SEMINO11 14.4 998282 SEMINOL1 138 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515044 SEMINOL4 138 998289 SEMINOL2 138 1 515045 SEMINOL7 345 998289 SEMINOL2 138 1 515757 SEMINO21 14.4 998289 SEMINOL2 138 1 515044 SEMINOL4 138 998290 SEMINOL1 138 1 515045 SEMINOL7 345 998290 SEMINOL1 138 1 515756 SEMINO11 14.4 998290 SEMINOL1 138 1 515044 SEMINOL4 138 998286 SEMINOL2 138 1 515045 SEMINOL7 345 998286 SEMINOL2 138 1 515757 SEMINO21 14.4 998286 SEMINOL2 138 1 515044 SEMINOL4 138 998287 SEMINOL1 138 1 515045 SEMINOL7 345 998287 SEMINOL1 138 1 515756 SEMINO11 14.4 998287 SEMINOL1 138 1 | Internal | 105.26 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01299 | 127.68 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.46 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.46 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00176 | 117.05 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 116.94 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 104.59 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 104.49 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01281 | 129.62 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 129.45 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.3 | 921961: 541400 EASTOWN7 345 997758 EASTOWNE11 161 11 541400 EASTOWN7 345 997765 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | External | 109.16 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 134.99 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 134.96 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00143 | 102.49 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 102.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 114.47 | Base Case | External | 114.46 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.7 | 657747 ASH1 9 34.5 657701 BARNES 4 230 1: 657747 ASH1 9 34.5 657701 BARNES 4 230 1 | External | 113.61 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00168 | 101.1 | P12:161:MEC:AUTO-SINGLE:HAYES5:POMEROY5:1 | External | 101.06 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.77 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 106.77 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01225 | 138.25 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 138.16 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.06 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | Internal | 104.41 | 1.65
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0011 | 113.7 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 113.66 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.46 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 116.36 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00341 | 102.5 | 104529: 541205 BLSPE 5 161 541211 BLSPS 5 161 1 541206 PRALEE 5 161 541211 BLSPS 5 161 1 541205 BLSPE 5 161 541226 GRAINVL5 161 1 | External | 102.42 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 125.82 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 125.85 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.55 | P13:18-345:OPPD:NEBCTY1G | External | 129.55 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 126.72 | 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1: 635737 J475-J555POI 345 635731 N ENGL B1 9 34.5 1 | External | 126.62 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 105.73 | 81775: 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 512650 GRDA1 7 345 512750 TONECE7 345 1 512650 GRDA1 7 345 512865 GREC TAP5 345 1 512688 GRDA17-1 22.8 512650 GRDA1 7 345 1 512650 GRDA1 7 345 998343 GRDAUTO1 161 1 512650 GRDA1 7 345 998351 GRDAUTO1 161 1 512650 GRDA1 7 345 998348 GRDAUTO1 161 1 | External | 105.63 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.24 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1 | External | 113.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0039 | 105.8 | P24:345:AMMO::RUSHISLAND:V14 | External | 105.84 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 109.88 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK | External | 109.8 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01332 | 124.59 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 124.49 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00067 | 124.44 | P23:345:AMMO::ZACHARY:2 | External | 124.35 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 105.47 | P12:HV:EES::5NEWMAD!:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00251 | 116.34 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | External | 116.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.33 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 101.27 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00106 | 106 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 105.82 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.11 | 85478: 640184 GENTLMN4 230 640010 GENTLM1G 23.0 1 640183 GENTLMN3 345 640011 GENTLM2G 24.0 1 | External | 135.23 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00895 | 134.69 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 134.62 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 110.13 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 110.03 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 135.48 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 135.5 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.62 | 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1: 344012 7HPW-N 345 344014 2HPW-PAD-N 34.5 1 | External | 124.53 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00016 | 103.29 | 636225 UNIONTP5 161 636240 BUTLER 5 161 1: 636225 UNIONTP5 161 636240 BUTLER 5 161 1 | External | 103.25 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635641 NORWLK5 161 635653 GRENFLD5 161 1 | 409 | 410 | 0.00399 | 100.58 | P23:345:MEC:SE POLK 901 OR 902 | External | 100.53 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00307 | 104.61 | P23:345:AMMO::BLAND:V15 | External | 104.55 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 104.59 | 104500: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 104.49 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 105.33 | P23:345:MEC:WALCOTT 914 | External | 105.26 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 123.08 | P23:345:XEL:8S22 WLM | External | 123 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00391 | 107.34 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.18 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.67 | P12:EHV:EES::8SANS SOUCI%:1 | External | 115.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00136 | 110.94 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 110.86 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00201 | 133.58 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 133.17 | 0.41
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00029 | 103.76 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 103.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00145 | 117.62 | P21:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 117.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.85 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 150.79 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.5 | P11:22:CLEC::G3MADISN:1 | External | 116.48 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 117.06 | P11:HV:EES::PIRKEY 1:1 | External | 117 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.24 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 112.24 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 138.78 | Base Case | External | 138.78 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0007 | 100.41 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 100.34 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.9 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.82 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0022 | 106.16 | P21:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 106.13 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.8 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 127.04 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00102 | 116.82 | 86694: 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 631048 EMERY 5 161 656201 SHEFFLD5 161 1 | External | 116.73 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00198 | 124.25 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 124.12 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00301 | 100.95 | 300088 5HUBEN 161 300042 7HUBEN 345 1: 300088 5HUBEN 161 300042 7HUBEN 345 1 | External | 100.82 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 109.39 | 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1: 608729 HIBBTACG 13.8 608728 HIBBTAC7 115 1 | External | 109.37 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 111.43 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 111.44 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 125.7 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 125.95 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00034 | 100.41 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 100.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 111.26 | P23:345:MEC:LOUISA 954 | External | 111.24 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.54 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | Internal | 104.84 | 1.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 119.06 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 119 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 114.27 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 114.23 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 138.86 | P13:18-115:ALTW:AUTO-SINGLE:PRCRK4G:PRARCK7:1 | External | 138.81 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00559 | 114.74 | 104653: 300071 5CLINTN 161 542969 STILWEL5 161 1 541198 PECULR 7 345 542968 STILWEL7 345 1 | External | 114.66 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:20:AMMO:1LAB G2:2 | External | 107.19 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.88 | 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1: 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1 | External | 108.9 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 101.75 | P23:345:MEC:KOSSUTH 904 | External | 101.66 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00378 | 102.48 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 102.4 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.36 | 92382: 543109 WG CT 4 13.8 543105 BULLCRK5 161 1 543108 WG CT 3 13.8 543105 BULLCRK5 161 1 543107 WG CT 2 13.8 543105 BULLCRK5 161 1 543106 WG CT 1 13.8 543105 BULLCRK5 161 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.32 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00774 | 111.63 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 111.5 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 135.63 | P23:345:ALTW:MITCHLCO:1150 | External | 135.41 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.42 | 631081 M-TOWN 5 161 629214 MGS CT1 18 1: 631081 M-TOWN 5 161 629214 MGS CT1 18.0 1 | External | 109.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00012 | 150.96 | P12:161:DPC:ALM-ROC | External | 150.9 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.5 | P11:345:MEC-OPPD:NEBRASKA CITY 1 | External | 129.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.7 | P12:345:OKGE-SPS:BKRBKR430 | Internal | 106.67 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 100.54 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 100.45 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00011 | 103.68 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 103.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 105.9 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 105.88 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.48 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 117.48 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01159 | 110.15 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 110.07 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14563 | 129.44 | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | Internal | 128.46 | 0.98
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0109 | 119.27 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 119.19 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0011 | 141.01 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 140.92 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00057 | 127.24 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 127.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 109.1 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 109.07 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 106.96 | P22:345:AMMO::LABADIE:2 | External | 106.98 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01079 | 117.3 | P23:345-161:XEL:ADAMS_I:680_S | External | 117.25 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 4e-05 | 110.56 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00022 | 148.89 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9: 601002 ADAMS 3 345 997679 ADAMS 3 161 9 631046 ADAMS 5 161 997679 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997679 ADAMS 3 161 9 601002 ADAMS 3 345 997686 ADAMS 3 161 9 631046 ADAMS 5 161 997686 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997686 ADAMS 3 161 9 601002 ADAMS 3 345 997682 ADAMS 3 161 9 631046 ADAMS 5 161 997682 ADAMS 3 161 9 605739 ADAMS1 9 13.8 997682 ADAMS 3 161 9 | External | 149.02 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 113.91 | P13:13-115:ALTW:AUTO-SINGLE:SUTHLCT1:M-TOWN7:1 | External | 113.91 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06926 | 109.42 | P12:115:MKEC:FORTDODGE-SHOOTINGSTARTAP:: | Internal | 107.92 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 121.32 | 84406: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 121.33 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00048 | 126.9 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 126.69 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 137.56 | P23:345:MEC:LOUISA 954 | External | 137.52 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.99 | P13:13-161:ALTW:AUTO-SINGLE:SUTHLCT3:M-TOWN5:1 | External | 134.99 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 100.54 | P23:345:MEC:CBEC 908 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 149.7 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 149.62 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 105.5 | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1 | External | 105.35 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00192 | 115.08 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 115.15 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 135.79 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 135.72 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 128.03 | P11:161:ITCM:MGS CT1:1C | External | 128.04 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00048 | 150.06 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 150 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 103.33 | 104501: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541209 SEDALIA5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 103.22 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.78 | 344886 7LABADIE3 345 344896 1LAB G3 20 1: 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 956 | 1152 | 0.00654 | 110.33 | P23:345:MEC:LOUISA 924 | External | 110.28 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997576 345-161 161 2 | 500 | 500 | 0.00041 | 111.94 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997577 345-161 161 1 615307 GRE-PL VLLY5 161 997577 345-161 161 1 615308 GRE-PL VLL1T 13.8 997577 345-161 161 1 615306 GRE-PL VLLY3 345 997585 345-161 161 1 615307 GRE-PL VLLY5 161 997585 345-161 161 1 615308 GRE-PL VLL1T 13.8 997585 345-161 161 1 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 111.92 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.17683 | 100.82 | P12:115:MIDW:RICE-LYONS | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 103.95 | 345409 5OVERTON 161 346117 2OVERTON 69 1: 345409 5OVERTON 161 346117 2OVERTON 69.0 1 | External | 103.86 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0013 | 120.62 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 120.55 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00292 | 103.18 | P13:161-345:AMMO::MONTGOMERY:1 | External | 103.1 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.8 | 631037 MPWSPLIT 161 631108 DENMARK5 161 1: 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01313 | 127.8 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 127.69 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 120.76 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 120.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00125 | 128.53 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External | 128.47 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00162 | 109.92 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 109.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00105 | 114.13 | P12:161:MEC-CBPC:FRANKLIN-HAMPTON-SHEFFIELD | External | 114.02 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00167 | 101.92 | P23:345-161:XEL:ADAMS_I:680_S | External | 101.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 119.15 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 119.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00129 | 114.04 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 114.11 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00309 | 104.3 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 104.21 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.95 | P11:24:AEPW:TURKCOAL | External | 116.9 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.98 | 631081 M-TOWN 5 161 629215 MGS CT2 18 1: 631081 M-TOWN 5 161 629215 MGS CT2 18.0 1 | External | 125.99 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 123.47 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 123.5 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.92 | P13:138-24:AEPW:PIRKEY 4 | External | 116.85 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06965 | 116.72 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 115.18 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 106.18 | 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2: 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2 | External | 106.19 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00015 | 127.33 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 127.25 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.96 | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1: 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | External | 121.89 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01177 | 126.28 | P23:345:AMMO::MONTGOMERY:V43 | External | 126.17 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303006 1BCAJUN2_U1% 24.0 303005 8BIG_CAJUN2% 500 1 | 615 | 615 | 0.00045 | 100.11 | P11:18:EES:STGABE:1 | External | 100.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 129.25 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 129.11 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00574 | 114.87 | 104253: 542969 STILWEL5 161 543126 LACKMAN5 161 1 300071 5CLINTN 161 542969 STILWEL5 161 1 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | External | 114.77 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07076 | 119.37 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 117.57 | 1.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.11 | 300001 1THLG1 20 300120 5THMHILB1 161 1: 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 109.08 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.54 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 122.6 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00214 | 107.47 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 107.4 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.3 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 100.29 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0011 | 150.9 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 150.75 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00018 | 111.86 | P23:345-161:XEL:ADAMS_I:681_S | External | 111.84 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 116.67 | P11:345:MEC:GDMEC ST | External | 116.67 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 117.63 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 117.58 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.7 | P13:18-345:OPPD:NEBCTY1G | External | 117.71 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01207 | 137.98 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 137.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00385 | 105.76 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 105.62 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.5 | P11:345:OPPD:NEBCTY1G:LT | External | 129.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.3 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 112.34 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 115.47 | P23:345:XEL:8N8 MNN | External | 115.37 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.47 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 108.44 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.92 | 636625 IPSCO 3 345 636627 IPSCOSV9 34 1: 636625 IPSCO 3 345 636627 IPSCOSV9 34.0 1 | External | 117.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.04 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | Internal | 106.44 | 1.6
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00046 | 127.97 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 127.91 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.34 | 303006 1BCAJUN2_U1% 24 303005 8BIG_CAJUN2% 500 1: 303006 1BCAJUN2_U1% 24.0 303005 8BIG_CAJUN2% 500 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00194 | 100.18 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 100.05 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 100.66 | P12:345:AMMO::BLAND:FRANKS:3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00028 | 175.76 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 175.74 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 140.54 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 140.48 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00034 | 114.67 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 114.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 151.14 | P12:115:ALTW:AUTO-SINGLE:6ST7:SAINTSRUN7:1 | External | 151.13 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 114.71 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 114.71 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.64 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 118.69 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0006 | 158.01 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 157.94 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 0.00018 | 115.48 | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | External | 115.48 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.54 | 336250 69MILE% 230 336251 1NMIL U4! 26 1: 336250 69MILE% 230 336251 1NMIL U4! 26.0 1 | External | 110.52 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.0016 | 109.27 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 109.21 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 109.24 | P23:345:ALTW:MITCHLCO:1130 | External | 109.07 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01151 | 112.98 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 112.87 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 158.76 | P13:34-161:ALTW:AUTO-SINGLE:PARNEL9:PARNEL5:1 | External | 158.76 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.07488 | 125.08 | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 123.75 | 1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0004 | 137.9 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 137.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00124 | 114.05 | P23:345:ITCM:HCKRYCK:FUT3 | External | 113.53 | 0.52
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 119.31 | 631109 BRLGTN 5 161 630037 BRLGTN18 69 1: 631109 BRLGTN 5 161 630037 BRLGTN18 69.0 1 | External | 119.22 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01334 | 131.59 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 131.45 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.74 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.75 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00586 | 104.27 | P23:345:MEC:WALCOTT 944 | External | 104.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00161 | 124.25 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 124.17 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01097 | 116.93 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 116.89 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00058 | 117.4 | 631075 CARBIDE5 161 630006 CARBIDE8 69 1: 631075 CARBIDE5 161 630006 CARBIDE8 69.0 1 | External | 117.32 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15917 | 136.48 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 135.44 | 1.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.001 | 139.82 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 139.68 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00528 | 119.21 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 119.1 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 129.78 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 129.74 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05903 | 101.76 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 100.43 | 1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.9 | 103758: 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | External | 104.82 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.59 | P23:HV-EHV:EES::8STERLING2%:4 | External | 100.5 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00552 | 116.27 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 116.1 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 125.53 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 125.78 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 177.73 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 177.72 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06985 | 110.74 | 38761: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 130.23 | P22:345:XEL:ADAMS 3 N1:MN | External | 130.08 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00054 | 106.16 | P23:345:ALTW:MITCHLCO:1150 | External | 106.07 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01079 | 111.07 | P23:345-161:XEL:ADAMS_I:681_S | External | 111.05 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00179 | 121.82 | P23:345:ATC:NORTHMADISON:6037-S | External | 121.77 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 133.34 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 133.35 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00033 | 100.75 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 100.7 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00045 | 119.55 | P23:345:AMMO::MONTGOMERY:V43 | External | 119.52 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 137.37 | P23:345:ATC:NORTHMADISON:6033-S | External | 137.3 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 117.59 | P13:115-41:OTP:AUTO-SINGLE:GRE-GRACEV7:GRE-GRACEV9:1 | External | 117.57 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00022 | 157.59 | P12:161:ALTW-MEC:AUTO-SINGLE:PARNEL5:HILLS5:1 | External | 157.56 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.18 | P11:18:ALTW:AUTO-SINGLE:MGSCT2:2C | External | 126.19 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 113.13 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 113.07 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00118 | 103.24 | P45:345:OPPD:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 123.79 | P23:EHV:EES::8STERLING2%:9 | External | 123.63 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00166 | 108.09 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 107.98 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 129.68 | P13:34-161:MEC:AUTO-SINGLE:WALLLK9:WALLLK5:2 | External | 129.69 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.71 | P12:345:MEC:TIFFIN 9T1 SPS | External | 121.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00141 | 119.24 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.15 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0135 | 124.58 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT | External | 124.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00182 | 117.59 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.85 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | External | 103.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.6 | P13:18-161:ALTW:AUTO-SINGLE:MGSST1:M-TOWN5:1 | External | 101.62 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 119.15 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 119.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00774 | 117.47 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 117.37 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00305 | 100.56 | P22:345:AMMO::RUSHISLAND:2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 144.71 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 144.63 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.36 | P13:138-24:AEPW:R.S.S.-4 | Internal | 104.82 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 102.8 | P23:345:MEC:OAK GROVE 904 | External | 102.71 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 145.67 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 145.61 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00194 | 100.36 | P22:345:XEL:ADAMS 3 N1:MN | External | 100.27 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00034 | 103.18 | P23:345:MEC:LOUISA 924 | External | 103.13 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.38 | 336250 69MILE% 230 336252 1NMIL U5! 26 1: 336250 69MILE% 230 336252 1NMIL U5! 26.0 1 | External | 109.31 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00013 | 150.53 | 681532 WABACO 5 161 681537 ROCHSTR5 161 1: 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | External | 150.46 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00035 | 134.14 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 133.98 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.92 | P12:HV:EES::TURK 4%:1(1) | External | 110.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0004 | 125.19 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 125.15 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 73.1 | 73.1 | 0.27224 | 104.6 | P12:230:WERE:CIRC-GRTBND_230:: | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 115.7 | 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z: 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z | External | 115.65 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.69 | P23:EHV:EES::8STERLING2%:9 | External | 110.59 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00012 | 140.34 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 140.31 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 1 | 500 | 500 | 0.0004 | 110.95 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 110.93 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.7 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 105.52 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00032 | 142.95 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 142.89 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 113.33 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | External | 113.31 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01027 | 122.82 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 122.74 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00289 | 119.48 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 119.46 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 126.85 | 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1: 635737 J475-J555POI 345 635732 N ENGL B2 9 34.5 1 | External | 126.75 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00128 | 110.4 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.59 | P11:18:ALTW:AUTO-SINGLE:MGSCT1:1C | External | 109.61 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.17332 | 102.75 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 101.66 | 1.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.00561 | 127.08 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 126.86 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.06047 | 101.36 | P12:69:MIDW:GRT BND N-BNKR HLL | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.85 | 337413 8STERLING2% 500 337434 8OUACHITA% 500 1: 337413 8STERLING2% 500 337434 8OUACHITA% 500 1 | External | 123.82 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.22 | P11:HV:EES::1NMIL U5!:1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.5 | P11:345:MEC:GDMEC CT2 | External | 130.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 100.19 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 100.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 107.29 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 107.18 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 129.03 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 128.03 | 1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00067 | 124.44 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 124.35 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00214 | 113.23 | P23:345:MEC:LOUISA 964 | External | 113.21 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 153.49 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 153.47 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.85 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | External | 123.82 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.08 | 103758: 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | External | 100.03 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 124.38 | P11:HV:EES::1GOXY U1!:1 | External | 124.36 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.8 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:DENMARK5:1 | External | 105.8 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.34 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z: 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | External | 110.32 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01207 | 134.46 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 134.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 100.42 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 100.24 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01096 | 117.98 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 117.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.33 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 117.34 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.71 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 121.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0021 | 101.9 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 101.88 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.15 | P11:34:ALTW:AUTO-SINGLE:H096_WF9:1 | External | 109.15 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0022 | 106.16 | P12:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | External | 106.13 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.42 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 122.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00047 | 131.61 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 131.59 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00137 | 112.37 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 112.38 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01207 | 127.94 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 127.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00583 | 106.92 | P22:345:MEC:SUB 92 | External | 106.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00469 | 105.12 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | External | 105.04 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 115.44 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 115.33 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01299 | 127.68 | 104522: 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 127.58 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00032 | 103.69 | P12:161:ALTW:AUTO-SINGLE:MQOKETA5:WYOMING5:1 | External | 103.63 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01401 | 130.83 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 130.49 | 0.34
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 108.48 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 108.38 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0007 | 100.41 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 100.34 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 103.38 | Base Case | External | 103.31 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 121.98 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:CARBIDE5:1 | External | 121.89 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0005 | 134.99 | P12:115:XEL:AUTO-SINGLE:CRYSTAL7:RIVFLSN7:1 | External | 135.02 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 116.32 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 116.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00436 | 105.52 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.39 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.52 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.38 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.39 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 124.47 | P11:HV:EES::1GYP_U4 G1:1 | External | 124.47 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 108.7 | P23:345:ALTW:MITCHLCO:1150 | External | 108.62 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.66 | P11:22:CLEC::G3MADISN:1 | External | 100.54 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 144.71 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 144.63 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 135.51 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | External | 135.45 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01606 | 129.98 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 129.86 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00285 | 121.09 | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | External | 120.98 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.00953 | 111.07 | P23:345:MEC:ATCHISON CO 903 | External | 111.04 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01088 | 114.98 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 114.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00528 | 107.32 | 104628: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541209 SEDALIA5 161 541241 SEDEAST5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 300082 5GEORGE 161 541209 SEDALIA5 161 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 541271 SEDN 2 69.0 541273 KELHYS 2 69.0 1 | External | 107.24 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 118.05 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.0016 | 109.27 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 109.21 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.75 | P23:HV-EHV:EES::8STERLING2%:4 | Internal | 106.17 | 1.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 5e-05 | 114.27 | P12:115:XEL:AUTO-SINGLE:MAYNARD7:KERKHOVENTP7:1 | External | 114.09 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00011 | 104.43 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 104.42 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01606 | 129.98 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 129.86 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00033 | 109.64 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 109.58 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 169.81 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 169.71 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 130.3 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 130.26 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00542 | 121.3 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | External | 121.18 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00194 | 100.15 | P23:345:ALTW:MITCHLCO:1140 | External | 100.02 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00048 | 128.22 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 128.23 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03247 | 100.02 | 105092: 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | Internal | 100.09 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00044 | 144.34 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 144.27 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00105 | 114.13 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 114.02 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 140.38 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 140.3 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:HV:EES::TURKCOAL:1 | External | 107.18 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 137.09 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 136.99 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 123.52 | P23:345-161:XEL:ADAMS_I:681_S | External | 123.47 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 138.3 | P23:345:AMMO::ZACHARY:2 | External | 138.21 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0002 | 130.07 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 129.82 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0108 | 116.55 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 116.5 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05892 | 102.07 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 100.74 | 1.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00583 | 106.92 | P23:345:MEC:HILLS 934 | External | 106.88 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00197 | 101.85 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 101.8 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00035 | 120.06 | 300090 5KINGDM 161 300523 5WLMSBG 161 1: 300090 5KINGDM 161 300523 5WLMSBG 161 1 | External | 119.32 | 0.74
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 102.87 | 106092: 656367 WEB TAP8 69.0 656879 PASSWATR8 69.0 1 656367 WEB TAP8 69.0 656857 DUNCOMBE8 69.0 1 656367 WEB TAP8 69.0 656778 IESLYONT8 69.0 1 | External | 102.77 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00051 | 138.02 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 137.88 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00119 | 109.63 | P12:161:ALTW-MEC:AUTO-SINGLE:BNEJCT5:FT.DODG5:1 | External | 109.48 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0021 | 101.31 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 101.24 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.91 | P11:24:AEPW:TURKCOAL | External | 108.83 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00047 | 141.89 | 603065 CHISAGO7 115 605269 LINDSTM7 115 1: 603065 CHISAGO7 115 605269 LINDSTM7 115 1 | External | 141.86 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.79 | 501801 G1DOLHIL 24 500250 DOLHILL7 345 1: 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 | External | 100.66 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.54 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 122.6 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00165 | 101.23 | P22:345:XEL:ADAMS 3 N1:MN | External | 101.07 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 136.19 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 136.14 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 101.17 | 635000 CBLUFFS3 345 635023 WSEC 3G 24 1: 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 116 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 116.01 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 107.29 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 107.18 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15184 | 102.73 | Base Case | Internal | 101.7 | 1.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | P13:230,22:CLEC::G3MADISN::1 | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.013 | 127.84 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00127 | 129.8 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 129.71 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00144 | 103.67 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 103.68 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00177 | 102.32 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 102.24 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.66 | P11:345:OPPD:NEBCTY1G:LT | External | 117.66 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 136.03 | P23:345-161:XEL:ADAMS_I:681_S | External | 135.98 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.8 | P11:EHV:EES::1TRACTBEL C1:1 | External | 104.73 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06968 | 121.07 | P12:230:WERE:SUMM-MWE_230:: | Internal | 119.44 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 128.11 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 127.99 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 103.53 | Base Case | Internal | 102.07 | 1.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00196 | 100.82 | 345027 5MARIOSA 161 345238 7MARIOSA 345 1: 345027 5MARIOSA 161 345238 7MARIOSA 345 1 | External | 100.74 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.09296 | 104.58 | P13:115-230:MIDW:RICE COUNTY | Internal | 103.91 | 0.67
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.22 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Internal | 105.71 | 1.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.96 | P11:18:ITCM:EMERYGT2:1 | External | 125.97 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03175 | 100.22 | 94508: 523315 RB-S&S 3 115 523318 DUMAS_19ST 3 115 1 523304 MOORE_W 3 115 523315 RB-S&S 3 115 1 523309 MOORE_CNTY 6 230 523323 MCDOWELL 6 230 1 | Internal | 100.03 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.54 | 620223 HOOT LK7 115 620324 HOOTLK3G 13.8 1: 620223 HOOT LK7 115 620324 HOOTLK3G 13.8 1 | External | 115.48 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.00089 | 102.13 | P23:500:EMI:ABF_MCKNT-A | External | 102.13 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00034 | 115.32 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 115.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00106 | 112.46 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 112.38 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00034 | 105.94 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 105.89 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.13 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 112.14 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 100.88 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 101.77 | P23:345:AMMO::BLAND:V23 | External | 100.97 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.01 | P23:345:GRE:CHL 304JB22 | External | 113.96 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00033 | 139.19 | P12:161:ALTW:AUTO-SINGLE:JASPER5:LAUREL_5:1 | External | 139.13 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.7 | P42:345:OKGE:SB_BOER7304 | Internal | 106.67 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 101.82 | P23:345:AMMO::BLAND:V21 | External | 101.02 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06914 | 107.75 | P44:345:OPPD:S3458-HOL&R1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00391 | 106.3 | P23:345:ALTW:MITCHLCO:1130 | External | 106.18 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.27 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 134.28 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 118.37 | 601029 LKFLDXL3 345 615040 GRE-LKFDGEN3 345 Z: 601029 LKFLDXL3 345 615040 GRE-LKFDGEN3 345 Z | External | 118.37 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 128.87 | P13:18-161:ALTW:AUTO-SINGLE:MGSCT1:M-TOWN5:1 | External | 128.87 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 121.29 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 121.27 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01331 | 131.39 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 130.62 | 0.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00082 | 136.18 | P23:345:AMMO::ZACHARY:2 | External | 136.07 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01313 | 127.82 | P23:345:ATC:NORTHMADISON:6037-S | External | 127.69 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 108.39 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 108.35 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 148.61 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 148.5 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 117.87 | 104522: 541199 ST JOE 3 345 997776 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 997783 ST. JOSEPH33 161 33 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 115.94 | 1.93
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00072 | 127.82 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 127.7 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00147 | 140.61 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 140.48 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06915 | 107.88 | 92687: 514704 MILLERT4 138 514802 SOONER 4 138 1 514707 PERRY 4 138 514802 SOONER 4 138 1 514798 SNRPMPT4 138 514802 SOONER 4 138 1 514802 SOONER 4 138 515447 MORISNT4 138 1 514802 SOONER 4 138 514805 SOONER1G 22.0 1 514802 SOONER 4 138 998311 SOONER5 138 1 514802 SOONER 4 138 998319 SOONER5 138 1 514802 SOONER 4 138 998316 SOONER5 138 1 | Internal | 106.51 | 1.37
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | 501813 G3MADISN 22 500770 RODEMR 6 230 1: 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.06 | P12:HV:EES::TURK 4%:1(1) | External | 124.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.09 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 126.27 | -0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 102.39 | 300041 7FRANKS 345 344327 7LOOSECRK 345 1: 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | External | 101.57 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.61 | P41:345:AEP,CLEC::DOLHILL7::BUS:::: | External | 100.56 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00082 | 136.18 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 136.07 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.8 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | External | 118.86 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.85 | 104744: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 127.09 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00218 | 111.13 | P12:161:WAUW:# 3102 #: TI IN MT. TI-TT-SH2 & TT-RY-HV | External | 111.04 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.55 | P22:345:OPPD:S3458 NEBCTY1G | External | 129.55 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.74 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 120.74 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00162 | 109.92 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 109.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 118.8 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 118.86 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 134.61 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00021 | 158.76 | P13:69-161:ALTW:AUTO-SINGLE:PARNEL8:PARNEL5:1 | External | 158.76 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 125.74 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 125.61 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 108.1 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 109.16 | -1.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00565 | 105.74 | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | External | 105.55 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 4e-05 | 105.9 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 105.88 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00131 | 105.49 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 105.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.98 | P11:24:CLEC::G1DOLHIL:1 | External | 100.96 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 108.47 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 108.44 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00144 | 103.58 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 103.62 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 115.69 | P11:115:XEL:HBR #6 7 8 | External | 115.65 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 105.11 | P46:345:GRDA:GRDA CB400T | External | 105.08 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00032 | 102.13 | P23:345:ALTW:MITCHLCO:1130 | External | 101.98 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 115.59 | 104645: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 115.61 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 3e-05 | 118.41 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 118.38 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 6e-05 | 103.06 | Base Case | External | 103.06 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 100.3 | 344154 7BLAND 345 344224 7CALAWY 1 345 1: 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 100.3 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.39 | 92337: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 106.33 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 117.51 | P23:345:ALTW:MITCHLCO:1140 | External | 117.39 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00062 | 165.06 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 164.99 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.92 | P22:345:AMMO::RUSHISLAND:1 | External | 104.74 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 106.73 | P11:345:AMMO::RUSHISLAND:U2 | External | 106.61 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 141.24 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 141.22 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01031 | 114.51 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External | 114.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.45 | P11:230-22:CLEC::RODEMR 6:1(2) | External | 100.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 113.47 | P11:115:XEL:HBR #6 7 8 | External | 113.42 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.84 | P11:22:CLEC::G3MADISN:1 | External | 123.81 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.6 | 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1: 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1 | External | 125.62 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01323 | 122.62 | 635700 SYCAMOR3 345 3WXFMR DAG9T1 1: 635700 SYCAMOR3 345 997479 DAG9T1 161 1 635701 SYCAMOR5 161 997479 DAG9T1 161 1 635706 SYCA1XT9 13.8 997479 DAG9T1 161 1 635700 SYCAMOR3 345 997486 DAG9T1 161 1 635701 SYCAMOR5 161 997486 DAG9T1 161 1 635706 SYCA1XT9 13.8 997486 DAG9T1 161 1 | External | 122.49 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01151 | 118.76 | P23:345:MEC:KOSSUTH 904 | External | 118.66 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 4e-05 | 100.74 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 100.74 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 115.32 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 115.26 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00053 | 147.45 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 147.42 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00018 | 144.35 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:DENMARK5:1 | External | 144.35 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00126 | 122.5 | P23:345:ITCM:HCKRYCK:FUT3 | External | 121.95 | 0.55
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0005 | 120.24 | P12:161:ALTW:AUTO-SINGLE:DENMARK5:BRLGTN5:1 | External | 120.24 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00215 | 118.71 | P13:161:CIPCO:DUNDEE 5 T3:IA-NE | External | 118.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00427 | 105.79 | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | External | 105.69 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00035 | 191.08 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 191.09 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00062 | 148.41 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 148.33 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00425 | 106.86 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 106.81 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.95 | P11:HV:EES::1GYP_U4 G1:1 | External | 100.93 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.71 | 92354: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 126.94 | -0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00323 | 109.26 | 921960: 541400 EASTOWN7 345 997758 EASTOWNE11 161 11 541400 EASTOWN7 345 997765 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | External | 109.13 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01177 | 126.57 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 126.47 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00053 | 128.16 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 128.05 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00176 | 117.05 | P23:345:AMMO::ZACHARY:2 | External | 116.94 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01085 | 116.78 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 116.24 | 0.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05992 | 103.85 | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 102.31 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 123.71 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 123.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 127 | P23:345:ITCM:HCKRYCK:FUT3 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 3e-05 | 102.1 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 102.1 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.38 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 112.39 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00035 | 100.98 | P12:345:MEC:WALCOTT-SUB 56 + SUB 56 9T1 | External | 100.93 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00204 | 109.43 | P23:345:MEC:NORWALK 901 | External | 109.32 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00019 | 158.27 | P12:161:ALTW:AUTO-SINGLE:DYSART5:VINTON5:1 | External | 158.23 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0028 | 111.06 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External | 110.97 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.22 | P23:345:MEC:TIFFIN 944 | External | 116.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00062 | 134.62 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 134.55 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0014 | 105 | 636050 WRIGHT 5 161 636051 WRIGHT 8 69 1: 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | External | 104.9 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 117.01 | 631110 WAPELLO5 161 631112 APANOSE5 161 1: 631110 WAPELLO5 161 631112 APANOSE5 161 1 | External | 116.98 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00062 | 165.09 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 165.01 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 103.12 | P11:161:ITCM:MGS CT2:2C | External | 103.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00118 | 103.24 | P42:345:OPPD-MEC:S3451-RAUN&T4 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00059 | 125.08 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 125 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15838 | 133.59 | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | Internal | 132.47 | 1.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00341 | 101.75 | 84399: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 101.66 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.47 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1 | External | 116.38 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.22 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 103.22 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.41 | P11:HV:EES::PIRKEY 1:1 | External | 100.29 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06926 | 112.09 | P12:115:MKEC:MEDICINELODGE-SHOOTINGSTARTAP:: | Internal | 110.59 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06914 | 107.67 | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | Internal | 106.08 | 1.59
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.3 | 601029 LKFLDXL3 345 615040 GRE-LKFDGEN3 345 Z: 601029 LKFLDXL3 345 615040 GRE-LKFDGEN3 345 Z | External | 130.29 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 6e-05 | 150.85 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9: 601044 BRIGGS RD 3 345 997642 10008630_001 161 9 601043 BRIGGS RD 5 161 997642 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997642 10008630_001 161 9 601044 BRIGGS RD 3 345 997649 10008630_001 161 9 601043 BRIGGS RD 5 161 997649 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997649 10008630_001 161 9 601044 BRIGGS RD 3 345 997645 10008630_001 161 9 601043 BRIGGS RD 5 161 997645 10008630_001 161 9 605783 BRIGGS RD 9 34.5 997645 10008630_001 161 9 | External | 150.79 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.0038 | 113.61 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 113.4 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00059 | 113.77 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 113.87 | -0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00215 | 111.44 | P12:161:WAPA-ALTW:AUTO-SINGLE:ANTATP5:ANITA5:1 | External | 111.42 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00065 | 154.55 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 154.48 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 130.33 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:DENMARK5:1 | External | 130.3 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.86 | P11:230-22-18:EES:HOOKER_E | External | 116.85 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.66 | 92464: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00135 | 101.97 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.35 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 110.33 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00037 | 212.03 | P13:115-161:ALTW:AUTO-SINGLE:STONPT7:STONPT5:1 | External | 211.98 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00098 | 116.32 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 116.28 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.86 | 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1: 631047 LIME CK L1 5 161 631220 CLKREACT5 161 1 | External | 100.88 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00058 | 138.28 | P23:345:ITCM:HCKRYCK:FUT3 | External | 138.15 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.0003 | 101.31 | P12:500:LAGN:BC2:WEB:1 | External | 101.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 235.56 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 235.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00054 | 106.58 | P23:345:ALTW:MITCHLCO:1160 | External | 106.52 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.45 | P22:EHV:EES::8COTNWOOD1! | Internal | 105.95 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00049 | 141.16 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 141.05 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 1 | 500 | 500 | 0.0004 | 108.42 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997578 345-161 161 2 615307 GRE-PL VLLY5 161 997578 345-161 161 2 615309 GRE-PL VLL2T 13.8 997578 345-161 161 2 615306 GRE-PL VLLY3 345 997584 345-161 161 2 615307 GRE-PL VLLY5 161 997584 345-161 161 2 615309 GRE-PL VLL2T 13.8 997584 345-161 161 2 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 108.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00204 | 108.33 | P23:345:MEC:SYCAMORE 905 | External | 108.14 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.14 | 300026 1NDWYG2 13.8 300104 5NODWAY 161 2: 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 109.14 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00128 | 110.3 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External | 110.19 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.92 | P13:138-24:AEPW:TURK 4 | External | 110.86 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00026 | 101.71 | P23:345:AMMO::BLAND:V21 | External | 100.91 | 0.8
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.68 | P13:138-24:AEPW:PIRKEY 4 | External | 108.6 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00193 | 101.8 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 101.33 | 0.47
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00057 | 109.34 | P13:161-345:ALTW:AUTO-SINGLE:HUNTLEY5:HUNTLEY3:1 | External | 109.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00062 | 118.76 | 82356: 646258 S1258 5 161 646263 S1263 5 161 1 646258 S1258 5 161 646366 S1366 5 161 1 646258 S1258 5 161 645113 NBHST1 9 4.20 1 646258 S1258 5 161 645114 NBHST2 9 4.20 1 646258 S1258 5 161 645115 NBHST3 9 4.20 1 646258 S1258 5 161 645116 NBHST4 9 4.20 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 118.77 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00489 | 105.91 | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | External | 105.71 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00225 | 105.68 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 105.55 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 115.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | External | 115.6 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 142.71 | 630963 TIMBERCREEK8 69 631082 TIMBRCK5 161 1: 630963 TIMBERCREEK8 69.0 631082 TIMBRCK5 161 1 | External | 142.73 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.39 | P22:345:AMMO::LABADIE:1 | External | 123.41 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00014 | 107.66 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External | 107.56 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 120.31 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 120.26 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 135.33 | P23:345:ALTW:MITCHLCO:1140 | External | 135.06 | 0.27
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00267 | 120.24 | P23:345:MEC:LOUISA 954 | External | 120.23 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.44 | P11:345:MEC-OPPD:NEBRASKA CITY 2 | External | 129.44 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.00322 | 134.42 | P23:345:MEC:SYCAMORE 905 | External | 134.23 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0002 | 120.58 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 120.52 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.79 | P23:345:GRE:CHL 304JB22 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.5 | P11:345:MEC:GDMEC CT1 | External | 130.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.002 | 105.61 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 105.46 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00069 | 100.9 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 100.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0007 | 100.41 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 100.34 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 121.32 | 104647: 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 2 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 121.33 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.37 | 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z: 345989 7RACCOON_CRK 345 348493 7XENIA 345 Z | External | 109.32 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00341 | 101.75 | 104640: 541205 BLSPE 5 161 541226 GRAINVL5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | External | 101.66 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 132.26 | 104651: 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 132.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620263 FORMN 7 115 997497 230/115 115 1 | 112 | 132 | 0.0006 | 101.02 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External | 100.99 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00117 | 136.87 | 105985: 656191 HAMPTON5 161 656207 HAMPTONTAP5 161 1 656201 SHEFFLD5 161 656207 HAMPTONTAP5 161 1 636230 FRANKLN5 161 656207 HAMPTONTAP5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.18 | P12:HV:EES::PIRKEY 4:1 | External | 100.09 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01079 | 117.3 | P23:345-161:XEL:ADAMS_I:681_S | External | 117.25 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 110.49 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1:::: | External | 110.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00144 | 128.42 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 128.16 | 0.26
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 106.97 | P22:345:AMMO::LABADIE:1 | External | 107 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00141 | 119.24 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 119.15 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 6e-05 | 105.5 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 105.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00204 | 102.83 | P12:161:MEC:ADAIR-EARLHAM-BOONEVILLE | External | 102.73 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.46 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 124.3 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00071 | 134.22 | P23:345:MEC:LOUISA 924 | External | 134.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00313 | 111.37 | P12:345:AMMO::CALLAWAY:LOOSECREEK:1 | External | 111.26 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01292 | 127.09 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 126.9 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00117 | 136.87 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 136.75 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01067 | 110.48 | P23:345:MEC:LOUISA 964 | External | 110.43 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00034 | 114.67 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 114.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 113.77 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 113.56 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 2e-05 | 118.04 | 631052 LANSING L1 5 161 681523 GENOA 5 161 1: 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | External | 118 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0104 | 114.2 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 114.17 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 3e-05 | 154.47 | 300076 5FAIRPT 161 300039 7FAIRPT 345 3: 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | External | 154.43 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01091 | 118.34 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.2 | 81748: 514861 MUSTANG4 138 515674 MSTNG12G 13.8 1 515673 MSTNG11G 13.8 998205 MSTNG C 13.8 1 515672 MSTNG10G 13.8 998205 MSTNG C 13.8 1 515671 MSTNG 9G 13.8 998206 MSTNG B 13.8 1 515670 MSTNG 8G 13.8 998206 MSTNG B 13.8 1 514860 MSTANG 2 69.0 515668 MSTNG 6G 13.8 1 514860 MSTANG 2 69.0 515669 MSTNG 7G 13.8 1 515673 MSTNG11G 13.8 998213 MSTNG C 13.8 1 515672 MSTNG10G 13.8 998213 MSTNG C 13.8 1 515671 MSTNG 9G 13.8 998214 MSTNG B 13.8 1 515670 MSTNG 8G 13.8 998214 MSTNG B 13.8 1 515673 MSTNG11G 13.8 998210 MSTNG C 13.8 1 515672 MSTNG10G 13.8 998210 MSTNG C 13.8 1 515671 MSTNG 9G 13.8 998211 MSTNG B 13.8 1 515670 MSTNG 8G 13.8 998211 MSTNG B 13.8 1 | Internal | 105.81 | 1.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.17332 | 105.61 | P12:115:MKEC:PRICHARD-SEMCRUDE:: | Internal | 104.52 | 1.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | External | 103.79 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 110.48 | P23:345:ALTW:MITCHLCO:1140 | External | 110.23 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 143.64 | P12:161:MEC-CFU:BLACK HAWK-UNION-BUTLER | External | 143.59 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06918 | 106.16 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | Internal | 104.63 | 1.53
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 113.33 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | External | 113.31 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0109 | 113.46 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 113.36 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 108.84 | P23:345:ALTW:MITCHLCO:1160 | External | 108.75 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00413 | 105.65 | 104660: 543080 HAWTH 2 69.0 548803 SUB F 69.0 1 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.42 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 122.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00225 | 109.34 | P23:345:AMMO::ZACHARY:2 | External | 109.23 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.28 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.29 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0013 | 120.56 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 120.51 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 119.12 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 119.04 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 124.84 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 124.74 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.46 | 104741: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00051 | 119.7 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 119.64 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00015 | 135.8 | P12:161:ALTW-MEC:AUTO-SINGLE:JASPER5:NEANKNY5:1 | External | 135.78 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.36 | 92424: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.32 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.61 | 812121: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 514881 SPRNGCK7 345 587804 G16-100-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.08953 | 103.74 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 103.13 | 0.61
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 2e-05 | 148.68 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 148.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01022 | 113.63 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 113.6 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 128.36 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 128.3 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 120.15 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1) | External | 120.09 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00033 | 100.75 | 636635 OAKGROV3 345 636640 SUB 93 3 345 1: 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | External | 100.7 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00069 | 148.28 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 148.16 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01225 | 138.25 | P23:345:AMMO::ZACHARY:2 | External | 138.16 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00022 | 136.04 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.05 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 106.14 | P12:EHV:EES::WELSH 7:1(1) | External | 106.07 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00112 | 111.89 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997277 S3451 T3 161 1 646251 S1251 5 161 997276 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997277 S3451 T3 161 1 645451 S3451 3 345 997276 S3451 T4 161 1 646251 S1251 5 161 997284 S3451 T3 161 1 646251 S1251 5 161 997283 S3451 T4 161 1 645451 S3451 3 345 997284 S3451 T3 161 1 645451 S3451 3 345 997283 S3451 T4 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External | 111.83 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.27 | P11:HV:EES::JTEC GEN#2 1:2 | External | 100.18 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.92 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 135.04 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 111.17 | P23:345:ALTW:MITCHLCO:1130 | External | 111.13 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00078 | 130.26 | P12:161:MEC:AUTO-SINGLE:SB185:SB1125:1 | External | 130.12 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01034 | 122.04 | P23:345:ALTW:MITCHLCO:1130 | External | 121.95 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00062 | 125.7 | P23:345:MEC:OAK GROVE 904 | External | 125.54 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00021 | 130.59 | P12:230:OTP::BIGSTON4:HANKSON4 | External | 130.45 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00419 | 105.31 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1: 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | External | 105.17 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00126 | 128.21 | P23:345:OPPD:S3451-RAUN&T4 | External | 128.13 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00133 | 106.38 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997661 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 601020 INVRHLS3 345 997668 IVH TR9 115 9 601020 INVRHLS3 345 997664 IVH TR9 115 9 | External | 105.54 | 0.84
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00231 | 143.31 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 143.17 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00214 | 107.47 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 107.4 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00466 | 108.15 | 301342 5BUTLER 161 541240 ADRIAN 5 161 1: 301342 5BUTLER 161 541240 ADRIAN 5 161 1 | External | 108.01 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00391 | 106.84 | P12:345:AMMO::AUDRAIN:SPS:1 | External | 106.71 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00038 | 116.7 | P23:345:MEC:HILLS 9114 | External | 116.64 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01097 | 110.57 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 110.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01088 | 123.41 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 123.31 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 126.31 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 126.22 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00018 | 111.86 | P23:345-161:XEL:ADAMS_I:680_S | External | 111.84 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01225 | 129.9 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 129.85 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00048 | 150.06 | P13:161-345-34:XEL:AUTO-SINGLE:BRIGGSRD5:BRIGGSRD3:BRIGGSRD9:9 | External | 150 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.4 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | Internal | 104.92 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.69 | 104747: 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 126.93 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01207 | 137.98 | P23:345:MEC:MONTEZUMA 902 | External | 137.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.92 | P12:HV:EES::TURK 4%:1(1) | External | 108.85 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 132.97 | 92489: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 132.98 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 101.53 | 345231 5MONTGMRY 161 345941 5WARENTN 161 1: 345231 5MONTGMRY 161 345941 5WARENTN 161 1 | External | 100.71 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00024 | 101.39 | 300591 2BIG CK 69 300059 5BIG CK 161 1: 300591 2BIG CK 69.0 300059 5BIG CK 161 1 | External | 100.57 | 0.82
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.6 | P11:345:OPPD:NEBCTY1G | External | 129.6 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 126.4 | P13:18-161:ALTW:AUTO-SINGLE:MGSST1:M-TOWN5:1 | External | 126.41 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.01 | P11:HV:EES::1GYP_U4 G1:1 | External | 105.03 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01207 | 134.46 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 134.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.54 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 122.6 | -0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.42 | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | External | 122.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00136 | 103.73 | 71703: 694075 STONE LK B1 345 694076 STONE LK B2 345 Z 694076 STONE LK B2 345 699676 GARDR PK 345 1 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 694076 STONE LK B2 345 694077 STONE LK B3 345 Z 603152 T-CRNRS7 115 699706 WIEN 115 1 | External | 103.48 | 0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0014 | 107.9 | 636050 WRIGHT 5 161 636051 WRIGHT 8 69 1: 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | External | 107.8 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00122 | 104.98 | P12:161:MEC:AUTO-SINGLE:BROOKS5:ADAMSWF5:1 | External | 104.98 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00213 | 105.05 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 104.99 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.6 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 116.47 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00041 | 235.56 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 235.56 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 113.3 | 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1: 601044 BRIGGS RD 3 345 694098 NMA B5 345 345 1 | External | 113.23 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 9e-05 | 145.12 | 631048 EMERY 5 161 636300 FLOYD 5 161 1: 631048 EMERY 5 161 636300 FLOYD 5 161 1 | External | 145.08 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 115.6 | 300070 5CLARK 161 541208 NEVADA 5 161 1: 300070 5CLARK 161 541208 NEVADA 5 161 1 | External | 115.63 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 141.42 | P23:345:MEC:LOUISA 954 | External | 141.39 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00168 | 101.54 | P12:161:MEC:AUTO-SINGLE:HAYES5:POMEROY5:1 | External | 101.5 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00219 | 115.58 | 84403: 300070 5CLARK 161 541208 NEVADA 5 161 1 541307 NEVPLT 2 69.0 541308 NEVADA 2 69.0 1 | External | 115.61 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06914 | 107.75 | P14:345:GMO-OPPD:S3458 REACTOR | Internal | 106.23 | 1.52
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.91 | P11:HV:EES::TURKCOAL:1 | External | 110.85 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.08953 | 105.68 | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | Internal | 105.09 | 0.59
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.61 | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W | External | 135.73 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.49 | P11:345-24:CLEC::DOLHILL7:1 | External | 110.44 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 119.15 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 119.11 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.38 | 620314 BIGSTON4 230 3WXFMR BSP 230 1: 620314 BIGSTON4 230 997504 BSP 230 115 1 620316 BIGSTON9 13.8 997504 BSP 230 115 1 620314 BIGSTON4 230 997512 BSP 230 115 1 620316 BIGSTON9 13.8 997512 BSP 230 115 1 620314 BIGSTON4 230 997505 BSP 230 115 1 620316 BIGSTON9 13.8 997505 BSP 230 115 1 | External | 108.28 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 112.51 | P12:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 112.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 145.37 | P23:345:ALTW:MITCHLCO:1160 | External | 145.34 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00063 | 149.71 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:STONPT5:1 | External | 149.64 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 6e-05 | 149.47 | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1: 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | External | 149.47 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.62 | P12:138:AEPW:ARSHILL4:STLGENS4 | External | 116.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00138 | 115.17 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.04 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.1 | 344886 7LABADIE3 345 344896 1LAB G3 20 1: 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00214 | 117.53 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 117.39 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00041 | 119.73 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 119.65 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00697 | 116.04 | P23:345:MEC:WALCOTT 934 | External | 116 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.22 | 336250 69MILE% 230 336252 1NMIL U5! 26 1: 336250 69MILE% 230 336252 1NMIL U5! 26.0 1 | Internal | 105.71 | 1.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00057 | 140.19 | P12:161:ALTW:AUTO-SINGLE:POWESHK5:REASNOR5:1 | External | 140.1 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 120.37 | 631084 VIELE 5 161 630013 VIELE 8 69 1: 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | External | 120.26 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 124.38 | P11:230-22-18:EES:HOOKER_E | External | 124.36 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.0016 | 119.55 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 119.66 | -0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00024 | 122.98 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 122.89 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00039 | 139.65 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 139.59 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.52 | P11:115:XEL:AUTO-SINGLE:FIBROMN7:1 | External | 116.42 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01281 | 130.54 | P23:345:ALTW:MITCHLCO:1160 | External | 130.37 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 1e-05 | 120.39 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.38 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01207 | 134.46 | P23:345:MEC:MONTEZUMA 902 | External | 134.41 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 130.32 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 130.26 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01022 | 115.07 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 114.99 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00054 | 105.78 | P23:345:ALTW:MITCHLCO:1140 | External | 105.71 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00042 | 131.74 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 131.69 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01622 | 128.07 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 127.88 | 0.19
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 116.77 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 116.74 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 115.48 | 636235 WALL LK5 161 636236 WALL LK8 69 1: 636235 WALL LK5 161 636236 WALL LK8 69.0 1 | External | 115.38 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.66 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT | External | 116.62 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 102.53 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.47 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0108 | 110.5 | 635650 SE POLK 3 345 635651 SE POLK 5 161 1: 635650 SE POLK 3 345 635651 SE POLK 5 161 1 | External | 110.45 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.84 | P12:HV:EES::PIRKEY 4:1 | External | 110.76 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.63 | 601010 MNTCELO3 345 600005 MNTCE31G 22 1: 601010 MNTCELO3 345 600005 MNTCE31G 22.0 1 | External | 114.51 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 136.08 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 135.94 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00313 | 111.37 | 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 | External | 111.26 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00063 | 153.82 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 153.73 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 131.69 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 130.7 | 0.99
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01031 | 121.71 | P12:345:MEC:TIFFIN-ARNOLD | External | 121.62 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0009 | 127.02 | P12:161:UMZC:# 2458 #: IN IA. HAMPTON THREE TERMINAL FAULT | External | 126.91 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00392 | 108.58 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 108.43 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.85 | 92359: 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 127.09 | -0.24
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0107 | 115.44 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 115.33 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 111.26 | P11:161:ITCM:MGS CT1:1C | External | 111.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.36 | 104750: 640139 COOPER 3 345 640009 COOPER1G 22.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.31 | P13:161-22:AEPW:FLINTCR5 | External | 100.24 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00153 | 111.31 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 111.21 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00127 | 103.65 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 103.57 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00063 | 124.07 | P12:345:AMIL-MEC::OAKGROVE:SANDBURG:1 | External | 123.96 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 133.98 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1 | External | 134.06 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00021 | 107.1 | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | External | 107.1 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00025 | 103.11 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 103.11 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 135.61 | P11:0:XEL:AUTO-SINGLE:J278PVSW1:W | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 117.87 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.51 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 116.45 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01225 | 134.43 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 134.32 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0114 | 116.2 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 115.98 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.82 | 92345: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 127.04 | -0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00035 | 191.08 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 191.09 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 128.33 | P23:345:ALTW:MITCHLCO:1150 | External | 128.22 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00146 | 116.96 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 116.92 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0023 | 131.91 | 84408: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541308 NEVADA 2 69.0 541309 METZ 2 69.0 1 | External | 131.98 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 102.51 | P12:345:AMMO::LOOSECREEK:FRANKS:1 | External | 101.68 | 0.83
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.6 | 501801 G1DOLHIL 24 500250 DOLHILL7 345 1: 501801 G1DOLHIL 24.0 500250 DOLHILL7 345 1 | External | 123.55 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 5e-05 | 116.37 | P12:115:XEL:AUTO-SINGLE:MAYNARD7:KERKHOVENTP7:1 | External | 116.24 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.85 | P12:500:EES:STL500:OUACHI:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.01229 | 101.82 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:GDMEC:1 | External | 101.72 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0011 | 150.9 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 150.75 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00016 | 103.29 | P12:161:MEC:AUTO-SINGLE:UNIONTP5:BUTLER5:1 | External | 103.25 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 111.23 | P23:345:ALTW:MITCHLCO:1160 | External | 110.9 | 0.33
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 121.29 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 121.27 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00078 | 137.3 | P23:345:AMIL::SANDBURG:1 | External | 137.1 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01093 | 111.83 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 111.74 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 122.08 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 122.06 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00032 | 101.98 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 101.84 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 5e-05 | 105.8 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:APANOSE5:1 | External | 105.79 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.69 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | External | 122.66 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00547 | 115.19 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 115.01 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00153 | 113.46 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 113.54 | -0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01027 | 117.51 | P23:345:MEC:MORGANV FUT2:IA-EC | External | 117.4 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01085 | 121.91 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 121.48 | 0.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 251 | 251 | 4e-05 | 103.46 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.46 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01225 | 134.43 | P23:345:AMMO::ZACHARY:2 | External | 134.32 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 128.4 | P11:345:MEC:GDMEC ST | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.17683 | 100.54 | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.19 | P23:345:ITCM:HCKRYCK:FUT3 | External | 135.06 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 128.77 | P13:13-161:ALTW:AUTO-SINGLE:SUTHLCT3:M-TOWN5:1 | External | 128.78 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01082 | 110.85 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 110.73 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 140.85 | P13:115-161:ALTW:AUTO-SINGLE:ECALMS7:ECALMS5:1 | External | 140.83 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00309 | 101.5 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 101.42 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 105.51 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 105.5 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00069 | 135.15 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 135.09 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00075 | 125.84 | P23:345:AMIL::HERLEMAN:3 | External | 125.77 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.8 | P12:161:ALTW:AUTO-SINGLE:MPWSPLIT:NEWPORT5:1 | External | 105.81 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00361 | 126.24 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External | 126.12 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.92 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1 | External | 127.17 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.67 | P13:230,22:CLEC::G3MADISN::1 | Internal | 106.13 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.47 | 657700 PILSBRY4 230 657701 BARNES 4 230 1: 657700 PILSBRY4 230 657701 BARNES 4 230 1 | External | 116.38 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00069 | 125.61 | 631084 VIELE 5 161 630013 VIELE 8 69 1: 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | External | 125.47 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00054 | 138.71 | P12:161:MEC:AUTO-SINGLE:UNIONTP5:BUTLER5:1 | External | 138.64 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00266 | 108.3 | P12:161:KCPL:AECINORTON-KCPLNORTON-MARSHALLJCT | External | 108.2 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01225 | 129.9 | P23:345:AMMO::ZACHARY:2 | External | 129.85 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.04 | P11:HV:EES::TURKCOAL:1 | External | 124.95 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 124.75 | 300003 1THLG3 24 300049 7THOMHL 345 1: 300003 1THLG3 24.0 300049 7THOMHL 345 1 | External | 124.63 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.1 | P41:345:AEP,CLEC::DOLHILL7::BUS:::: | Internal | 106.68 | 1.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.58 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 101.48 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00217 | 116.32 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 116.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00435 | 104.59 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 104.49 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00119 | 113.77 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 113.56 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 110.56 | 620238 WINGER 7 115 3WXFMR WINGER 1: 620238 WINGER 7 115 997512 WINGER 69.0 1 657805 WINGER 8 69.0 997512 WINGER 69.0 1 620138 WINGER 9 41.6 997512 WINGER 69.0 1 620238 WINGER 7 115 997519 WINGER 69.0 1 657805 WINGER 8 69.0 997519 WINGER 69.0 1 620138 WINGER 9 41.6 997519 WINGER 69.0 1 | External | 110.59 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06898 | 107.06 | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | Internal | 105.56 | 1.5
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.18 | P13:138-24:AEPW:TURK 4 | Internal | 105.7 | 1.48
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 132.87 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1 | External | 133 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.26 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | External | 116.28 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 107.96 | 81816: 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | External | 107.91 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 4e-05 | 101.26 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.28 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 111.09 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 111.06 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00024 | 102.17 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 102.15 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 106.62 | P21:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1 | External | 106.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.88 | 92474: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 127.1 | -0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 102.49 | 104732: 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 102.49 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.47 | P12:HV:EES::PIRKEY 4:1 | External | 110.43 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01088 | 118.36 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 118.25 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00011 | 135.61 | 105835: 652520 OAHE 7 115 652559 OAHE 1G 13.8 1 587764 G16-094-TAP 230 652519 OAHE 4 230 1 652507 FTTHOMP4 230 652519 OAHE 4 230 2 652507 FTTHOMP4 230 652519 OAHE 4 230 3 652507 FTTHOMP4 230 652519 OAHE 4 230 4 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 652519 OAHE 4 230 659188 PHILIP_T-BE4 230 1 652519 OAHE 4 230 652556 OAHE2-3G 13.8 1 652519 OAHE 4 230 652557 OAHE4-5G 13.8 1 652519 OAHE 4 230 652558 OAHE6-7G 13.8 1 652519 OAHE 4 230 997156 OA NO. 5 115 1 652519 OAHE 4 230 997155 OA NO. 6 115 1 652489 PIERRE 7 115 652600 ASH TAP 115 1 652520 OAHE 7 115 652600 ASH TAP 115 1 652600 ASH TAP 115 658120 GARFLD 7 115 1 652476 EAGLEBT7 115 652520 OAHE 7 115 1 652491 IRVSIMM7 115 652520 OAHE 7 115 1 652520 OAHE 7 115 997156 OA NO. 5 115 1 652520 OAHE 7 115 997155 OA NO. 6 115 1 652589 OAHE 9 13.8 997156 OA NO. 5 115 1 652507 FTTHOMP4 230 652519 OAHE 4 230 1 652519 OAHE 4 230 997163 OA NO. 5 115 1 652519 OAHE 4 230 997162 OA NO. 6 115 1 652520 OAHE 7 115 997163 OA NO. 5 115 1 652520 OAHE 7 115 997162 OA NO. 6 115 1 652589 OAHE 9 13.8 997163 OA NO. 5 115 1 652519 OAHE 4 230 997154 OA NO. 5 115 1 652519 OAHE 4 230 997153 OA NO. 6 115 1 652520 OAHE 7 115 997154 OA NO. 5 115 1 652520 OAHE 7 115 997153 OA NO. 6 115 1 652589 OAHE 9 13.8 997154 OA NO. 5 115 1 | External | 135.73 | -0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01116 | 118.67 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 118.62 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.16061 | 103.89 | P12:115:MKEC:SAINTJOHN-SAINTJOHN(MIDWEST):: | Internal | 102.89 | 1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00576 | 115.18 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 115.04 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00225 | 109.34 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 109.23 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 119.11 | 601011 SHERCO 3 345 600000 SHERC31G 24 1: 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | External | 119.1 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 110.94 | Base Case | External | 110.84 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 110.67 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 110.65 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 126.32 | P11:18:ALTW:AUTO-SINGLE:PRCRK4G:4 | External | 126.28 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 122 | P12:161:MPW-MEC-ITC-CIPCO::NEWPORT5:MPWSPLIT:DENMARK5:1 | External | 121.97 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.87 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 124.79 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00059 | 137.75 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 137.7 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00053 | 123.52 | P23:345-161:XEL:ADAMS_I:680_S | External | 123.47 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01031 | 114.51 | P23:345:MEC:TIFFIN 954 | External | 114.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05892 | 102.07 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 100.64 | 1.43
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00011 | 104.43 | 338170 5JONESBORO! 161 505418 JONESBO5 161 1: 338170 5JONESBORO! 161 505418 JONESBO5 161 1 | External | 104.42 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.3 | P11:HV:EES::FLINTCR1:1 | External | 105.25 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.48 | 92468: 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 100.33 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 135.67 | 82356: 646258 S1258 5 161 646263 S1263 5 161 1 646258 S1258 5 161 646366 S1366 5 161 1 646258 S1258 5 161 645113 NBHST1 9 4.20 1 646258 S1258 5 161 645114 NBHST2 9 4.20 1 646258 S1258 5 161 645115 NBHST3 9 4.20 1 646258 S1258 5 161 645116 NBHST4 9 4.20 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 135.68 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00509 | 102.49 | 69840: 270700 CORDOVA ; B 345 270867 QUAD 8-10 345 1 270867 QUAD 8-10 345 636605 MECCORD3 345 1 | External | 102.45 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.17 | P11:24:AEPW:TURKCOAL | Internal | 105.66 | 1.51
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00057 | 119.11 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 119.03 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 117.73 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 117.73 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 133.94 | 601003 PR ISLD3 345 600003 PR IS31G 20 2: 601003 PR ISLD3 345 600003 PR IS31G 20.0 2 | External | 134.01 | -0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.31 | P13:13-115:ALTW:AUTO-SINGLE:SUTHLCT1:M-TOWN7:1 | External | 135.31 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 601055 SCOTTCO3 345 997640 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.00283 | 110.71 | P23:345:XEL:8M57 SCO | External | 110.58 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 106.74 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | Internal | 105.21 | 1.53
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01102 | 118.47 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 118.42 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00077 | 130.33 | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1: 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | External | 130.29 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 140.54 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 140.48 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00034 | 100.41 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 100.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 103.39 | 657756 SQBUTTE4 230 657848 YNG2 4 230 1: 657756 SQBUTTE4 230 657848 YNG2 4 230 1 | External | 103.38 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.94 | P11:18:ITCM:EMERYGT1:1 | External | 125.95 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 124.78 | P12:HV:EES::PIRKEY 4:1 | External | 124.7 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00049 | 134.89 | P12:115:XEL:AUTO-SINGLE:WILOWRV7:THREELAKES7:1 | External | 134.85 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01034 | 117.55 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 117.43 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00218 | 160.18 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 159.76 | 0.42
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 106.51 | P12:345:MEC:TIFFIN-ARNOLD | External | 106.43 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 100.91 | P23:345:AMMO::BLAND:V15 | External | 100.21 | 0.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 101.02 | P23:345:AMMO::BLAND:V15 | External | 100.32 | 0.7
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00018 | 140.22 | P23:345:AMMO::ZACHARY:2 | External | 140.2 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01314 | 130.19 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 130.05 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.85 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 109.79 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 119.31 | P13:69-161:ALTW:AUTO-SINGLE:BRLGTN18:BRLGTN5:1 | External | 119.22 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00048 | 116.51 | 92723: 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 116.52 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.29 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 101.24 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01207 | 127.94 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 127.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 3e-05 | 116.51 | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | External | 116.45 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00044 | 102.22 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External | 102.02 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0009 | 127.02 | P12:161:MEC-CBPC:FRANKLIN-HAMPTON-SHEFFIELD | External | 126.91 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 112.22 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 112.21 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00302 | 100.53 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 100.46 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00302 | 101.85 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 101.76 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00217 | 111.06 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | External | 111.19 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.12 | P11:230-22:CLEC::RODEMR 6:1(2) | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.75 | 635000 CBLUFFS3 345 635024 WSEC 4G 26 1: 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | External | 108.65 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00021 | 104.38 | 300626 2CHAMOI 69 300067 5CHAMOI 161 1: 300626 2CHAMOI 69.0 300067 5CHAMOI 161 1 | External | 104.41 | -0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.26 | P12:345:XEL:AUTO-SINGLE:HMPTCNR3:GRE-CHUBLAK3:1 | External | 101.26 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.00093 | 101.69 | 335836 8MCKNIGHT% 500 336562 8FRANKLIN% 500 1: 335836 8MCKNIGHT% 500 336562 8FRANKLIN% 500 1 | External | 101.67 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00027 | 103.92 | 300060 5BIGSPG 161 300067 5CHAMOI 161 1: 300060 5BIGSPG 161 300067 5CHAMOI 161 1 | External | 103.03 | 0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00094 | 101.33 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 101.27 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.11 | 92360: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 134.25 | -0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 115.94 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 115.9 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00994 | 111.07 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997279 S3456 T4 161 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 645456 S3456 3 345 997270 S3456 T4 161 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 111.05 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00065 | 121.25 | 633261 KPECKTP5 161 636673 SB 112 5 161 1: 633261 KPECKTP5 161 636673 SB 112 5 161 1 | External | 121.15 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00062 | 123.1 | P23:345:MEC:OAK GROVE 903 | External | 123 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0005 | 128.58 | 631024 E CALMS7 115 631095 E CALMS5 161 1: 631024 E CALMS7 115 631095 E CALMS5 161 1 | External | 128.5 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00565 | 105.75 | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | External | 105.55 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.00151 | 104.59 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 104.54 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00097 | 124.62 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 335360 6CANKTON% 230 500940 WELLS 6 230 1 | External | 124.59 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01088 | 123.41 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.31 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01034 | 123.06 | P23:345:ALTW:MITCHLCO:1160 | External | 122.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 1e-05 | 119.27 | 1061260: 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z 659105 LELAND_O-BE3 345 659424 LO.LS-FT-BE3 345 Z 560074 G16-017-TAP 345 652806 FTTHOM1-LNX3 345 1 | External | 119.22 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 116.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | External | 116.75 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00013 | 170.95 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:WILLIAMSBRG5:1 | External | 170.91 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.93 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z: 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | External | 123.93 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.49 | P23:EHV:EES::8STERLING2%:9 | External | 116.48 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 117.81 | P12:115:XEL-OTP:AUTO-SINGLE:FIBROMN7:GRE-BENSON7:1 | External | 117.71 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.7 | 92336: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541228 WBURGE 5 161 541335 WAFBW_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 106.65 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.64 | P13:345,24:CLEC::G1DOLHILL::1 | Internal | 107.01 | 1.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01624 | 128.18 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 127.98 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 131.69 | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 130.7 | 0.99
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.08908 | 145.6 | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | Internal | 144.02 | 1.58
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01073 | 110.21 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 110.14 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.03 | P11:24:AEPW:PIRKEY 1 | External | 124.9 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00069 | 100.9 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 100.86 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523961 POTTER_CO 7 345 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 102.12 | P12:345:OKGE:BKRBKR429 | Internal | 102.02 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.8 | P12:161:MPW-MEC-ITC-CIPCO::NEWPORT5:MPWSPLIT:DENMARK5:1 | External | 105.81 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.29 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 101.24 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00072 | 140.03 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 139.97 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01329 | 124.39 | 636000 WEBSTER3 345 3WXFMR WEB AB 1: 636000 WEBSTER3 345 997477 WEB AB 161 1 636001 WEBSTER5 161 997477 WEB AB 161 1 636002 WEBS1XT9 13.8 997477 WEB AB 161 1 636000 WEBSTER3 345 997484 WEB AB 161 1 636001 WEBSTER5 161 997484 WEB AB 161 1 636002 WEBS1XT9 13.8 997484 WEB AB 161 1 | External | 124.22 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.71 | P12:500:EES:STL500:OUACHI:1 | Internal | 106.14 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 117.45 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | External | 117.38 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 114.18 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 114.15 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 102.75 | Base Case | External | 102.71 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 118.45 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External | 118.39 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 130.68 | 92357: 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 | External | 130.57 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0006 | 158.01 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 157.94 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01056 | 109.71 | 344000 7ZACKARY 345 344010 5ZACKARY 161 1: 344000 7ZACKARY 345 344010 5ZACKARY 161 1 | External | 109.63 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00022 | 122.08 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 122.06 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.22 | P11:24:AEPW:PIRKEY 1 | External | 110.19 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00341 | 102.5 | P23:161-345:GMO:BLUESPRINGSE_R4-12::DUNCAN-BLUESPRINGSE-BLUESPRINGSW | External | 102.42 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.6 | P23:345:MEC:LOUISA 954 | External | 125.51 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00427 | 105.8 | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | External | 105.66 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01075 | 116.65 | P23:345:AEPW:WELSH CB 10620 NBTB | External | 116.6 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.5 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External | 109.41 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 133.05 | 104746: 532766 JEC N 7 345 532653 JEC U3 26.0 1 532852 JEC 6 230 532651 JEC U1 26.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 | External | 133.06 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 131.21 | P11:13:XEL:AUTO-SINGLE:WHT52G:2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00336 | 109.57 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 109.49 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00028 | 173.26 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:M-TOWN5:1 | External | 173.23 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05815 | 101.49 | 40231: 530580 PAWNEE 2 69.0 530585 BAZINE 2 69.0 1 530585 BAZINE 2 69.0 530700 WALNTCRK3 69.0 1 530580 PAWNEE 2 69.0 530598 CHSPIP 2 69.0 1 | Internal | 100.21 | 1.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 121.52 | P23:345:ATC:NORTHMADISON:6037-S | External | 121.46 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00028 | 100.88 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 100.84 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 110.19 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 110.17 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01281 | 129.97 | P23:345:ALTW:MITCHLCO:1150 | External | 129.76 | 0.21
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.98 | 635200 RAUN 3 345 635213 NEAL 3G 22 1: 635200 RAUN 3 345 635213 NEAL 3G 22.0 1 | External | 129.98 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00035 | 109.87 | P23:345:MEC:SUB 56 934 OR 937 | External | 109.81 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 129.68 | 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2: 636235 WALL LK5 161 636234 CENTURY B2 9 34.5 2 | External | 129.69 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01182 | 135.79 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 135.62 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.76 | P11:24:AEPW:PIRKEY 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.00151 | 104.59 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 104.54 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 5e-05 | 126.26 | 105811: 620263 FORMN 7 115 652438 FORMAN 7 115 1 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1 652438 FORMAN 7 115 652462 ELLIOTT7 115 1 652438 FORMAN 7 115 659172 LUDDEN -CP7 115 1 652438 FORMAN 7 115 997172 FO KY1A 69.0 1 652439 FORMAN 8 69.0 655630 COGSWELL-CP8 69.0 1 652327 FORMAN 9 41.8 652439 FORMAN 8 69.0 1 652439 FORMAN 8 69.0 997172 FO KY1A 69.0 1 652393 FORMAN9 12.5 997172 FO KY1A 69.0 1 620262 GWINNER7 115 620263 FORMN 7 115 1 620263 FORMN 7 115 997498 230/115 115 1 620163 FORMN 9 41.6 997498 230/115 115 1 652438 FORMAN 7 115 997179 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997179 FO KY1A 69.0 1 652393 FORMAN9 12.5 997179 FO KY1A 69.0 1 620263 FORMN 7 115 997505 230/115 115 1 620163 FORMN 9 41.6 997505 230/115 115 1 652438 FORMAN 7 115 997170 FO KY1A 69.0 1 652439 FORMAN 8 69.0 997170 FO KY1A 69.0 1 652393 FORMAN9 12.5 997170 FO KY1A 69.0 1 | External | 126.22 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01182 | 112.48 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 112.45 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.55 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | External | 108.42 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00039 | 109.2 | P22:345:MEC:SUB 92 | External | 109.15 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0028 | 109.14 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | External | 109.05 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01031 | 116.22 | P23:345:MEC:TIFFIN 954 | External | 116.11 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01225 | 134.43 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 134.32 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00201 | 101.89 | 635630 BOONVIL3 345 3WXFMR DEB9T1 1: 635630 BOONVIL3 345 997480 DEB9T1 161 1 635631 BOONVIL5 161 997480 DEB9T1 161 1 635629 BOON1XT9 13.8 997480 DEB9T1 161 1 635630 BOONVIL3 345 997487 DEB9T1 161 1 635631 BOONVIL5 161 997487 DEB9T1 161 1 635629 BOON1XT9 13.8 997487 DEB9T1 161 1 | External | 101.76 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 109.13 | P11:0:MEC:AUTO-SINGLE:MRNGLIGHTW:W | External | 109.14 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00231 | 143.31 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 143.17 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00053 | 101.47 | 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1: 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.46 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00022 | 123.11 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 123.12 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 109.42 | 631081 M-TOWN 5 161 629215 MGS CT2 18 1: 631081 M-TOWN 5 161 629215 MGS CT2 18.0 1 | External | 109.43 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00062 | 165.06 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 164.99 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.15838 | 133.76 | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | Internal | 132.72 | 1.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997521 CHL345-115-1 115 1 | 448 | 448 | 0.00041 | 104.85 | P23:345:XEL:8S51 HMP | External | 104.82 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 103.11 | P11:161:ITCM:MGS CT1:1C | External | 103.12 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.57 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | External | 125.58 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00196 | 100.83 | P11:345:MEC:GDMEC CT2 | External | 100.79 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 8e-05 | 105.22 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 105.2 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.34 | P12:EHV:EES::WELSH 7:1(1) | External | 110.28 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107 | 81816: 512614 GRECCTG_1 20.0 512865 GREC TAP5 345 1 512615 GRECSTG_1 21.0 512865 GREC TAP5 345 1 | Internal | 105.54 | 1.46
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636401 HILLS 5 161 636678 SB 89 5 161 1 | 240 | 240 | 0.00136 | 100.48 | P23:345:MEC:HILLS 9114 | External | 100.44 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 108.57 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 108.51 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 104.8 | P23:HV-EHV:EES::8STERLING2%:4 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 120.76 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 120.65 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.25 | P23:500:EAI:NBF_SAN SOUC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 126.39 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 126.3 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615306 GRE-PL VLLY3 345 997577 345-161 161 1 | 500 | 500 | 0.0004 | 108.42 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 108.41 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00994 | 111.35 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997272 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997267 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997272 S3456 T4 161 1 646206 S1206 5 161 997268 S1206 T1 69.0 1 646206 S1206 5 161 997267 S1206 T2 69.0 1 646206 S1206 5 161 997266 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997268 S1206 T1 69.0 1 645456 S3456 3 345 997279 S3456 T4 161 1 647006 S906 N 8 69.0 997274 S1206 T2 69.0 1 646206 S1206 5 161 997279 S3456 T4 161 1 646206 S1206 5 161 997275 S1206 T1 69.0 1 646206 S1206 5 161 997274 S1206 T2 69.0 1 646206 S1206 5 161 997273 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997275 S1206 T1 69.0 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 111.36 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 118.76 | 601011 SHERCO 3 345 600002 SHERC33G 26 1: 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | External | 118.66 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00036 | 113.13 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 113.07 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 118.05 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 117.95 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 109.06 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 109.01 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00186 | 139.04 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 138.66 | 0.38
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01097 | 110.82 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 110.77 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 127.74 | 344011 7HUGHES 345 344012 7HPW-N 345 1: 344011 7HUGHES 345 344012 7HPW-N 345 1 | External | 127.66 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00135 | 135.38 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 135.2 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0039 | 106.14 | P22:345:AMMO::RUSHISLAND:2 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01074 | 116.22 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 116.19 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0006 | 123.71 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 123.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00061 | 135.81 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.04 | P23:500:LAGN:PD:BC2:XF:FK55687 | Internal
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 107.69 | 300575 2MONTGY 69 300099 5MONTCT 161 1: 300575 2MONTGY 69.0 300099 5MONTCT 161 1 | External | 106.73 | 0.96
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00049 | 128.6 | P23:345:ALTW:MITCHLCO:1160 | External | 128.54 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.6 | 631081 M-TOWN 5 161 629216 MGS ST1 18 1: 631081 M-TOWN 5 161 629216 MGS ST1 18.0 1 | External | 101.62 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00034 | 115.32 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 115.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 108.5 | 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1: 300106 5NOVELY_SW 161 344006 5ADAIR3 161 1 | External | 108.47 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.5 | 635568 S HILLS 3 345 637047 STH HILL WD 345 1: 635568 S HILLS 3 345 637047 STH HILL WD 345 1 | External | 130.49 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 102.04 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.97 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00126 | 110.78 | P23:345:ALTW:MITCHLCO:1150 | External | 110.58 | 0.2
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00295 | 133.76 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 133.59 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.38 | P23:345:ALTW:MITCHLCO:1140 | External | 153.12 | 0.26
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.24 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 116.16 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 180.76 | P11:024:DPC:ALMA2:6 | External | 180.77 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01196 | 128.09 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 127.96 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 123.53 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 123.52 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 117.6 | 104748: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 117.56 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 113.44 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 113.43 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00026 | 100.3 | P12:345:AMMO::CALLAWAY:BLAND:1 | External | 100.3 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00094 | 109.06 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 109.01 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00092 | 127.37 | P12:161:ALTW-WAPA:AUTO-SINGLE:EMERY5:SHEFFLD5:1 | External | 127.29 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00016 | 103.55 | 636230 FRANKLN5 161 636240 BUTLER 5 161 1: 636230 FRANKLN5 161 636240 BUTLER 5 161 1 | External | 103.51 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00027 | 134.66 | P23:345-161:XEL:ADAMS_I:680_S | External | 134.64 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | 1195 | 1195 | 0.00054 | 105.92 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 105.84 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.67 | P11:230-22:CLEC::RODEMR 6:1(2) | Internal | 106.13 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 116.49 | P12:500:EES:STL500:OUACHI:1 | External | 116.48 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01088 | 114.98 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 114.92 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00053 | 135.03 | P23:345:XEL:8S22 WLM | External | 135 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.85 | 631155 CRYSTLK5 161 631220 CLKREACT5 161 1: 631155 CRYSTLK5 161 631220 CLKREACT5 161 1 | External | 108.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00011 | 103.68 | P12:161:EES-EAI:JONSB2:JONSBR:1 | External | 103.67 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00015 | 143.8 | 630902 VINTON 8 69 631087 VINTON 5 161 1: 630902 VINTON 8 69.0 631087 VINTON 5 161 1 | External | 143.78 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00575 | 115.06 | 300071 5CLINTN 161 542969 STILWEL5 161 1: 300071 5CLINTN 161 542969 STILWEL5 161 1 | External | 114.94 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.00953 | 117.41 | P23:345:MEC:ATCHISON CO 903 | External | 117.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 108.14 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 108.14 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.01229 | 101.82 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:GDMEC:1 | External | 101.72 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00034 | 100.41 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 100.36 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01075 | 110.5 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT | External | 110.44 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06909 | 116.33 | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 114.76 | 1.57
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.00125 | 101.83 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 101.6 | 0.23
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 101.18 | P11:18:ITCM:EMERYGT2:1 | External | 101.19 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 108.12 | 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1: 661092 FOXTAIL4 230 661985 FOXTAIL9 34.5 1 | External | 108.03 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 112.98 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1 | External | 112.88 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03247 | 104.09 | 105092: 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | Internal | 104.13 | -0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 110.21 | P11:345:NIPS:RM-U17:17SCHAFER:17 | External | 110.15 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00022 | 153.37 | P23:345:ALTW:MITCHLCO:1130 | External | 153.15 | 0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00285 | 121.08 | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | External | 120.95 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00214 | 107.47 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 107.4 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.28 | P11:345:AMMO::LABADIE:4 | External | 107.19 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01034 | 114.16 | P23:345:ALTW:MITCHLCO:1130 | External | 114.12 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00776 | 120.11 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 120.04 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 533413 CIRCLE 3 115 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14537 | 110.43 | 8646: 533417 EMCPHER3 115 533426 MANVILE3 115 1 533417 EMCPHER3 115 533427 REFINRY3 115 1 533417 EMCPHER3 115 997917 EMCP TX-1 115 1 533417 EMCPHER3 115 997924 EMCP TX-1 115 1 533417 EMCPHER3 115 997920 EMCP TX-1 115 1 | Internal | 109.45 | 0.98
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.85 | 92483: 541176 LAKERD6_1 13.8 541169 LAKERD34 34.5 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 541177 LAKERD7_1 13.8 541169 LAKERD34 34.5 1 541175 LAKERD5_1 13.8 541169 LAKERD34 34.5 1 541172 LAKERD2_1 13.8 541169 LAKERD34 34.5 1 541173 LAKERD3_1 13.8 541169 LAKERD34 34.5 1 541170 LAKERD#4 13.8 541255 LAKE RD5 161 1 541171 LAKERD1_1 13.8 541169 LAKERD34 34.5 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 | External | 134.98 | -0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00045 | 119.42 | P23:345:AMMO::MONTGOMERY:V43 | External | 119.39 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00039 | 114.64 | P23:345:MEC:WALCOTT 914 | External | 114.56 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00025 | 116.18 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 116.14 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 127.06 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 126.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 112.13 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 112.14 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0107 | 118.96 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD | External | 118.9 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.5 | P23:345:OPPD:S3458 NEBCTY1G:LT | External | 129.5 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 140.7 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 140.68 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00011 | 141.94 | P12:161:ALTW:AUTO-SINGLE:JASPER5:LAUREL_5:1 | External | 141.92 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00289 | 119.48 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 119.46 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 130.51 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 130.41 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.04 | 104737: 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 103.03 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01282 | 132.11 | P22:345:XEL:ADAMS 3 N1:MN | External | 131.84 | 0.27
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539643 ROLLHLS3 115 539660 EHALLTP3 115 1 | 73.1 | 73.1 | 0.20789 | 111.13 | P13:115-230:MIDW:RICE COUNTY | Internal | 105.5 | 5.63
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00013 | 108.42 | P23:345:ALTW:MITCHLCO:1130 | External | 108.35 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00045 | 127.79 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 127.8 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 108.09 | P11:22:CLEC:RODEMR1:1 | Internal | 106.45 | 1.64
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00194 | 100.41 | P23:345:ALTW:MITCHLCO:1160 | External | 100.31 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0038 | 118.11 | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | External | 117.37 | 0.74
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.95 | P23:345:XEL:8N17 SHC | External | 117 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00054 | 144.64 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 144.57 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00151 | 100.15 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 100.08 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.0002 | 132.77 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BROWNSV4:1 | External | 132.64 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00058 | 121.68 | P13:161-69:ITCM:CARBIDE5 T1:IA-EC | External | 121.62 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.29 | P11:HV:EES::PIRKEY 1:1 | External | 107.17 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00014 | 121.04 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 121.01 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00025 | 101.67 | P12:161:AMMO::WARRENTON:MONTGOMERY:3 | External | 100.78 | 0.89
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01074 | 109.44 | P11:23:EES-EAI:PLUM17:1 | External | 109.38 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 114.63 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | External | 114.51 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00071 | 122.69 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | External | 122.66 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 100.88 | 620314 BIGSTON4 230 620315 BIGSTN1G 24 1: 620314 BIGSTON4 230 620315 BIGSTN1G 24.0 1 | External | 100.82 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00292 | 103.18 | 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1: 345230 7MONTGMRY 345 345231 5MONTGMRY 161 1 | External | 103.1 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00025 | 107.57 | 300575 2MONTGY 69 300099 5MONTCT 161 1: 300575 2MONTGY 69.0 300099 5MONTCT 161 1 | External | 106.61 | 0.96
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.001 | 139.82 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 139.68 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.42 | P11:24:AEPW:TURKCOAL | External | 100.33 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00267 | 119.26 | P23:345:MEC:HILLS 934 | External | 119.21 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 1e-05 | 116.74 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | External | 116.68 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01281 | 129.33 | P23:345:ALTW:MITCHLCO:1130 | External | 129.16 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0042 | 105.24 | P11:HV:EES::JTEC GEN#2 1:2 | External | 105.06 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.01207 | 127.94 | P23:345:MEC:MONTEZUMA 902 | External | 127.93 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 140.7 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 140.68 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0047 | 106.39 | 92233: 541270 KNOSTER2 69.0 541534 KNOSTERTP 69.0 1 541524 MONSERTP 69.0 541534 KNOSTERTP 69.0 1 541534 KNOSTERTP 69.0 541535 LAMONTETP 69.0 1 541271 SEDN 2 69.0 541535 LAMONTETP 69.0 1 541535 LAMONTETP 69.0 541536 LAMONTE 69.0 1 541335 WAFBW_SW5 161 541337 WAFBE_SW5 161 1 541269 WBURGE 2 69.0 541524 MONSERTP 69.0 1 | External | 106.33 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 134.99 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 134.96 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00105 | 114.13 | P12:161:UMZ:# 5519 #: IN . PROPER N-1 (LINE) FOR 636230-656207-1 | External | 114.02 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 134.88 | 601014 AS KING3 345 600006 KING 31G 20 1: 601014 AS KING3 345 600006 KING 31G 20.0 1 | External | 134.81 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01022 | 115.07 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 114.99 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00151 | 100.15 | P23:345:AMMO::ZACHARY:2 | External | 100.08 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.48 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 106.47 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 7e-05 | 106.48 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 106.47 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 135.23 | 630772 SUTHL CT2 13.5 631004 M-TOWN 7 115 1: 630772 SUTHL CT2 13.5 631004 M-TOWN 7 115 1 | External | 135.22 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.6 | P11:345-24:CLEC::DOLHILL7:1 | External | 123.55 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 532871 CIRCLE 6 230 997920 CIRC TX-1 115 1 | 280 | 308 | 0.14601 | 129.03 | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | Internal | 128.03 | 1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 1e-05 | 120.74 | P13:161-69:EES-EAI:HERGET:AT1 | External | 120.74 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 | 559 | 0.03315 | 106.76 | P12:345:OKGE:BKRBKR429 | Internal | 106.61 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.94 | P11:230-22-18:EES:HOOKER_E | External | 100.8 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.07022 | 114.99 | P42:345:SPS:FINNEY_OR70_19L | Internal | 113.39 | 1.6
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00017 | 134.68 | 92488: 546653 NEARMAN5 161 546723 NM CT4 1 15.0 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.69 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01317 | 122.93 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 122.82 | 0.11
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00092 | 139.38 | P23:345:AMIL::HERLEMAN:1 | External | 139.23 | 0.15
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00149 | 124.54 | P23:345:AEPW:WELSH CB 11680 NBTB | External | 124.51 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.00216 | 102.2 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 102.12 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 0.00122 | 103.34 | P12:161:MEC:AUTO-SINGLE:CLRNDA5:BROOKS5:1 | External | 103.31 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01314 | 130.19 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 130.05 | 0.14
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 615307 GRE-PL VLLY5 161 997577 345-161 161 1 | 500 | 500 | 0.0004 | 110.95 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 110.93 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0008 | 125.63 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00133 | 115.48 | P13:161-69:MEC:AUTO-SINGLE:WALLLK5:WALLLK8:1 | External | 115.38 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0018 | 121.75 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1 | External | 121.69 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01073 | 116.46 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.4 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.0022 | 120.47 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 120.4 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 145.04 | P23:345:ALTW:MITCHLCO:1150 | External | 144.98 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01075 | 116.23 | P23:345:AEPW:WILKES CB 1U70 NBTB | External | 116.18 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00012 | 103.83 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 103.8 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 130.51 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 130.41 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 118.63 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 118.62 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01074 | 116.96 | P13:138-24:AEPW:TURK 4 | External | 116.91 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 107.12 | 344056 7AUDRAIN 345 345992 7SPENCER 345 Z: 344056 7AUDRAIN 345 345992 7SPENCER 345 Z | External | 107.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 110.79 | P23:500:EES-EAI:SANSSU:B3935_3925_3975 | External | 110.71 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00052 | 118.37 | P12:345:XEL-GRE:AUTO-SINGLE:LKFLDXL3:GRE-LKFDGEN3:Z | External | 118.37 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 108.58 | P12:161:AMMO-ITC::APANOSE:ADAIR:1 | External | 108.54 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 153.57 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1 | External | 153.56 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 128.09 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 128.04 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00047 | 117.49 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 117.42 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 130.28 | P23:345:MEC:ROLLING HILLS 906 | External | 130.27 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 131.62 | 71615: 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 694076 STONE LK B2 345 699676 GARDR PK 345 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 | External | 130.85 | 0.77
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00047 | 140.7 | 71593: 603065 CHISAGO7 115 603172 WYOMING7 115 1 603136 HUGO 7 115 603172 WYOMING7 115 1 603065 CHISAGO7 115 605269 LINDSTM7 115 1 605269 LINDSTM7 115 617031 GRE-SHAFER 7 115 1 603197 LAW CRK7 115 617031 GRE-SHAFER 7 115 1 | External | 140.69 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.00807 | 109.26 | P23:345:MEC:LOUISA 964 | External | 109.23 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 127.14 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00189 | 114.04 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 114 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.26 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT | External | 108.22 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 111.13 | 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1: 631085 PARNEL 5 161 629099 PARNEL 9 34.5 1 | External | 111.1 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.82 | 104726: 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 645011 NEBCTY1G 18.0 645111 NBAXT1 9 4.20 1 645011 NEBCTY1G 18.0 645112 NBAXT2 9 4.20 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 127.04 | -0.22
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.85 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | External | 108.86 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01253 | 127.47 | P44:345:OPPD:S3458-HOL&R1 | External | 127.31 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 126.31 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 126.22 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05815 | 101.49 | 40230: 530580 PAWNEE 2 69.0 530585 BAZINE 2 69.0 1 530585 BAZINE 2 69.0 530700 WALNTCRK3 69.0 1 530580 PAWNEE 2 69.0 530598 CHSPIP 2 69.0 1 | Internal | 100.21 | 1.28
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 105.46 | P11:HV:EES::1NM G1:1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.00693 | 112.51 | 636615 SB 56 3 345 636620 WALCOTT3 345 1: 636615 SB 56 3 345 636620 WALCOTT3 345 1 | External | 112.48 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00191 | 100.32 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 100.3 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.00113 | 106.11 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.07 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00068 | 130.36 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 130.26 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.00198 | 109.85 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External | 109.82 | 0.03
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00117 | 136.87 | P12:161:UMZ:# 5519 #: IN . PROPER N-1 (LINE) FOR 636230-656207-1 | External | 136.75 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 112.29 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 112.23 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 4e-05 | 116.57 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 116.57 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01077 | 109.57 | P23:345:AMMO::SPENCERCREEK:V3 | External | 109.48 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00393 | 105.47 | P11:138:AMMO::MERAMEC:4 | External | 105.38 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 2e-05 | 111.08 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 111.07 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.004 | 101.74 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 101.67 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 144.98 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 144.94 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00035 | 134.14 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 133.98 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 1e-05 | 107.82 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1:::: | External | 107.72 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00422 | 105.71 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 105.53 | 0.18
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 111.26 | P11:161:ITCM:MGS CT2:2C | External | 111.27 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00023 | 106.51 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01086 | 116.76 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 116.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.58 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 100.49 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0013 | 108.91 | P11:HV:EES::TURKCOAL:1 | External | 108.83 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00118 | 120.31 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 120.26 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00027 | 173.45 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 173.44 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01086 | 110.5 | 631080 STON PT5 161 631015 STON PT7 115 1: 631080 STON PT5 161 631015 STON PT7 115 1 | External | 110.43 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.00093 | 101.69 | P12:EHV:EES::8MCKNIGHT%:8FRANKLIN%:1 | External | 101.67 | 0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0103 | 120.15 | P23:345:MEC:HILLS 984 | External | 120.09 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 8e-05 | 133.97 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2 | External | 134.06 | -0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01319 | 128.55 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1 | External | 128.45 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 103.95 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 104 | -0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.06917 | 107.62 | P11:138:OKGE:BKRBKR_GSU03 | Internal | 106.08 | 1.54
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00146 | 125.98 | 631081 M-TOWN 5 161 629214 MGS CT1 18 1: 631081 M-TOWN 5 161 629214 MGS CT1 18.0 1 | External | 125.99 | -0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00013 | 170.95 | 631009 NEWHAL5 161 631224 WILLIAMSBRG5 161 1: 631009 NEWHAL5 161 631224 WILLIAMSBRG5 161 1 | External | 170.91 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0007 | 131.63 | 344290 5CARBID T 161 631075 CARBIDE5 161 1: 344290 5CARBID T 161 631075 CARBIDE5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00027 | 141.94 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 141.9 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.01032 | 124.09 | P22:345:XEL:ADAMS 3 N1:MN | External | 123.92 | 0.17
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0104 | 121.32 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 121.23 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0102 | 115.14 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 115.1 | 0.04
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00137 | 100.25 | 84125: 509807 ONETA--7 345 509836 OEC 7 345 1 509807 ONETA--7 345 509836 OEC 7 345 2 509836 OEC 7 345 511938 OECSTM 1 18.0 1 509836 OEC 7 345 511939 OECGT1-1 18.0 1 509836 OEC 7 345 511940 OECGT1-2 18.0 1 509836 OEC 7 345 511941 OECSTM 2 18.0 1 509836 OEC 7 345 511942 OECGT2-1 18.0 1 509836 OEC 7 345 511943 OECGT2-2 18.0 1 | External | 100.16 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 128 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 128.02 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 334070 1G1LEWIS! 22.0 334072 4LEWIS% 138 1 | 290 | 290 | 0.00724 | 102.23 | P11:EHV:EES::1FRNTR 1!:1(1) | External | 102.25 | -0.02
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 101 | 101 | 0.05904 | 104.58 | P12:230:WERE:SUMM-MWE_230:: | Internal | 103.19 | 1.39
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00052 | 129.14 | 105019: 645001 FT CAL1G 22.0 645101 FC1A1 9 4.20 1 645001 FT CAL1G 22.0 645102 FC1A2 9 4.20 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | External | 129.14 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00036 | 100.55 | P21:345:MEC:AUTO-SINGLE:SB563:WALCOTT3:1 | External | 100.5 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.0006 | 123.71 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 123.65 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0102 | 117.43 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 117.35 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 135.06 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 134.98 | 0.08
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00052 | 126.83 | P11:18:XEL:AUTO-SINGLE:FEPCTG:1 | External | 127.08 | -0.25
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.93 | P11:HV:EES::1GOXY U1!:1 | External | 100.8 | 0.13
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.00863 | 114.74 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640277 MOORE 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 640139 COOPER 3 345 997438 COOPER T2 161 1 640139 COOPER 3 345 997437 COOPER T5 161 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | External | 114.68 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00056 | 116.95 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 116.88 | 0.07
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.01027 | 117.21 | P23:345:MEC:MORGANV FUT1:IA-EC | External | 117.11 | 0.1
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00055 | 120.94 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 120.85 | 0.09
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.01377 | 128.78 | 631113 POWESHK5 161 631117 REASNOR5 161 1: 631113 POWESHK5 161 631117 REASNOR5 161 1 | External | 128.62 | 0.16
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00016 | 140.54 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 140.48 | 0.06
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00016 | 109.04 | P23:345:AMIL::HERLEMAN:3 | External | 109.04 | 0
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.00297 | 100.66 | P11:22:CLEC:RODEMR1:1 | External | 100.54 | 0.12
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00035 | 100.98 | P23:345:MEC:SUB 56 934 OR 937 | External | 100.93 | 0.05
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00068 | 123.66 | 501813 G3MADISN 22 500770 RODEMR 6 230 1: 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 123.65 | 0.01
Thermal | 00NR | S2 | 29SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 123.53 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 123.52 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00012 | 165.09 | P23:500:EES-EAI:WH_BLF:B7914 | External | 165.09 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00032 | 118.45 | P23:500:EES-EAI:WH_BLF:B7914 | External | 118.45 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00032 | 111.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 111.37 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00022 | 140.38 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.38 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00032 | 113.91 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.91 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 111.11 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 111.11 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00032 | 113.92 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.92 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 110.66 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 110.66 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 130.68 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 130.67 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00019 | 130.68 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 130.67 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 124.31 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 124.3 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 124.31 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 124.3 | 0.01
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 121.39 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 121.39 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00023 | 143.06 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.06 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 2e-05 | 107.55 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.55 | 0
Thermal | 04HVER | S1 | 20G0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00034 | 124.31 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 124.3 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 100.4 | 81734: 337909 8ANO% 500 515305 FTSMITH8 500 1 515305 FTSMITH8 500 998252 FTSMITH3 161 3 515305 FTSMITH8 500 998251 FTSMTH6 161 6 515305 FTSMITH8 500 998250 FTSMITH4 161 4 515305 FTSMITH8 500 998248 FTSMITH1 345 1 515305 FTSMITH8 500 998260 FTSMITH3 161 3 515305 FTSMITH8 500 998259 FTSMTH6 161 6 515305 FTSMITH8 500 998258 FTSMITH4 161 4 515305 FTSMITH8 500 998256 FTSMITH1 345 1 515305 FTSMITH8 500 998257 FTSMITH3 161 3 515305 FTSMITH8 500 998256 FTSMTH6 161 6 515305 FTSMITH8 500 998255 FTSMITH4 161 4 515305 FTSMITH8 500 998253 FTSMITH1 345 1 | External | 100.4 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.0002 | 126.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 126.9 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.17 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 103.17 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P23:345:MEC:MONTEZUMA 902 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00096 | 121.45 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 121.44 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00015 | 165.63 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 165.63 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00018 | 175.79 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 175.78 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 103.23 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 103.23 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.22 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 103.21 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 100.39 | P42:500:OKGE:SB_FTTH8581 | External | 100.39 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 105.47 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.46 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.09 | P12:161:ALTW:AUTO-SINGLE:OTTUMWA5:LUCAS5:1 | External | 105.09 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00045 | 112.82 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 112.81 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 334217 4MAG AMS 138 334218 4PINTAIL% 138 1 | 112 | 112 | 0.00029 | 100.3 | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 100.29 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.38 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.42 | -0.04
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 104.48 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 104.48 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00045 | 112.82 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 112.81 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.92 | P23:345:MEC:MONTEZUMA 903 | External | 102.92 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 100.02 | Base Case | External | 100.01 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.38 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 216.37 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00023 | 104.05 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.05 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 7e-05 | 115.3 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 115.3 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.6 | P23:345:MEC:HILLS 974 | External | 102.6 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 105.2 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 105.19 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00018 | 175.79 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 175.78 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 104.91 | P13:161-345:ALTW:AUTO-SINGLE:OTTUMWA5:OTTUMWA3:1 | External | 104.91 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 105.47 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 105.46 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00142 | 108.63 | P23:500:EES-EAI:ARK_NU:B5106 | External | 108.63 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 123.65 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:JEFF5:1 | External | 123.66 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00023 | 106.98 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.98 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 101.34 | P23:345:MEC:HILLS 914 | External | 101.33 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 102.03 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 102.03 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.09 | 631115 OTTUMWA5 161 631118 LUCAS 5 161 1: 631115 OTTUMWA5 161 631118 LUCAS 5 161 1 | External | 105.09 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 5e-05 | 117.67 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.67 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.46 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.45 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00054 | 106.88 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 106.87 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.0002 | 100.55 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 100.54 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.38 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 216.37 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00094 | 114.52 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 114.52 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 105.21 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 105.21 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00033 | 101.23 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 101.23 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00463 | 122.43 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 122.43 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00012 | 104.91 | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1: 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | External | 104.91 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.09 | P13:69-161:ALTW:AUTO-SINGLE:LUCAS8:LUCAS5:1 | External | 105.09 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00086 | 104.45 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 104.46 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 105.61 | 631112 APANOSE5 161 630033 APANOSE8 69 1: 631112 APANOSE5 161 630033 APANOSE8 69.0 1 | External | 105.61 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 105.61 | P13:69-161:ALTW:AUTO-SINGLE:APANOSE8:APANOSE5:1 | External | 105.61 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.55 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.55 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00031 | 106.17 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 106.16 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.00151 | 100.39 | P42:500:OKGE:SB_FTTH8585 | External | 100.39 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.46 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.45 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 101.32 | P13:345-161-13:MEC:AUTO-SINGLE:HILLS3:HILLS5:HILL1XT9:1 | External | 101.32 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00094 | 114.52 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 114.52 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.0002 | 129.33 | P23:500:EES-EAI:WH_BLF:B7914 | External | 129.33 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0011 | 103.46 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.45 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.47 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.47 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.97 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 102.97 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 104.01 | P12:161:ALTW-MEC:AUTO-SINGLE:TRICNTYL15:BEACON5:1 | External | 104 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00116 | 103.22 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 103.21 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0001 | 102.97 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 102.97 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 8e-05 | 104.34 | P12:161:ITCM:WAPELLO5 - APANOSE5:IA-SW | External | 104.34 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 216.38 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 216.37 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00051 | 129.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 129.84 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00028 | 123.65 | 631110 WAPELLO5 161 631111 JEFF 5 161 1: 631110 WAPELLO5 161 631111 JEFF 5 161 1 | External | 123.66 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 108.39 | P11:024:DPC:ALMA2:6 | External | 108.38 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.33 | 630036 JEFF 8 69 631111 JEFF 5 161 1: 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | External | 116.33 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 7e-05 | 115.14 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 115.14 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00031 | 106.24 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 106.23 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 5e-05 | 117.24 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.24 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00022 | 126.78 | P13:161-69:ITCM:JEFF 5 T1:IA-SE | External | 126.77 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 108.58 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.58 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00249 | 108.56 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 108.51 | 0.05
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00057 | 108.39 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 108.38 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00086 | 104.45 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 104.46 | -0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00051 | 110.15 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.15 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00096 | 121.45 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 121.44 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00054 | 107.32 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 107.31 | 0.01
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 7e-05 | 101.86 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 101.86 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 4e-05 | 100.81 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.81 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.0002 | 101.04 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 101.04 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 6e-05 | 105.09 | 630044 LUCAS 8 69 631118 LUCAS 5 161 1: 630044 LUCAS 8 69.0 631118 LUCAS 5 161 1 | External | 105.09 | 0
Thermal | 04HVER | S1 | 20SP0 | G04_G056 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00011 | 116.33 | P13:69-161:ALTW:AUTO-SINGLE:JEFF8:JEFF5:1 | External | 116.33 | 0
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.13589 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.08961 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04281 | NConv | 81730: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | P12:345:WERE:N345-AECI_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07461 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.07005 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P12:345:WERE:N345-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.05132 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03707 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03044 | NConv | P23:345:WERE:N345_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:RENO_345-160:: | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06209 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04278 | NConv | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:RENO_345-150:: | NA
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06061 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06062 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.03305 | NConv | P23:345:WERE:N345_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.04837 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.20158 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G04_G056 |  | Non-Converge |  |  | 0.06442 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.05413 | NConv | 20632: 640065 AXTELL 3 345 640312 PAULINE3 345 1 560062 G15088_T 345 640277 MOORE 3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.03106 | NConv | 94070: 533394 CORONAD3 115 533438 WMCPHER3 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.13565 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.03297 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.03106 | NConv | P12:115:WERE:CORO-WMCP_115:: | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.09307 | NConv | 104382: 533438 WMCPHER3 115 533439 WHEATLD3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530620 LYONS 3 115 533439 WHEATLD3 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.03187 | NConv | 81731: 514880 NORTWST7 345 514908 ARCADIA7 345 1 514908 ARCADIA7 345 514909 REDBUD 7 345 1 514908 ARCADIA7 345 514909 REDBUD 7 345 2 514908 ARCADIA7 345 514909 REDBUD 7 345 3 514908 ARCADIA7 345 515045 SEMINOL7 345 1 514908 ARCADIA7 345 587804 G16-119-TAP 345 1 514908 ARCADIA7 345 998295 ARCADIA2 138 1 514908 ARCADIA7 345 998294 ARCADIA3 138 1 514908 ARCADIA7 345 998293 ARCADIA4 138 1 514908 ARCADIA7 345 587804 G16-100-TAP 345 1 514908 ARCADIA7 345 998303 ARCADIA2 138 1 514908 ARCADIA7 345 998302 ARCADIA3 138 1 514908 ARCADIA7 345 998301 ARCADIA4 138 1 514908 ARCADIA7 345 998300 ARCADIA2 138 1 514908 ARCADIA7 345 998299 ARCADIA3 138 1 514908 ARCADIA7 345 998298 ARCADIA4 138 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.09227 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.04235 | NConv | 81733: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514934 DRAPER 7 345 515045 SEMINOL7 345 1 514934 DRAPER 7 345 515045 SEMINOL7 345 2 514934 DRAPER 7 345 515045 SEMINOL7 345 3 514934 DRAPER 7 345 998290 DRAPER2 138 1 514934 DRAPER 7 345 998289 DRAPER3 138 1 514934 DRAPER 7 345 998288 DRAPER4 138 1 514934 DRAPER 7 345 998298 DRAPER2 138 1 514934 DRAPER 7 345 998297 DRAPER3 138 1 514934 DRAPER 7 345 998296 DRAPER4 138 1 514934 DRAPER 7 345 998295 DRAPER2 138 1 514934 DRAPER 7 345 998294 DRAPER3 138 1 514934 DRAPER 7 345 998293 DRAPER4 138 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.05413 | NConv | 852690: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 560062 G15088_T 345 640277 MOORE 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997353 PAULINE T1 115 1 640312 PAULINE3 345 997353 PAULINE T1 115 1 640315 PAULINE9 13.8 997353 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.09227 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0605 | NConv | 104293: 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532874 UNIONRG6 230 532875 DVISTA 6 230 1 532874 UNIONRG6 230 997914 UNIO TX-1 115 1 532874 UNIONRG6 230 997921 UNIO TX-1 115 1 532874 UNIONRG6 230 997917 UNIO TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0581 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.0605 | NConv | P12:230:WERE:MORR-UNIO_230:: | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.09307 | NConv | 92564: 530623 RICE 3 115 530681 BUSHTON3 115 1 530620 LYONS 3 115 530623 RICE 3 115 1 530686 RICE 6 230 997980 RICE T1 115 1 530623 RICE 3 115 997980 RICE T1 115 1 530687 RICET1 12.5 997980 RICE T1 115 1 530686 RICE 6 230 997986 RICE T1 115 1 530623 RICE 3 115 997986 RICE T1 115 1 530687 RICET1 12.5 997986 RICE T1 115 1 530686 RICE 6 230 997982 RICE T1 115 1 530623 RICE 3 115 997982 RICE T1 115 1 530687 RICET1 12.5 997982 RICE T1 115 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.04992 | NConv | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA
Non-Converge | 00NR | S2 | 24SP0 | G04_G056 |  | Non-Converge |  |  | 0.07417 | NConv | P12:115:MKEC:SMITHCENTER-CONCORDIA(SOUTH):: | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06078 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06078 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.0621 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.04389 | NConv | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09446 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.0621 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | P12:345:WERE:RENO-WICH_345:: | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03562 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.0621 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.04869 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.05982 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.0621 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.07406 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09895 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.0621 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.14971 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.04869 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06403 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.03692 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.20131 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.09895 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06374 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | G04_G056 |  | Non-Converge |  |  | 0.06034 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06052 | NConv | 104288: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | P12:345:WERE:BENT-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84582: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 42750: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P12:345:WERE:LATH-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 8618: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06052 | NConv | 8622: 532856 SWISVAL6 230 532863 MORRIS 6 230 1 532862 MCDOWEL6 230 532863 MORRIS 6 230 1 532863 MORRIS 6 230 532874 UNIONRG6 230 1 532863 MORRIS 6 230 997949 MORR TX-1 230 1 532863 MORRIS 6 230 997920 MORR TX-2 115 1 532863 MORRIS 6 230 997955 MORR TX-1 230 1 532863 MORRIS 6 230 997927 MORR TX-2 115 1 532863 MORRIS 6 230 997951 MORR TX-1 230 1 532863 MORRIS 6 230 997923 MORR TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 42991: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_REOW7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 83836: 523093 HITCHLAND 3 115 523195 HANSFORD 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.15135 | NConv | 8645: 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533413 CIRCLE 3 115 533419 HEC 3 115 1 533413 CIRCLE 3 115 533421 HEC GT 3 115 1 533413 CIRCLE 3 115 997918 CIRC TX-1 115 1 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 533413 CIRCLE 3 115 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P55:161-345:KCPL-GMO:STILWELL_BUS_11_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104225: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P12:345:WERE:BENT-ROSE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.14926 | NConv | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044561: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828730: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104250: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | P23:345:WERE:JEC_345-17:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P12:345:WERE:N345-PSO_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104077: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | 105000: 515576 RANCHRD7 345 515621 OPENSKY7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04165 | NConv | P12:345:OKGE:BKRBKR336 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 105088: 523352 HERRING_TP 3 115 523377 RIVERVIEW 3 115 1 523304 MOORE_W 3 115 523366 RB-SNEED 3 115 1 523352 HERRING_TP 3 115 523366 RB-SNEED 3 115 1 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 523352 HERRING_TP 3 115 523359 HERRING 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104978: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 830510: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7393 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 42990: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.13556 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 82850: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84500: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P23:345:AEPW:DELAWARE CB 3401A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P23:345:WERE:ROSE_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | P23:345:WERE:WICH_345-116:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P12:345:OKGE:BKRBKR336_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 84834: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P42:345:OKGE:SB_TAGA7386 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P12:345:OKGE:BKRBKR357_2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | 47130011: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P23:345:WERE:EMPR_345-330:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997930 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997936 WOLF TX-6 69.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 998311 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998319 SOONER5 138 1 514803 SOONER 7 345 998316 SOONER5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06249 | NConv | P12:230:WERE:CIRC-GRTBND_230:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P42:345:SPS:FINNEY_OR70_19L | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828720: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:WERE:WOLF_345-120:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P12:345:WERE:RENO-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104897: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515407 TATONGA7 345 515582 SLNGWND7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044511: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P12:345:OKGE:BKRBKR421 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104979: 515852 DGRASSE7 345 539801 THISTLE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 81730: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 84377: 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 8612: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04168 | NConv | P12:345:OKGE:BKBK443NEW2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_RARD7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08565 | NConv | 828710: 532771 RENO 7 345 997948 RENO TX-1 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 532807 RENO 1X1 14.4 997948 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997954 RENO TX-1 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 532807 RENO 1X1 14.4 997954 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | P12:345:WERE:N345-AECI_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:161-345:KCPL:STILWELL_R12-22::STILWELL-WGARD-STILT22 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_SOER7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 82851: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | 104258: 532765 HOYT 7 345 532766 JEC N 7 345 1 532766 JEC N 7 345 532767 GEARY 7 345 1 532766 JEC N 7 345 532770 MORRIS 7 345 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 997953 JEC TX-13 230 1 532766 JEC N 7 345 997952 JEC TX-26 230 1 532766 JEC N 7 345 997959 JEC TX-13 230 1 532766 JEC N 7 345 997958 JEC TX-26 230 1 532766 JEC N 7 345 997955 JEC TX-13 230 1 532766 JEC N 7 345 997954 JEC TX-26 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84501: 543044 MOONLT 5 161 543132 BNSF 5 161 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04165 | NConv | P42:345:OKGE:SB_WWHV7382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:NES CB 3441A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38761: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:WERE:WAVS_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P12:345:WERE:WAVS-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08356 | NConv | 104291: 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 997917 EMCP TX-1 115 1 532872 EMCPHER6 230 997924 EMCP TX-1 115 1 532872 EMCPHER6 230 997920 EMCP TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03062 | NConv | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-119-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 830520: 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997950 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | 47130010: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03349 | NConv | 83937: 523309 MOORE_CNTY 6 230 523959 POTTER_CO 6 230 1 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1 523959 POTTER_CO 6 230 998120 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998120 WAUK 90343-A 230 1 523959 POTTER_CO 6 230 998126 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998126 WAUK 90343-A 230 1 523323 MCDOWELL 6 230 523959 POTTER_CO 6 230 1 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 523957 POTTER_TR 1 13.2 998123 WAUK 90343-A 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P12:345:WERE:CANR-LATH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03862 | NConv | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.14926 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P12:345:AEPW-WERE:DELWARE7:NEOSHO7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_WONG7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104160: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:NES CB 3445A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104277: 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532799 WAVERLY7 345 532802 WAVERTX7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:HOYT_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P12:345:OKGE-WERE:BKRBKR422 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104187: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 532802 WAVERTX7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:ROSE_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82902: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | 7821: 533305 MORRIS 3 115 533309 WEMPORI3 115 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 8656: 533413 CIRCLE 3 115 533416 RENO 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533415 DAVIS 3 115 533416 RENO 3 115 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 997948 RENO TX-1 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 533416 RENO 3 115 997954 RENO TX-1 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04171 | NConv | P12:345:OKGE:BKBK443NEW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P12:345:WERE:N345-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104268: 532780 CANEYRV7 345 532781 CANEYWF7 345 1 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P12:345:WERE:WAVS-WOLF_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 104290: 530686 RICE 6 230 532871 CIRCLE 6 230 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 532871 CIRCLE 6 230 997918 CIRC TX-1 115 1 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 532871 CIRCLE 6 230 997921 CIRC TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P12:345:OKGE:BKRBKR400 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:LATH_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104221: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07172 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82901: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | 84128: 510380 DELWARE7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 998406 DELAWARE 138 1 510380 DELWARE7 345 998414 DELAWARE 138 1 510380 DELWARE7 345 998411 DELAWARE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104226: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P12:345:AEPW:DELWARE7:N.E.S.-7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 8585: 532765 HOYT 7 345 532772 STRANGR7 345 1 533211 ARNOLD 3 115 533268 STRANGR3 115 1 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | 84129: 509807 ONETA--7 345 510406 N.E.S.-7 345 1 509852 T.NO.--7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 510406 N.E.S.-7 345 1 511840 NES3-1 22.0 510406 N.E.S.-7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P42:345:OKGE:SB_REOW7319 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:DELAWARE CB 3405A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:WERE:N345_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104219: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P23:161-345:KCPL:STILWELL_R11-12::STILWELL-WGARD-STILT11 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03111 | NConv | P23:345:WERE:N345_345-20:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104222: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997755 STILWELL11 161 11 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:PWT:THIS-DGRS_345_2::FUTURE | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04171 | NConv | 81729: 515407 TATONGA7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P12:345:WERE:HOYT-STRA_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | P23:345:ITCGP:SV_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:OKGE-ITC:BKRBKR502_1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | 104257: 532765 HOYT 7 345 532766 JEC N 7 345 1 532765 HOYT 7 345 532772 STRANGR7 345 1 532765 HOYT 7 345 997954 HOYT TX-1 115 1 532765 HOYT 7 345 997960 HOYT TX-1 115 1 532765 HOYT 7 345 997956 HOYT TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84504: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | P12:345:WERE:HOYT-JEC_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P12:345:WERE:VIOL-OGE_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 77951: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P23:345:AEPW:DELAWARE CB 3409A NBTB | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:RENO_345-160:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_WONG7313 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104161: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542969 STILWEL5 161 543126 LACKMAN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03203 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84583: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08721 | NConv | 82900: 532771 RENO 7 345 997947 RENO TX-2 115 1 533416 RENO 3 115 997947 RENO TX-2 115 1 532810 RENO 2X1 14.4 997947 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997953 RENO TX-2 115 1 533416 RENO 3 115 997953 RENO TX-2 115 1 532810 RENO 2X1 14.4 997953 RENO TX-2 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104266: 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 532774 SWISVAL7 345 997943 SWIS TX-1 230 1 532774 SWISVAL7 345 997942 SWIS TX-2 230 2 532774 SWISVAL7 345 997949 SWIS TX-1 230 1 532774 SWISVAL7 345 997948 SWIS TX-2 230 2 532774 SWISVAL7 345 997945 SWIS TX-1 230 1 532774 SWISVAL7 345 997944 SWIS TX-2 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104701: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04779 | NConv | 81736: 514880 NORTWST7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 515407 TATONGA7 345 515497 MATHWSN7 345 1 515407 TATONGA7 345 515497 MATHWSN7 345 2 515497 MATHWSN7 345 515875 REDNGTN7 345 1 515497 MATHWSN7 345 900001 TRAVERSE1 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | P23:345:WERE:CANR_BKRS:: | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104703: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03495 | NConv | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.08381 | NConv | P42:345:OKGE:SB_REOW7389 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05837 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | 104262: 532766 JEC N 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532770 MORRIS 7 345 997949 MORR TX-1 230 1 532770 MORRIS 7 345 997955 MORR TX-1 230 1 532770 MORRIS 7 345 997951 MORR TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 104278: 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532800 LATHAMS7 345 532801 ELKRVR17 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | 104218: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P23:345:WERE:MORR_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06946 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 84584: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:PWT:THIS-DGRS_345_1::FUTURE | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:WERE:SWIS_345-5:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03441 | NConv | P12:345:WERE:EMPR-MORR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P12:345:OKGE:BKRBKR357_1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0687 | NConv | P12:345:OKGE-ITC:BKRBKR503_1 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 42751: 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03241 | NConv | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0712 | NConv | P12:345:WERE:VIOL-WICH_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.07634 | NConv | P42:345:OKGE:SB_REOW7312 | NA
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.13556 | NConv | P23:345:SUNC:SV_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | P23:345:WERE:BENT_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:RENO_345-150:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | P23:345:WERE:SWIS_345-1:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03166 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P12:345:WERE:SWIS-WGAR_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.03505 | NConv | 81776: 509852 T.NO.--7 345 512694 CLEVLND7 345 1 512694 CLEVLND7 345 560056 G15066_T 345 1 512694 CLEVLND7 345 998333 CLVAUTO1 138 1 512694 CLEVLND7 345 998341 CLVAUTO1 138 1 512694 CLEVLND7 345 998338 CLVAUTO1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 7801: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532991 WEAVER 4 138 533062 ROSEHIL4 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38760: 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09049 | NConv | 8604: 532765 HOYT 7 345 532766 JEC N 7 345 1 532766 JEC N 7 345 532767 GEARY 7 345 1 532766 JEC N 7 345 532770 MORRIS 7 345 1 532766 JEC N 7 345 532652 JEC U2 26.0 1 532766 JEC N 7 345 532653 JEC U3 26.0 1 532766 JEC N 7 345 997953 JEC TX-13 230 1 532766 JEC N 7 345 997952 JEC TX-26 230 1 532766 JEC N 7 345 997959 JEC TX-13 230 1 532766 JEC N 7 345 997958 JEC TX-26 230 1 532766 JEC N 7 345 997955 JEC TX-13 230 1 532766 JEC N 7 345 997954 JEC TX-26 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 104976: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515853 DGRASSE4 138 998198 DGRASSE 138 1 515852 DGRASSE7 345 998198 DGRASSE 138 1 515854 DGRASSE1 13.8 998198 DGRASSE 138 1 515853 DGRASSE4 138 998206 DGRASSE 138 1 515852 DGRASSE7 345 998206 DGRASSE 138 1 515854 DGRASSE1 13.8 998206 DGRASSE 138 1 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P55:161-345:KCPL:STILWELL_BUS_22_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06543 | NConv | P42:345:OKGE:SB_OPKY7388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.17242 | NConv | 8587: 533441 MEADOW 115 533455 TWR 33 3 115 2 533441 MEADOW 115 533455 TWR 33 3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 2 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 533411 ARKVAL 3 115 533412 ARKVALJ3 115 1 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 533435 3 VANBU3 115 533441 MEADOW 115 1 530686 RICE 6 230 532871 CIRCLE 6 230 1 533440 43LORAN 115 533455 TWR 33 3 115 1 533435 3 VANBU3 115 533441 MEADOW 115 2 532871 CIRCLE 6 230 539679 GRTBEND6 230 1 530618 HUNTSVL3 115 533412 ARKVALJ3 115 1 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 533419 HEC 3 115 533440 43LORAN 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05898 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.05386 | NConv | P12:345:WERE:EMPR-SWIS_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | 104702: 542966 WGARDNR5 161 543132 BNSF 5 161 1 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04814 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0351 | NConv | P23:345:WERE:N345_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 104251: 542968 STILWEL7 345 997751 STILWELL22 161 22 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09692 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06288 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.06158 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.12169 | NConv | P23:345:WERE:BENT_345-110:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | P42:345:OKGE:SB_WWHV7383 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.0842 | NConv | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.1996 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.09181 | NConv | P23:345:WERE:STRA_345-95:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | G04_G056 |  | Non-Converge |  |  | 0.04174 | NConv | 84346: 542965 W.GRDNR7 345 542968 STILWEL7 345 1 543044 MOONLT 5 161 543132 BNSF 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.08481 | NConv | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044561: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0897 | NConv | P23:345:WERE:JEC_345-17:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.04245 | NConv | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03876 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 42990: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 177402: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06427 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.12545 | NConv | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03342 | NConv | 84834: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | P23:345:WERE:STRA_345-100:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | P12:345:WERE:N345-LACY_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03342 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044511: 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06289 | NConv | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P23:345:SUNC:HLC_BRK282 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997997 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 528219 CHINA_DRAW 1 13.2 998003 UPDATE LATER 115 1 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998148 SIEM 8743067 230 2 523097 HITCHLAND 7 345 523094 HITCHLD_TR21 13.2 998154 SIEM 8743067 230 2 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05356 | NConv | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03342 | NConv | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.08481 | NConv | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03726 | NConv | P23:345:WERE:MORR_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | 104216: 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05356 | NConv | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03512 | NConv | 805052: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03342 | NConv | 104219: 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997944 SUMM TX-1 230 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 997950 SUMM TX-1 230 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09922 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | 104257: 532765 HOYT 7 345 532766 JEC N 7 345 1 532765 HOYT 7 345 532772 STRANGR7 345 1 532765 HOYT 7 345 997954 HOYT TX-1 115 1 532765 HOYT 7 345 997960 HOYT TX-1 115 1 532765 HOYT 7 345 997956 HOYT TX-1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0897 | NConv | P12:345:WERE:HOYT-JEC_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 77951: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0609 | NConv | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.08461 | NConv | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0494 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03726 | NConv | 104262: 532766 JEC N 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532770 MORRIS 7 345 997949 MORR TX-1 230 1 532770 MORRIS 7 345 997955 MORR TX-1 230 1 532770 MORRIS 7 345 997951 MORR TX-1 230 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0609 | NConv | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06928 | NConv | 105454: 531511 HARBNGR-T 13.8 997958 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997958 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 531511 HARBNGR-T 13.8 997964 HARBGR345 115 1 531512 HARBNGR7 345 997964 HARBGR345 115 1 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 531512 HARBNGR7 345 997960 HARBGR345 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05626 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.03155 | NConv | P23:345:WERE:N345_345-80:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05067 | NConv | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997932 WICH TX-11 138 1 532796 WICHITA7 345 997931 WICH TX-12 138 1 532796 WICHITA7 345 997938 WICH TX-11 138 1 532796 WICHITA7 345 997937 WICH TX-12 138 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06201 | NConv | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.12545 | NConv | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09017 | NConv | P23:345:WERE:HOYT_345_BKRS:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.05741 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998239 WWDEHV 138 1 515375 WWRDEHV7 345 998238 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998247 WWDEHV 138 1 515375 WWRDEHV7 345 998246 WWDEHV-T2 138 2 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.0494 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | P23:345:WERE:WICH_345-50:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.20113 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.09922 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997880 ROSE TX-1 138 1 532794 ROSEHIL7 345 997879 ROSE TX-3 138 1 532794 ROSEHIL7 345 997878 ROSE TX-5 138 1 532794 ROSEHIL7 345 997887 ROSE TX-1 138 1 532794 ROSEHIL7 345 997886 ROSE TX-3 138 1 532794 ROSEHIL7 345 997885 ROSE TX-5 138 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G04_G056 |  | Non-Converge |  |  | 0.06397 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA | non-Converged in the BC | N/A

## All Voltage
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | MONITORED ELEMENT | BC Voltage (PU) | TC Voltage (PU) | Voltage Differ (PU) | VINIT (PU) | VMIN (PU) | VMAX(PU) | TDF | CONTINGENCY | Footprint
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEYPL | 0.9332 | 0.8948 | -0.0384 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEYPL | 0.9332 | 0.8948 | -0.0384 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ROCKCRK2 | 0.9617 | 0.9196 | -0.0421 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NASHUA 7 | 0.9282 | 0.8734 | -0.0548 | 345 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NASHUA 7 | 0.9282 | 0.8734 | -0.0548 | 345 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SOUTHTN3 | 0.9581 | 0.9209 | -0.0372 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | OAKGRV 5 | 0.929 | 0.8987 | -0.0303 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | OAKGRV 5 | 0.929 | 0.8987 | -0.0303 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SATMKEC3 | 0.954 | 0.8981 | -0.0559 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HASKELL3 | 0.953 | 0.8963 | -0.0567 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NORTONV2 | >0.95 | 0.9053 | >0.0447 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NORTONV2 | >0.95 | 0.9053 | >0.0447 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TECHILL6 | 0.955 | 0.9318 | -0.0232 | 230 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | PENTAGN3 | 0.9573 | 0.9283 | -0.029 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MIDLAND6 | >0.97 | 0.9461 | >0.0239 | 230 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WAVERLY3 | 0.9623 | 0.9277 | -0.0346 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WATHENA2 | 0.9476 | 0.8699 | -0.0777 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WATHENA2 | 0.9476 | 0.8699 | -0.0777 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | FRTLEAV3 | >0.95 | 0.9239 | >0.0261 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | FRTLEAV3 | >0.95 | 0.9239 | >0.0261 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5LATHRP | 0.883 | 0.8412 | -0.0418 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5LATHRP | 0.883 | 0.8412 | -0.0418 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | RICHMND5 | 0.9206 | 0.8881 | -0.0325 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5REX | 0.8777 | 0.8372 | -0.0405 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | GRAINVL5 | 0.9309 | 0.8999 | -0.031 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | GRAINVL5 | 0.9309 | 0.8999 | -0.031 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | CIM-PLT3 | 0.9441 | 0.8825 | -0.0616 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | E-PINE 3 | 0.9588 | 0.8989 | -0.0599 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | FAIRGDS3 | 0.9669 | 0.9288 | -0.0381 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | FAIRGDS3 | 0.9669 | 0.9288 | -0.0381 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | PARALEL3 | >0.95 | 0.9152 | >0.0348 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | PARALEL3 | >0.95 | 0.9152 | >0.0348 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SWLWRNC3 | 0.9681 | 0.9296 | -0.0385 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SWLWRNC3 | 0.9681 | 0.9296 | -0.0385 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | CARPENTER 7 | 0.9293 | 0.8439 | -0.0854 | 345 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | KERFORD3 | >0.95 | 0.9187 | >0.0313 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | KERFORD3 | >0.95 | 0.9187 | >0.0313 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SWISVAL7 | >0.97 | 0.9462 | >0.0238 | 345 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SWISVAL6 | 0.9693 | 0.9448 | -0.0245 | 230 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 166TH 3 | 0.9691 | 0.9286 | -0.0405 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 166TH 3 | 0.9691 | 0.9286 | -0.0405 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MW SOLV2 | >0.95 | 0.9052 | >0.0448 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MW SOLV2 | >0.95 | 0.9052 | >0.0448 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | GRANT 3 | 0.9505 | 0.8863 | -0.0642 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SPRINGH3 | 0.956 | 0.9171 | -0.0389 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NLIB 3 | 0.9521 | 0.891 | -0.0611 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIB REA1 | 0.924 | 0.8846 | -0.0394 | 345 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIB REA1 | 0.924 | 0.8846 | -0.0394 | 345 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NW LEAV3 | >0.95 | 0.9279 | >0.0221 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NW LEAV3 | >0.95 | 0.9279 | >0.0221 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | CLAYCM15 | 0.95 | 0.8998 | -0.0502 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | CLAYCM15 | 0.95 | 0.8998 | -0.0502 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WALNUT 3 | >0.95 | 0.914 | >0.036 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WALNUT 3 | >0.95 | 0.914 | >0.036 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 19THSTJ3 | 0.9668 | 0.9284 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 19THSTJ3 | 0.9668 | 0.9284 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | LBRTYWT5 | 0.9463 | 0.8957 | -0.0506 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | LBRTYWT5 | 0.9463 | 0.8957 | -0.0506 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MUSCOTA2 | 0.9566 | 0.8896 | -0.067 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MUSCOTA2 | 0.9566 | 0.8896 | -0.067 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TONGATP3 | >0.95 | 0.9283 | >0.0217 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TONGATP3 | >0.95 | 0.9283 | >0.0217 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TIMBRLN3 | 0.9618 | 0.9254 | -0.0364 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MOONLIT3 | 0.9581 | 0.922 | -0.0361 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | EDMOND5 | 0.9294 | 0.8998 | -0.0296 | 161 | 0.9 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HLLMRK 5 | 0.9425 | 0.8938 | -0.0487 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HLLMRK 5 | 0.9425 | 0.8938 | -0.0487 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | NATBEEF3 | 0.9571 | 0.8971 | -0.06 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | AMELIA 3 | >0.95 | 0.9169 | >0.0331 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | AMELIA 3 | >0.95 | 0.9169 | >0.0331 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MOONLTJ3 | 0.9595 | 0.9234 | -0.0361 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HALLMRK3 | >0.95 | 0.9216 | >0.0284 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HALLMRK3 | >0.95 | 0.9216 | >0.0284 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SPRUCE 3 | >0.95 | 0.9228 | >0.0272 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SPRUCE 3 | >0.95 | 0.9228 | >0.0272 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5MPLTAP | 0.8806 | 0.8391 | -0.0415 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 87TH 7 | 0.95 | 0.9135 | -0.0365 | 345 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | JAGGARD3 | 0.9637 | 0.9283 | -0.0354 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | JAGGARD3 | 0.9637 | 0.9283 | -0.0354 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MUND 3 | 0.9482 | 0.9233 | -0.0249 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | THORNTN3 | >0.95 | 0.9228 | >0.0272 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | THORNTN3 | >0.95 | 0.9228 | >0.0272 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEY 5 | 0.9327 | 0.8942 | -0.0385 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEY 5 | 0.9327 | 0.8942 | -0.0385 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEY 7 | 0.924 | 0.8846 | -0.0394 | 345 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SIBLEY 7 | 0.924 | 0.8846 | -0.0394 | 345 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ODESSA 5 | 0.9226 | 0.8966 | -0.026 | 161 | 0.9 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HUGOTON3 | 0.9297 | 0.8537 | -0.076 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | BLUMILS5 | 0.9346 | 0.8959 | -0.0387 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5MOCITY | 0.9255 | 0.8863 | -0.0392 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | E-LIBER3 | 0.9587 | 0.8989 | -0.0598 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | KISMET 3 | 0.9525 | 0.8977 | -0.0548 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | LEC U5 6 | >0.97 | 0.9474 | >0.0226 | 230 | 0.95 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TCSEVRN3 | >0.95 | 0.91 | >0.04 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | TCSEVRN3 | >0.95 | 0.91 | >0.04 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | KU CAMP3 | 0.9664 | 0.928 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | KU CAMP3 | 0.9664 | 0.928 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ORRICK 5 | 0.9288 | 0.892 | -0.0368 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ORRICK 5 | 0.9288 | 0.892 | -0.0368 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | RTCHFLD5 | 0.941 | 0.8935 | -0.0475 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | RTCHFLD5 | 0.941 | 0.8935 | -0.0475 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WALNUT 2 | >0.95 | 0.907 | >0.043 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WALNUT 2 | >0.95 | 0.907 | >0.043 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5LATHROP | 0.8805 | 0.8389 | -0.0416 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | WALKMYR3 | 0.9316 | 0.853 | -0.0786 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 19THST 3 | 0.966 | 0.9276 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 19THST 3 | 0.966 | 0.9276 | -0.0384 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ARNOLD 2 | >0.95 | 0.9056 | >0.0444 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ARNOLD 2 | >0.95 | 0.9056 | >0.0444 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | CMRIVTP3 | 0.9504 | 0.8918 | -0.0586 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SAT-TAP3 | 0.954 | 0.8981 | -0.0559 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SEWARD-3 | 0.9488 | 0.8886 | -0.0602 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | VALLEY22 | 0.9649 | 0.9086 | -0.0563 | 69 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | VALLEY22 | 0.9649 | 0.9086 | -0.0563 | 69 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | PLTCTY 5 | 0.9555 | 0.8998 | -0.0557 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | PLTCTY 5 | 0.9555 | 0.8998 | -0.0557 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | W-LIBER3 | 0.9531 | 0.8917 | -0.0614 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5WINSLOW | 0.9204 | 0.8987 | -0.0217 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | 5WINSLOW | 0.9204 | 0.8987 | -0.0217 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | BONITA 3 | 0.9566 | 0.9184 | -0.0382 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HAWTH 7 | 0.9229 | 0.8734 | -0.0495 | 345 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HAWTH 7 | 0.9229 | 0.8734 | -0.0495 | 345 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | STRANGR3 | >0.95 | 0.9277 | >0.0223 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | STRANGR3 | >0.95 | 0.9277 | >0.0223 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | GRANTTP3 | 0.9508 | 0.8866 | -0.0642 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | N-CIMRN3 | 0.9441 | 0.8824 | -0.0617 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ECKLES-161 | 0.9348 | 0.8966 | -0.0382 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | ECKLES-161 | 0.9348 | 0.8966 | -0.0382 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HAYNE3 | 0.9451 | 0.8834 | -0.0617 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HARBNGR7 | 0.9293 | 0.8439 | -0.0854 | 345 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | HARBNGR3 | 0.9312 | 0.8519 | -0.0793 | 115 | 0.9 | 1.05 | 0.13565 | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997838 SPEARVL 230 1 531469 SPERVIL7 345 997796 SPEARVILLE 115 1 531469 SPERVIL7 345 997845 SPEARVL 230 1 531469 SPERVIL7 345 997803 SPEARVILLE 115 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | LBRTYST5 | 0.9366 | 0.8978 | -0.0388 | 161 | 0.9 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | LBRTYST5 | 0.9366 | 0.8978 | -0.0388 | 161 | 0.9 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | EFAIRMNT3 | >0.95 | 0.9252 | >0.0248 | 115 | 0.93 | 1.05 | 0.09227 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | EFAIRMNT3 | >0.95 | 0.9252 | >0.0248 | 115 | 0.93 | 1.05 | 0.09227 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997946 STRA TX-1 115 1 532772 STRANGR7 345 997945 STRA TX-3 115 1 532772 STRANGR7 345 997952 STRA TX-1 115 1 532772 STRANGR7 345 997951 STRA TX-3 115 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | MNTCLLO3 | 0.9611 | 0.9291 | -0.032 | 115 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | G07_G077&G085 | SPRGHL 5 | 0.9595 | 0.9195 | -0.04 | 161 | 0.93 | 1.05 | 0.03297 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997731 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997738 LACYGNE 7 69.0 1 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SIBLEYPL | 0.8994 | 0.8748 | -0.0246 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | AXTELL 3 | <1.03 | 1.054 | >0.024 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CHASE 3 | >0.92 | 0.8729 | >0.0471 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5FAIRPT | 0.8863 | 0.8505 | -0.0358 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NASHUA 7 | 0.8963 | 0.8685 | -0.0278 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MORRIS-3 | 0.9448 | 0.8394 | -0.1054 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | OSBORN7 | 0.8443 | 0.799 | -0.0453 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TECHILL5 | 0.9334 | 0.9098 | -0.0236 | 161 | 0.93 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MOUNDRG3 | >0.95 | 0.9206 | >0.0294 | 115 | 0.93 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLSPW 5 | 0.9104 | 0.8882 | -0.0222 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | P1 MPT PRI | 0.9236 | 0.8794 | -0.0442 | 345 | 0.9 | 1.05 | 0.07406 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | POSTROCK7 | <1.03 | 1.2502 | >0.2202 | 345 | 0.9 | 1.05 | 0.03692 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | POSTROCK7 | <1.03 | 1.2502 | >0.2202 | 345 | 0.9 | 1.05 | 0.03692 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G17-021-TAP | 0.9689 | 1.2639 | 0.295 | 345 | 0.9 | 1.05 | 0.03692 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G17-021-TAP | 0.9689 | 1.2639 | 0.295 | 345 | 0.9 | 1.05 | 0.03692 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G17-030-TAP | 0.9221 | 0.8922 | -0.0299 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MC REAC1 | 0.8658 | 0.8216 | -0.0442 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MC REAC3 | 0.8658 | 0.8216 | -0.0442 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MC REAC2 | 0.8658 | 0.8216 | -0.0442 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5MEADVL | 0.8791 | 0.8499 | -0.0292 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5PITTSV | 0.9156 | 0.8928 | -0.0228 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5LATHRP | 0.854 | 0.8199 | -0.0341 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S1263 5 | 0.965 | 0.9402 | -0.0248 | 161 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDWILO3 | <1.03 | 1.0632 | >0.0332 | 345 | 0.9 | 1.05 | 0.03692 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDWILO3 | <1.03 | 1.0632 | >0.0332 | 345 | 0.9 | 1.05 | 0.03692 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | THISTLE7 | 0.9467 | 0.9187 | -0.028 | 345 | 0.95 | 1.05 | 0.07406 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | FLETCHR3 | 0.965 | 0.8619 | -0.1031 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IRSKDOL3 | 0.9452 | 0.8386 | -0.1066 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HAWTH 7 | 0.8898 | 0.8638 | -0.026 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SWNDTAP3 | 0.9465 | 0.838 | -0.1085 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | RICHMND5 | 0.8889 | 0.8654 | -0.0235 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G15_021_1 | >0.92 | 0.8916 | >0.0284 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HILSBOR3 | 0.9636 | 0.9061 | -0.0575 | 115 | 0.93 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HILSBOR3 | 0.9636 | 0.9061 | -0.0575 | 115 | 0.93 | 1.05 | 0.20131 | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-115 | 0.8809 | 0.8381 | -0.0428 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CLAYCM25 | 0.9169 | 0.8931 | -0.0238 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WILLIAM3 | >0.92 | 0.8533 | >0.0667 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2017-052 | >0.92 | 0.8792 | >0.0408 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | AVENUECTY 5 | 0.884 | 0.849 | -0.035 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MULLNCR7 | 0.8658 | 0.8216 | -0.0442 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TRIB SW3 | 0.968 | 0.8487 | -0.1193 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PALMER3 | 0.9689 | 0.854 | -0.1149 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5REX | 0.8503 | 0.8144 | -0.0359 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PILE 3 | 0.9502 | 0.891 | -0.0592 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ROCKCK7 | 0.8805 | 0.8377 | -0.0428 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SAVANAH2 | 0.9269 | 0.8874 | -0.0395 | 69 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5HICKCK | 0.8588 | 0.825 | -0.0338 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S1280 5 | 0.961 | 0.9345 | -0.0265 | 161 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLSPE 5 | 0.9078 | 0.8853 | -0.0225 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | JOHNCR 3 | >0.92 | 0.8916 | >0.0284 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 7FAIRPT | 0.898 | 0.8618 | -0.0362 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5CHILLI | 0.8694 | 0.8383 | -0.0311 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WTCLFTP3 | >0.92 | 0.8895 | >0.0305 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SIB REA1 | 0.8831 | 0.8561 | -0.027 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G16-050-TAP | <1.03 | 1.2798 | >0.2498 | 345 | 0.9 | 1.05 | 0.03692 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G16-050-TAP | <1.03 | 1.2798 | >0.2498 | 345 | 0.9 | 1.05 | 0.03692 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GRDNCTY3 | 0.9475 | 0.8377 | -0.1098 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5LOCUST | 0.8542 | 0.8196 | -0.0346 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CLAYCM15 | 0.9217 | 0.8977 | -0.024 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BRMGHAM5 | 0.9171 | 0.8934 | -0.0237 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G14_001_1 | 0.9547 | 0.9342 | -0.0205 | 345 | 0.95 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 6 | >0.97 | 0.9433 | >0.0267 | 230 | 0.95 | 1.05 | 0.0621 | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 6 | >0.97 | 0.9433 | >0.0267 | 230 | 0.95 | 1.05 | 0.0621 | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 6 | >0.97 | 0.9433 | >0.0267 | 230 | 0.95 | 1.05 | 0.0621 | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | P2 MPT PRI | 0.9239 | 0.8797 | -0.0442 | 345 | 0.9 | 1.05 | 0.07406 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LBRTYWT5 | 0.9178 | 0.8931 | -0.0247 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DOBSON 3 | 0.9474 | 0.8443 | -0.1031 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BEARCRK3 | >0.92 | 0.8692 | >0.0508 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HLLMRK 5 | 0.9138 | 0.889 | -0.0248 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | FLORENC3 | 0.9645 | 0.9091 | -0.0554 | 115 | 0.93 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | FLORENC3 | 0.9645 | 0.9091 | -0.0554 | 115 | 0.93 | 1.05 | 0.20131 | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | UNIONRG6 | >0.97 | 0.9479 | >0.0221 | 230 | 0.95 | 1.05 | 0.0621 | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | UNIONRG6 | >0.97 | 0.9479 | >0.0221 | 230 | 0.95 | 1.05 | 0.0621 | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | UNIONRG6 | >0.97 | 0.9479 | >0.0221 | 230 | 0.95 | 1.05 | 0.0621 | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | JOHNSON2 | >0.92 | 0.8939 | >0.0261 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2017-030 | 0.8671 | 0.839 | -0.0281 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SHARNSP3 | >0.92 | 0.8729 | >0.0471 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5MPLTAP | 0.8519 | 0.8172 | -0.0347 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GARDNCY2 | 0.965 | 0.8487 | -0.1163 | 69 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CLARKCOUNTY7 | 0.9229 | 0.8787 | -0.0442 | 345 | 0.9 | 1.05 | 0.07406 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SPRGCRK3 | 0.967 | 0.9098 | -0.0572 | 115 | 0.93 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SPRGCRK3 | 0.967 | 0.9098 | -0.0572 | 115 | 0.93 | 1.05 | 0.20131 | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G17-030-SWYD | 0.8671 | 0.839 | -0.0281 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GANO 3 | 0.9489 | 0.871 | -0.0779 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S1399 5 | 0.9591 | 0.9312 | -0.0279 | 161 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SIBLEY 5 | 0.8982 | 0.8734 | -0.0248 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SIBLEY 7 | 0.8831 | 0.8561 | -0.027 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 7 | >0.97 | 0.9466 | >0.0234 | 345 | 0.95 | 1.05 | 0.0621 | 1044510: 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532767 GEARY 7 345 532773 SUMMIT 7 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 7 | >0.97 | 0.9466 | >0.0234 | 345 | 0.95 | 1.05 | 0.0621 | 77950: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUMMIT 7 | >0.97 | 0.9466 | >0.0234 | 345 | 0.95 | 1.05 | 0.0621 | 1044560: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5MAURER LK | 0.8938 | 0.8679 | -0.0259 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HUGOTON3 | 0.9374 | 0.8927 | -0.0447 | 115 | 0.9 | 1.05 | 0.06034 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLUMILS5 | 0.9024 | 0.8788 | -0.0236 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5MOCITY | 0.893 | 0.8668 | -0.0262 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PUCKET 3 | >0.92 | 0.8998 | >0.0202 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOLT 7 | 0.8875 | 0.8463 | -0.0412 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MIDWY2 2 | 0.9133 | 0.8829 | -0.0304 | 69 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KETCHEM7 | 0.8443 | 0.799 | -0.0453 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ORRICK 5 | 0.8952 | 0.8708 | -0.0244 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KSAVWTP3 | 0.9475 | 0.8384 | -0.1091 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5LATHROP | 0.8518 | 0.817 | -0.0348 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SYRACUS3 | >0.92 | 0.8538 | >0.0662 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G17-052-TAP | >0.92 | 0.8792 | >0.0408 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | G14_001T | 0.9547 | 0.9342 | -0.0205 | 345 | 0.95 | 1.05 | 0.20131 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DUNCAN 5 | 0.9061 | 0.8832 | -0.0229 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PK_GOAB3 | >0.92 | 0.8998 | >0.0202 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ODESSA 5 | 0.892 | 0.8699 | -0.0221 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MIDWAY_5 | 0.9133 | 0.883 | -0.0303 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TRANSFORMER | 0.9229 | 0.8787 | -0.0442 | 345 | 0.9 | 1.05 | 0.07406 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S1398 5 | 0.9572 | 0.9292 | -0.028 | 161 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5WINSLOW | 0.8972 | 0.8618 | -0.0354 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-149 | 0.9584 | 0.9363 | -0.0221 | 345 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-050 | <1.03 | 1.2798 | >0.2498 | 345 | 0.9 | 1.05 | 0.03692 | 177405: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-050 | <1.03 | 1.2798 | >0.2498 | 345 | 0.9 | 1.05 | 0.03692 | 805055: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | STRANGR7 | 0.9377 | 0.916 | -0.0217 | 345 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5GENTRY | 0.8959 | 0.8623 | -0.0336 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LEX161 5 | 0.8895 | 0.8664 | -0.0231 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-088 | 0.8443 | 0.799 | -0.0453 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5OSBORN | 0.8567 | 0.8194 | -0.0373 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TRIBUNE3 | 0.9681 | 0.8462 | -0.1219 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOLT_REACT7 | 0.8875 | 0.8463 | -0.0412 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ECKLES-161 | 0.9003 | 0.8757 | -0.0246 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S. WIND3 | 0.9464 | 0.838 | -0.1084 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LEOTI 3 | 0.9643 | 0.8841 | -0.0802 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SELKIRK3 | 0.965 | 0.872 | -0.093 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | 5LEVASY | 0.9099 | 0.8865 | -0.0234 | 161 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | External
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HUMBOLT5 | 0.9549 | 0.9274 | -0.0275 | 161 | 0.95 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WTCLF 3 | >0.92 | 0.8892 | >0.0308 | 115 | 0.9 | 1.05 | 0.06034 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ST JOE 3 | 0.9023 | 0.8677 | -0.0346 | 345 | 0.9 | 1.05 | 0.03692 | 805042: 530583 POSTROCK7 345 997989 POSTROCK T1 230 1 530584 POSTROCK6 230 997989 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997989 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997995 POSTROCK T1 230 1 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 | Internal
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | PRAIRIE3 | 0.9688 | 0.925 | -0.0438 | 115 | 0.93 | 1.05 | 0.09301 | 8660: 533394 CORONAD3 115 533438 WMCPHER3 115 1 533416 RENO 3 115 533438 WMCPHER3 115 1 533426 MANVILE3 115 533438 WMCPHER3 115 1 533428 MCPHER 3 115 533438 WMCPHER3 115 1 533438 WMCPHER3 115 533439 WHEATLD3 115 1 | Internal
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ARNOLD 3 | 0.9525 | 0.88 | 0.0725 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KEENE 3 | 0.9477 | 0.8867 | -0.061 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KEENE 3 | 0.9477 | 0.8867 | -0.061 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KINSLEY3 | 0.9251 | 0.8717 | -0.0534 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KINSLEY3 | 0.9251 | 0.8717 | -0.0534 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MARMTNE5 | 0.9556 | 0.9129 | -0.0427 | 161 | 0.93 | 1.05 | 0.0494 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MARMTNE5 | 0.9556 | 0.9129 | -0.0427 | 161 | 0.93 | 1.05 | 0.0494 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CHASE 3 | 0.9507 | 0.8117 | -0.139 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ROCKCRK2 | 0.9357 | 0.8808 | -0.0549 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ROCKCRK2 | 0.9357 | 0.8808 | -0.0549 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NSI TAP3 | 0.9673 | 0.8841 | -0.0832 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCDOWEL6 | >0.97 | 0.9091 | >0.0609 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCDOWEL6 | >0.97 | 0.9091 | >0.0609 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-073 | 0.9551 | 0.9205 | -0.0346 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-073 | 0.9551 | 0.9205 | -0.0346 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WJCCTY 3 | >0.95 | 0.9156 | >0.0344 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WJCCTY 3 | >0.95 | 0.9156 | >0.0344 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SG11KOC2 | 0.9471 | 0.9192 | -0.0279 | 69 | 0.93 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SG11KOC2 | 0.9471 | 0.9192 | -0.0279 | 69 | 0.93 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MURLEN 5 | 0.9387 | 0.8949 | -0.0438 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 6 GOLDN3 | 0.9335 | 0.8751 | -0.0584 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 6 GOLDN3 | 0.9335 | 0.8751 | -0.0584 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCDOWEL3 | >0.95 | 0.9126 | >0.0374 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCDOWEL3 | >0.95 | 0.9126 | >0.0374 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWISVAL7 | 0.9555 | 0.9041 | -0.0514 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWISVAL7 | 0.9555 | 0.9041 | -0.0514 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | READING3 | 0.9586 | 0.8612 | -0.0974 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | READING3 | 0.9586 | 0.8612 | -0.0974 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 3 VANBU2 | >0.95 | 0.8933 | >0.0567 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 3 VANBU2 | >0.95 | 0.8933 | >0.0567 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JOHNCR 2 | >0.92 | 0.8559 | >0.0641 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JOHNCR 3 | 0.9633 | 0.7827 | -0.1806 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYGEN3 | 0.9541 | 0.886 | -0.0681 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYGEN3 | 0.9541 | 0.886 | -0.0681 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2015-073 | >0.97 | 0.9304 | >0.0396 | 345 | 0.95 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FT JCT 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FT JCT 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LWRNCHL3 | 0.9602 | 0.9117 | -0.0485 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LWRNCHL3 | 0.9602 | 0.9117 | -0.0485 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCPHER 3 | 0.9692 | 0.8928 | -0.0764 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MCPHER 3 | 0.9692 | 0.8928 | -0.0764 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ELLIS 2 | 0.9292 | 0.8864 | -0.0428 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CENCITY7 | >0.92 | 0.872 | >0.048 | 115 | 0.9 | 1.05 | 0.05067 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997134 GI KU1A 230 1 640200 GR ISLD4 230 997133 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997134 GI KU1A 230 1 653316 GR ISL29 13.8 997133 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997134 GI KU1A 230 1 653571 GR ISLD3 345 997133 GI KU1B 230 2 640202 GR ISLD9 34.5 997407 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997410 GI KU3A 230 3 640200 GR ISLD4 230 997409 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997408 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997141 GI KU1A 230 1 640200 GR ISLD4 230 997140 GI KU1B 230 2 640201 GR ISLD7 115 997409 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997408 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997407 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997408 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997410 GI KU3A 230 3 653314 GR ISL19 13.8 997141 GI KU1A 230 1 653316 GR ISL29 13.8 997140 GI KU1B 230 2 653571 GR ISLD3 345 997410 GI KU3A 230 3 653571 GR ISLD3 345 997141 GI KU1A 230 1 653571 GR ISLD3 345 997140 GI KU1B 230 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAKOTA_5 | 0.948 | 0.8984 | -0.0496 | 161 | 0.9 | 1.05 | 0.0494 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAKOTA_5 | 0.948 | 0.8984 | -0.0496 | 161 | 0.9 | 1.05 | 0.0494 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILL6 | 0.9351 | 0.8798 | -0.0553 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILL6 | 0.9351 | 0.8798 | -0.0553 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILL5 | 0.9309 | 0.8826 | -0.0483 | 161 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILL5 | 0.9309 | 0.8826 | -0.0483 | 161 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PAWNEE 3 | 0.9174 | 0.8634 | -0.054 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PAWNEE 3 | 0.9174 | 0.8634 | -0.054 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN S 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN S 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MAPLE J2 | >0.95 | 0.8942 | >0.0558 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MAPLE J2 | >0.95 | 0.8942 | >0.0558 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WJCCTYW3 | >0.95 | 0.9156 | >0.0344 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WJCCTYW3 | >0.95 | 0.9156 | >0.0344 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRATTWF7 | >0.97 | 0.9425 | >0.0275 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRATTWF7 | >0.97 | 0.9425 | >0.0275 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JCTCTY 3 | >0.95 | 0.9149 | >0.0351 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JCTCTY 3 | >0.95 | 0.9149 | >0.0351 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRAIRIE3 | 0.9691 | 0.8643 | -0.1048 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRAIRIE3 | 0.9691 | 0.8643 | -0.1048 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | S GAGEE3 | 0.9342 | 0.875 | -0.0592 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | S GAGEE3 | 0.9342 | 0.875 | -0.0592 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BUFFALO7 | 0.9551 | 0.9205 | -0.0346 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BUFFALO7 | 0.9551 | 0.9205 | -0.0346 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MANTERT2 | >0.92 | 0.8525 | >0.0675 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRNJ22 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRNJ22 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RICHFLD2 | >0.92 | 0.8447 | >0.0753 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOUND 4 | 0.9587 | 0.9045 | -0.0542 | 138 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOUND 4 | 0.9587 | 0.9045 | -0.0542 | 138 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NMANHT6 | >0.97 | 0.9177 | >0.0523 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NMANHT6 | >0.97 | 0.9177 | >0.0523 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WATHENA2 | 0.9232 | 0.8751 | -0.0481 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NMANHT3 | >0.95 | 0.9203 | >0.0297 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NMANHT3 | >0.95 | 0.9203 | >0.0297 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FRTLEAV3 | 0.9682 | 0.9294 | -0.0388 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FRTLEAV3 | 0.9682 | 0.9294 | -0.0388 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FLETCHR3 | 0.9471 | 0.7621 | -0.185 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CIRCLVL3 | 0.954 | 0.9192 | -0.0348 | 115 | 0.93 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CHAPMAN3 | >0.95 | 0.9127 | >0.0373 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CHAPMAN3 | >0.95 | 0.9127 | >0.0373 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTHVW3 | 0.9697 | 0.8692 | -0.1005 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTHVW3 | 0.9697 | 0.8692 | -0.1005 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2MADISN2 | 0.9301 | 0.8719 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2MADISN2 | 0.9301 | 0.8719 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2MADISN3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2MADISN3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EABILEN3 | >0.95 | 0.8871 | >0.0629 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EABILEN3 | >0.95 | 0.8871 | >0.0629 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLAND6 | 0.9536 | 0.9041 | -0.0495 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLAND6 | 0.9536 | 0.9041 | -0.0495 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | S ALMA 3 | 0.9561 | 0.8941 | -0.062 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | S ALMA 3 | 0.9561 | 0.8941 | -0.062 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KSU E 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KSU E 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | S.OTTWA5 | 0.9394 | 0.8958 | -0.0436 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PIONEER3 | 0.9438 | 0.8468 | -0.097 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STAGGHL3 | >0.95 | 0.9161 | >0.0339 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STAGGHL3 | >0.95 | 0.9161 | >0.0339 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEARY 7 | 0.9642 | 0.9064 | -0.0578 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEARY 7 | 0.9642 | 0.9064 | -0.0578 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEARY 3 | >0.95 | 0.9209 | >0.0291 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEARY 3 | >0.95 | 0.9209 | >0.0291 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 54&MERI3 | 0.9455 | 0.8893 | -0.0562 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 54&MERI3 | 0.9455 | 0.8893 | -0.0562 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NEKOMA 3 | 0.9434 | 0.8943 | -0.0491 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HARTLND3 | 0.9374 | 0.8787 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HARTLND3 | 0.9374 | 0.8787 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ULYSPLT3 | 0.9485 | 0.8247 | -0.1238 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CEDARNL5 | 0.9539 | 0.8936 | -0.0603 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WM BROS3 | 0.9374 | 0.8787 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WM BROS3 | 0.9374 | 0.8787 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | F MONRO2 | >0.95 | 0.8931 | >0.0569 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | F MONRO2 | >0.95 | 0.8931 | >0.0569 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RICHMND5 | 0.9188 | 0.8987 | -0.0201 | 161 | 0.9 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BULLCRK5 | 0.9543 | 0.894 | -0.0603 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CIRCLE 6 | 0.9671 | 0.8992 | -0.0679 | 230 | 0.95 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CIRCLE 6 | 0.9671 | 0.8992 | -0.0679 | 230 | 0.95 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CIRCLE 3 | >0.95 | 0.8994 | >0.0506 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CIRCLE 3 | >0.95 | 0.8994 | >0.0506 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRAXAIR2 | 0.956 | 0.891 | -0.065 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | COLINE 3 | 0.9426 | 0.8858 | -0.0568 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | COLINE 3 | 0.9426 | 0.8858 | -0.0568 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-163 | 0.9686 | 0.9377 | -0.0309 | 345 | 0.95 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-163 | 0.9686 | 0.9377 | -0.0309 | 345 | 0.95 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DVISTA 6 | >0.97 | 0.914 | >0.056 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DVISTA 6 | >0.97 | 0.914 | >0.056 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HILSBOR3 | 0.9431 | 0.8729 | -0.0702 | 115 | 0.93 | 1.05 | 0.20113 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SANTAFJ2 | 0.9305 | 0.8723 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SANTAFJ2 | 0.9305 | 0.8723 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SHARNSP3 | 0.9508 | 0.8118 | -0.139 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STULL 3 | 0.9448 | 0.8923 | -0.0525 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STULL 3 | 0.9448 | 0.8923 | -0.0525 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LAMAR7 | 0.8948 | 0.8338 | -0.061 | 345 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LARNED3 | 0.9168 | 0.8628 | -0.054 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LARNED3 | 0.9168 | 0.8628 | -0.054 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SEOTTWA5 | 0.9408 | 0.8954 | -0.0454 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FAIRGDS3 | 0.9458 | 0.8981 | -0.0477 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FAIRGDS3 | 0.9458 | 0.8981 | -0.0477 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RULETON3 | >0.92 | 0.8991 | >0.0209 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2017-052 | 0.9588 | 0.7684 | -0.1904 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ETHNOL 3 | 0.9315 | 0.8894 | -0.0421 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ETHNOL 3 | 0.9315 | 0.8894 | -0.0421 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMBROSJ3 | 0.9682 | 0.87 | -0.0982 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMBROSJ3 | 0.9682 | 0.87 | -0.0982 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC W 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC W 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | REFINRY3 | 0.9666 | 0.8905 | -0.0761 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | REFINRY3 | 0.9666 | 0.8905 | -0.0761 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMBROS 3 | 0.9682 | 0.87 | -0.0982 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMBROS 3 | 0.9682 | 0.87 | -0.0982 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TRIB SW3 | 0.9469 | 0.7746 | -0.1723 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WGARDNR5 | 0.9543 | 0.894 | -0.0603 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PALMER3 | 0.9475 | 0.7827 | -0.1648 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-162 | 0.9685 | 0.9377 | -0.0308 | 345 | 0.95 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-162 | 0.9685 | 0.9377 | -0.0308 | 345 | 0.95 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VIOLA 7 | >0.97 | 0.941 | >0.029 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VIOLA 7 | >0.97 | 0.941 | >0.029 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SO GATE3 | 0.9585 | 0.858 | -0.1005 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SO GATE3 | 0.9585 | 0.858 | -0.1005 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWLWRNC3 | 0.9468 | 0.898 | -0.0488 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWLWRNC3 | 0.9468 | 0.898 | -0.0488 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-122-TAP | 0.9536 | 0.9068 | -0.0468 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-122-TAP | 0.9536 | 0.9068 | -0.0468 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KERFORD3 | 0.9677 | 0.925 | -0.0427 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KERFORD3 | 0.9677 | 0.925 | -0.0427 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BEELER 3 | 0.9363 | 0.8958 | -0.0405 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CNTRLPL3 | 0.9525 | 0.8963 | -0.0562 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RICE 6 | >0.92 | 0.8966 | >0.0234 | 230 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RICE 6 | >0.92 | 0.8966 | >0.0234 | 230 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U4 3 | 0.9617 | 0.9134 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U4 3 | 0.9617 | 0.9134 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWISVAL6 | 0.9496 | 0.8945 | -0.0551 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWISVAL6 | 0.9496 | 0.8945 | -0.0551 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SCHILNG3 | 0.9567 | 0.8569 | -0.0998 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SCHILNG3 | 0.9567 | 0.8569 | -0.0998 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMAN_W_3 | 0.9679 | 0.9054 | -0.0625 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMAN_W_3 | 0.9679 | 0.9054 | -0.0625 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 166TH 3 | 0.9495 | 0.9293 | -0.0202 | 115 | 0.93 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4CORNER3 | 0.9458 | 0.876 | -0.0698 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4CORNER3 | 0.9458 | 0.876 | -0.0698 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-016 | 0.9251 | 0.8717 | -0.0534 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-016 | 0.9251 | 0.8717 | -0.0534 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EXIDE 3 | 0.9559 | 0.8568 | -0.0991 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EXIDE 3 | 0.9559 | 0.8568 | -0.0991 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MW SOLV2 | 0.9606 | 0.9147 | -0.0459 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | THISTLE7 | 0.9458 | 0.9224 | -0.0234 | 345 | 0.95 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEVEE 3 | >0.95 | 0.9143 | >0.0357 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEVEE 3 | >0.95 | 0.9143 | >0.0357 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | COLINE 2 | 0.9482 | 0.8927 | -0.0555 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | COLINE 2 | 0.9482 | 0.8927 | -0.0555 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GRANT 3 | 0.917 | 0.8518 | -0.0652 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WTCLFTP3 | 0.9569 | 0.8392 | -0.1177 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 12&CLAY3 | 0.9289 | 0.87 | -0.0589 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 12&CLAY3 | 0.9289 | 0.87 | -0.0589 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOOKJCT3 | 0.9419 | 0.8849 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOOKJCT3 | 0.9419 | 0.8849 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 27CROCO3 | 0.9385 | 0.8808 | -0.0577 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 27CROCO3 | 0.9385 | 0.8808 | -0.0577 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-122 | 0.9594 | 0.9122 | -0.0472 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-122 | 0.9594 | 0.9122 | -0.0472 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2ND ELM2 | >0.95 | 0.8938 | >0.0562 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 2ND ELM2 | >0.95 | 0.8938 | >0.0562 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | INDNOLA3 | 0.9324 | 0.874 | -0.0584 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | INDNOLA3 | 0.9324 | 0.874 | -0.0584 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JARBALO3 | 0.9665 | 0.9268 | -0.0397 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JARBALO3 | 0.9665 | 0.9268 | -0.0397 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KSU W 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KSU W 3 | >0.95 | 0.9163 | >0.0337 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | E MADSN2 | >0.95 | 0.8932 | >0.0568 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | E MADSN2 | >0.95 | 0.8932 | >0.0568 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G14_001_1 | 0.9579 | 0.9295 | -0.0284 | 345 | 0.95 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MANTER 2 | >0.92 | 0.8506 | >0.0694 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G15_021_1 | 0.9633 | 0.7827 | -0.1806 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FMC 3 | 0.9521 | 0.9039 | -0.0482 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FMC 3 | 0.9521 | 0.9039 | -0.0482 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 7 | 0.9615 | 0.9115 | -0.05 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 7 | 0.9615 | 0.9115 | -0.05 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 6 | 0.9606 | 0.9093 | -0.0513 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 6 | 0.9606 | 0.9093 | -0.0513 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TCHOPE 3 | 0.9499 | 0.8912 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TCHOPE 3 | 0.9499 | 0.8912 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 3 | 0.9627 | 0.8629 | -0.0998 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SUMMIT 3 | 0.9627 | 0.8629 | -0.0998 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CORONAD3 | 0.9614 | 0.8718 | -0.0896 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CORONAD3 | 0.9614 | 0.8718 | -0.0896 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CITIES 3 | >0.95 | 0.8875 | >0.0625 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CITIES 3 | >0.95 | 0.8875 | >0.0625 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OSAGE J3 | 0.9513 | 0.8644 | -0.0869 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OSAGE J3 | 0.9513 | 0.8644 | -0.0869 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THSTJ3 | 0.9455 | 0.897 | -0.0485 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THSTJ3 | 0.9455 | 0.897 | -0.0485 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ANZIO 3 | >0.95 | 0.9126 | >0.0374 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ANZIO 3 | >0.95 | 0.9126 | >0.0374 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-004-TAP | 0.9645 | 0.9153 | -0.0492 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-004-TAP | 0.9645 | 0.9153 | -0.0492 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NINN1WF7 | >0.97 | 0.9425 | >0.0275 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NINN1WF7 | >0.97 | 0.9425 | >0.0275 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MUSCOTA2 | 0.9258 | 0.8728 | -0.053 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MUSCOTA2 | 0.9258 | 0.8728 | -0.053 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TONGATP3 | 0.96 | 0.9173 | -0.0427 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMANHAT3 | 0.9679 | 0.9054 | -0.0625 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMANHAT3 | 0.9679 | 0.9054 | -0.0625 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SEWARD 3 | 0.9422 | 0.8948 | -0.0474 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SEWARD 3 | 0.9422 | 0.8948 | -0.0474 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BISMARK3 | 0.9508 | 0.9028 | -0.048 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BISMARK3 | 0.9508 | 0.9028 | -0.048 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BEARCRK3 | 0.9548 | 0.7573 | -0.1975 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOONLT 5 | 0.9465 | 0.8925 | -0.054 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AUBURN 3 | 0.9406 | 0.8808 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AUBURN 3 | 0.9406 | 0.8808 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILE3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILE3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-052-TAP | 0.9588 | 0.7684 | -0.1904 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AUBURN 6 | 0.9463 | 0.8863 | -0.06 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AUBURN 6 | 0.9463 | 0.8863 | -0.06 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CNTRLXN3 | 0.9351 | 0.8763 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CNTRLXN3 | 0.9351 | 0.8763 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTONV2 | 0.9438 | 0.8919 | -0.0519 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTONV2 | 0.9438 | 0.8919 | -0.0519 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KANARAD3 | 0.9637 | 0.8696 | -0.0941 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SPRGCRK3 | 0.9489 | 0.8792 | -0.0697 | 115 | 0.93 | 1.05 | 0.20113 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FLORENC3 | 0.9479 | 0.881 | -0.0669 | 115 | 0.93 | 1.05 | 0.20113 | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SANTAFE2 | 0.9305 | 0.8723 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SANTAFE2 | 0.9305 | 0.8723 | -0.0582 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | UNIONRG3 | 0.9512 | 0.8926 | -0.0586 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | UNIONRG3 | 0.9512 | 0.8926 | -0.0586 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | UNIONRG6 | 0.9669 | 0.9089 | -0.058 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | UNIONRG6 | 0.9669 | 0.9089 | -0.058 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JOHNSON2 | 0.9614 | 0.787 | -0.1744 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-005-TAP | 0.9586 | 0.9269 | -0.0317 | 161 | 0.93 | 1.05 | 0.0494 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-005-TAP | 0.9586 | 0.9269 | -0.0317 | 161 | 0.93 | 1.05 | 0.0494 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FINNEY 7 | 0.9242 | 0.8728 | -0.0514 | 345 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OSAGE 3 | 0.9504 | 0.8634 | -0.087 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OSAGE 3 | 0.9504 | 0.8634 | -0.087 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GARDNER5 | 0.9468 | 0.8928 | -0.054 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SPRUCE 3 | 0.9668 | 0.9281 | -0.0387 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SPRUCE 3 | 0.9668 | 0.9281 | -0.0387 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CROOKED3 | 0.9405 | 0.8807 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CROOKED3 | 0.9405 | 0.8807 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WICHITA7 | 0.9545 | 0.9171 | -0.0374 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WICHITA7 | 0.9545 | 0.9171 | -0.0374 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 41CALIF3 | 0.9362 | 0.8779 | -0.0583 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 41CALIF3 | 0.9362 | 0.8779 | -0.0583 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BENTON 7 | 0.9673 | 0.9365 | -0.0308 | 345 | 0.95 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BENTON 7 | 0.9673 | 0.9365 | -0.0308 | 345 | 0.95 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SALINA 3 | 0.9594 | 0.8578 | -0.1016 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SALINA 3 | 0.9594 | 0.8578 | -0.1016 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NPHILPJ3 | 0.9571 | 0.8583 | -0.0988 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NPHILPJ3 | 0.9571 | 0.8583 | -0.0988 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SHAWNEE3 | 0.9421 | 0.8813 | -0.0608 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SHAWNEE3 | 0.9421 | 0.8813 | -0.0608 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WREN 3 | 0.9569 | 0.9082 | -0.0487 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WREN 3 | 0.9569 | 0.9082 | -0.0487 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOCKBRD3 | 0.948 | 0.8986 | -0.0494 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOCKBRD3 | 0.948 | 0.8986 | -0.0494 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLADS3 | 0.9556 | 0.9079 | -0.0477 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLADS3 | 0.9556 | 0.9079 | -0.0477 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GALE 2 | 0.9442 | 0.9162 | -0.028 | 69 | 0.93 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GALE 2 | 0.9442 | 0.9162 | -0.028 | 69 | 0.93 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SADLHRN3 | 0.9319 | 0.8864 | -0.0455 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SADLHRN3 | 0.9319 | 0.8864 | -0.0455 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMCPHER6 | 0.9622 | 0.8897 | -0.0725 | 230 | 0.95 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMCPHER6 | 0.9622 | 0.8897 | -0.0725 | 230 | 0.95 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GRTBEND6 | 0.9443 | 0.8907 | -0.0536 | 230 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GRTBEND6 | 0.9443 | 0.8907 | -0.0536 | 230 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMCPHER3 | 0.9661 | 0.891 | -0.0751 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMCPHER3 | 0.9661 | 0.891 | -0.0751 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ROSEHIL7 | >0.97 | 0.9461 | >0.0239 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ROSEHIL7 | >0.97 | 0.9461 | >0.0239 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PAWN-ED3 | 0.9222 | 0.8694 | -0.0528 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PAWN-ED3 | 0.9222 | 0.8694 | -0.0528 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VALLEY22 | 0.9362 | 0.8826 | -0.0536 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VALLEY22 | 0.9362 | 0.8826 | -0.0536 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WILLIAM3 | 0.9495 | 0.7466 | -0.2029 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 87TH 7 | 0.9378 | 0.8977 | -0.0401 | 345 | 0.95 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILW3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILW3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SHERWOD3 | 0.9388 | 0.879 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SHERWOD3 | 0.9388 | 0.879 | -0.0598 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FORBES 3 | 0.9362 | 0.8774 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FORBES 3 | 0.9362 | 0.8774 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | QUINTON3 | 0.9296 | 0.8707 | -0.0589 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | QUINTON3 | 0.9296 | 0.8707 | -0.0589 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AEC 3 | >0.95 | 0.8823 | >0.0677 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AEC 3 | >0.95 | 0.8823 | >0.0677 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HEIZER 6 | 0.9443 | 0.8908 | -0.0535 | 230 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HEIZER 6 | 0.9443 | 0.8908 | -0.0535 | 230 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RVROAD | 0.9358 | 0.8952 | -0.0406 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RVROAD | 0.9358 | 0.8952 | -0.0406 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ASGI15_001_1 | 0.9338 | 0.8919 | -0.0419 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ASGI15_001_1 | 0.9338 | 0.8919 | -0.0419 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WHEATLD3 | >0.95 | 0.897 | >0.053 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WHEATLD3 | >0.95 | 0.897 | >0.053 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTHST3 | 0.9631 | 0.8618 | -0.1013 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTHST3 | 0.9631 | 0.8618 | -0.1013 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRQN_WIND5 | 0.9474 | 0.8965 | -0.0509 | 161 | 0.9 | 1.05 | 0.0494 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRQN_WIND5 | 0.9474 | 0.8965 | -0.0509 | 161 | 0.9 | 1.05 | 0.0494 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SALTCRK3 | >0.95 | 0.8891 | >0.0609 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SALTCRK3 | >0.95 | 0.8891 | >0.0609 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | INDIANH3 | 0.9347 | 0.8754 | -0.0593 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | INDIANH3 | 0.9347 | 0.8754 | -0.0593 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | THORNTN3 | 0.9666 | 0.928 | -0.0386 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | THORNTN3 | 0.9666 | 0.928 | -0.0386 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OLATHE 5 | 0.9372 | 0.8982 | -0.039 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MATTERS3 | >0.95 | 0.9149 | >0.0351 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MATTERS3 | >0.95 | 0.9149 | >0.0351 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VAUGHN 3 | >0.95 | 0.8638 | >0.0862 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | VAUGHN 3 | >0.95 | 0.8638 | >0.0862 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EAST ST3 | 0.9683 | 0.8603 | -0.108 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EAST ST3 | 0.9683 | 0.8603 | -0.108 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U3 3 | 0.9595 | 0.9111 | -0.0484 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U3 3 | 0.9595 | 0.9111 | -0.0484 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAVIS 3 | >0.95 | 0.8895 | >0.0605 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAVIS 3 | >0.95 | 0.8895 | >0.0605 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SEMCRDE3 | 0.9258 | 0.8833 | -0.0425 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SEMCRDE3 | 0.9258 | 0.8833 | -0.0425 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRATT 3 | 0.9358 | 0.8952 | -0.0406 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PRATT 3 | 0.9358 | 0.8952 | -0.0406 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAVIS 2 | >0.95 | 0.8977 | >0.0523 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DAVIS 2 | >0.95 | 0.8977 | >0.0523 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC 2 | 0.9353 | 0.8775 | -0.0578 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC 2 | 0.9353 | 0.8775 | -0.0578 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KINGMAN7 | >0.97 | 0.9415 | >0.0285 | 345 | 0.95 | 1.05 | 0.12545 | 8599: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KINGMAN7 | >0.97 | 0.9415 | >0.0285 | 345 | 0.95 | 1.05 | 0.12545 | 104271: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532791 BENTON 7 345 532796 WICHITA7 345 1 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532791 BENTON 7 345 588320 GEN-2016-162 345 1 532791 BENTON 7 345 997903 BENT TX-1 138 1 532791 BENTON 7 345 997902 BENT TX-2 138 1 532791 BENTON 7 345 997910 BENT TX-1 138 1 532791 BENTON 7 345 997909 BENT TX-2 138 1 532791 BENTON 7 345 997906 BENT TX-1 138 1 532791 BENTON 7 345 997905 BENT TX-2 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PUCKET 3 | 0.9431 | 0.8123 | -0.1308 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOYT 3 | 0.9634 | 0.9106 | -0.0528 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOYT 3 | 0.9634 | 0.9106 | -0.0528 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOYT 7 | 0.958 | 0.9078 | -0.0502 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HOYT 7 | 0.958 | 0.9078 | -0.0502 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOUNDRG3 | 0.961 | 0.8902 | -0.0708 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOUNDRG3 | 0.961 | 0.8902 | -0.0708 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NINNESC3 | 0.9338 | 0.8919 | -0.0419 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NINNESC3 | 0.9338 | 0.8919 | -0.0419 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NCFOUND3 | >0.95 | 0.9155 | >0.0345 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NCFOUND3 | >0.95 | 0.9155 | >0.0345 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MARMTNW5 | 0.9557 | 0.913 | -0.0427 | 161 | 0.93 | 1.05 | 0.0494 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MARMTNW5 | 0.9557 | 0.913 | -0.0427 | 161 | 0.93 | 1.05 | 0.0494 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997906 N345 TX-2 161 1 532793 NEOSHO 7 345 997894 N345 TX-1 138 1 532793 NEOSHO 7 345 997913 N345 TX-2 161 1 532793 NEOSHO 7 345 997901 N345 TX-1 138 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U5 6 | 0.9548 | 0.905 | -0.0498 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEC U5 6 | 0.9548 | 0.905 | -0.0498 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRON 2 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRON 2 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMOKYHLLS3 | 0.9565 | 0.8568 | -0.0997 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SMOKYHLLS3 | 0.9565 | 0.8568 | -0.0997 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WILDCAT3 | >0.95 | 0.9184 | >0.0316 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WILDCAT3 | >0.95 | 0.9184 | >0.0316 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PEIL 3 | >0.95 | 0.9186 | >0.0314 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PEIL 3 | >0.95 | 0.9186 | >0.0314 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NSI | 0.9667 | 0.8835 | -0.0832 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KU CAMP3 | 0.9451 | 0.8967 | -0.0484 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KU CAMP3 | 0.9451 | 0.8967 | -0.0484 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BRKRIDG5 | 0.935 | 0.8989 | -0.0361 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRONJ2 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MWIRONJ2 | >0.95 | 0.8975 | >0.0525 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | COLBY 2 | 1.2159 | 1.2794 | 0.0635 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | AMOCO 3 | 0.9619 | 0.8973 | -0.0646 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 17&FAIR3 | 0.9317 | 0.8724 | -0.0593 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 17&FAIR3 | 0.9317 | 0.8724 | -0.0593 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WEMPORI3 | >0.95 | 0.8683 | >0.0817 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WEMPORI3 | >0.95 | 0.8683 | >0.0817 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EDWARDS3 | 0.9226 | 0.8703 | -0.0523 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EDWARDS3 | 0.9226 | 0.8703 | -0.0523 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WALNUT 2 | 0.9618 | 0.916 | -0.0458 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BALDCRK3 | 0.9526 | 0.9039 | -0.0487 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BALDCRK3 | 0.9526 | 0.9039 | -0.0487 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SYRACUS3 | 0.952 | 0.7452 | -0.2068 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BUFF_DUNES 7 | 0.9293 | 0.8776 | -0.0517 | 345 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMCPHER3 | >0.95 | 0.895 | >0.055 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WMCPHER3 | >0.95 | 0.895 | >0.055 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 6 | 0.9696 | 0.9052 | -0.0644 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 6 | 0.9696 | 0.9052 | -0.0644 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 7 | 0.9698 | 0.9061 | -0.0637 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 7 | 0.9698 | 0.9061 | -0.0637 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RANSOM 2 | 0.9367 | 0.8943 | -0.0424 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RANSOM 3 | 0.9398 | 0.8977 | -0.0421 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 3 | >0.95 | 0.8979 | >0.0521 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MORRIS 3 | >0.95 | 0.8979 | >0.0521 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-046 | 0.9292 | 0.8962 | -0.033 | 345 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-046 | 0.9292 | 0.8962 | -0.033 | 345 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | QUARRY 5 | 0.9427 | 0.8933 | -0.0494 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 29 GAGE3 | 0.9315 | 0.8724 | -0.0591 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 29 GAGE3 | 0.9315 | 0.8724 | -0.0591 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THST 3 | 0.9447 | 0.8964 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THST 3 | 0.9447 | 0.8964 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G14_001T | 0.9579 | 0.9295 | -0.0284 | 345 | 0.95 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 6TH ST 3 | 0.9541 | 0.9058 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 6TH ST 3 | 0.9541 | 0.9058 | -0.0483 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EEUREKA3 | 0.9615 | 0.8539 | -0.1076 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EEUREKA3 | 0.9615 | 0.8539 | -0.1076 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ARNOLD 2 | 0.9617 | 0.9159 | -0.0458 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ARNOLD 3 | 0.968 | 0.9248 | -0.0432 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ARNOLD 3 | 0.968 | 0.9248 | -0.0432 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NESSCTY3 | 0.938 | 0.8912 | -0.0468 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PK_GOAB3 | 0.9431 | 0.8123 | -0.1308 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SCRANTN3 | 0.9475 | 0.8704 | -0.0771 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SCRANTN3 | 0.9475 | 0.8704 | -0.0771 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NCTYSVC2 | >0.95 | 0.878 | >0.072 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NCTYSVC2 | >0.95 | 0.878 | >0.072 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EXIDE J3 | 0.9576 | 0.8587 | -0.0989 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EXIDE J3 | 0.9576 | 0.8587 | -0.0989 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWITZER5 | 0.934 | 0.8959 | -0.0381 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LANG 7 | >0.97 | 0.8608 | >0.1092 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LANG 7 | >0.97 | 0.8608 | >0.1092 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LANG 3 | 0.9691 | 0.8608 | -0.1083 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LANG 3 | 0.9691 | 0.8608 | -0.1083 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ST JOHN3 | 0.9301 | 0.8811 | -0.049 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ST JOHN3 | 0.9301 | 0.8811 | -0.049 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BIG BOW 3 | 0.9553 | 0.8017 | -0.1536 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SPRINT25 | 0.9329 | 0.8956 | -0.0373 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-046-TAP | 0.9292 | 0.8962 | -0.033 | 345 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-046-TAP | 0.9292 | 0.8962 | -0.033 | 345 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PHILIPS3 | 0.9577 | 0.8588 | -0.0989 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PHILIPS3 | 0.9577 | 0.8588 | -0.0989 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HTI JCT3 | 0.9624 | 0.9109 | -0.0515 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HTI JCT3 | 0.9624 | 0.9109 | -0.0515 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CARB-KW 3 | 0.9448 | 0.8769 | -0.0679 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CARB-KW 3 | 0.9448 | 0.8769 | -0.0679 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DEERCRK2 | 0.9317 | 0.8736 | -0.0581 | 69 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | DEERCRK2 | 0.9317 | 0.8736 | -0.0581 | 69 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | BNSF 5 | 0.9509 | 0.8933 | -0.0576 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | N TYLER3 | 0.9297 | 0.871 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | N TYLER3 | 0.9297 | 0.871 | -0.0587 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC E 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TEC E 3 | 0.942 | 0.885 | -0.057 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STULL T3 | 0.9448 | 0.8923 | -0.0525 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | STULL T3 | 0.9448 | 0.8923 | -0.0525 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYCSS3 | 0.9541 | 0.886 | -0.0681 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYCSS3 | 0.9541 | 0.886 | -0.0681 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GRANTTP3 | 0.9172 | 0.8521 | -0.0651 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HTI 3 | 0.9622 | 0.9107 | -0.0515 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HTI 3 | 0.9622 | 0.9107 | -0.0515 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 29EVENG3 | 0.9322 | 0.873 | -0.0592 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 29EVENG3 | 0.9322 | 0.873 | -0.0592 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CRAWFRD3 | 0.9569 | 0.856 | -0.1009 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CRAWFRD3 | 0.9569 | 0.856 | -0.1009 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CRAIG 7 | 0.939 | 0.8961 | -0.0429 | 345 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CHENEY 2 | 0.9542 | 0.9265 | -0.0277 | 69 | 0.93 | 1.05 | 0.08481 | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CHENEY 2 | 0.9542 | 0.9265 | -0.0277 | 69 | 0.93 | 1.05 | 0.08481 | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997929 VIOLA TX-1 138 1 532798 VIOLA 7 345 997928 VIOLA TX-2 138 2 532798 VIOLA 7 345 997874 SCJ TX-1 138 2 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 532798 VIOLA 7 345 997881 SCJ TX-1 138 2 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TRIBUNE3 | 0.9469 | 0.7695 | -0.1774 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MANVILE3 | 0.9624 | 0.886 | -0.0764 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MANVILE3 | 0.9624 | 0.886 | -0.0764 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RENO 3 | >0.95 | 0.8981 | >0.0519 | 115 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RENO 3 | >0.95 | 0.8981 | >0.0519 | 115 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RENO 7 | 0.9349 | 0.9025 | -0.0324 | 345 | 0.95 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LEOTI 3 | 0.9466 | 0.8414 | -0.1052 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NESCTY 3 | 0.938 | 0.8912 | -0.0468 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMANHAT3 | >0.95 | 0.9144 | >0.0356 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMANHAT3 | >0.95 | 0.9144 | >0.0356 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NTHLAND3 | 0.9358 | 0.878 | -0.0578 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NTHLAND3 | 0.9358 | 0.878 | -0.0578 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SELKIRK3 | 0.9461 | 0.8196 | -0.1265 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYCTR3 | 0.9578 | 0.89 | -0.0678 | 115 | 0.93 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CLAYCTR3 | 0.9578 | 0.89 | -0.0678 | 115 | 0.93 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JEC 6 | >0.97 | 0.919 | >0.051 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JEC 6 | >0.97 | 0.919 | >0.051 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HICKOCK2 | 0.9578 | 0.893 | -0.0648 | 69 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | HICKOCK3 | 0.963 | 0.8985 | -0.0645 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMPEC 7 | >0.97 | 0.9306 | >0.0394 | 345 | 0.95 | 1.05 | 0.0897 | P23:345:WERE:JEC_345-17:: | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G17-032-TAP | 0.9045 | 0.8453 | -0.0592 | 345 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | RILEY 5 | 0.9329 | 0.8957 | -0.0372 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLADN3 | 0.9555 | 0.9079 | -0.0476 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MIDLADN3 | 0.9555 | 0.9079 | -0.0476 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ALXNDR 3 | 0.9409 | 0.8894 | -0.0515 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LAWHILL6 | 0.9541 | 0.9044 | -0.0497 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | LAWHILL6 | 0.9541 | 0.9044 | -0.0497 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | PLSTVAL5 | 0.9512 | 0.8941 | -0.0571 | 161 | 0.9 | 1.05 | 0.08461 | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997753 WEST GARDN11 161 11 542965 W.GRDNR7 345 997760 WEST GARDN11 161 11 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN N 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN N 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CITYSVC2 | >0.95 | 0.8778 | >0.0722 | 69 | 0.93 | 1.05 | 0.20113 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | CITYSVC2 | >0.95 | 0.8778 | >0.0722 | 69 | 0.93 | 1.05 | 0.20113 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997948 RENO TX-1 115 1 532771 RENO 7 345 997947 RENO TX-2 115 1 532771 RENO 7 345 997954 RENO TX-1 115 1 532771 RENO 7 345 997953 RENO TX-2 115 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 4VAN 3 | 0.9285 | 0.8697 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | WTCLF 3 | 0.9566 | 0.8389 | -0.1177 | 115 | 0.9 | 1.05 | 0.05626 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997962 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997962 HOLCOMB 115 1 531449 HOLCOMB7 345 997968 HOLCOMB 115 1 531448 HOLCOMB3 115 997968 HOLCOMB 115 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMANHAT6 | >0.97 | 0.917 | >0.053 | 230 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EMANHAT6 | >0.97 | 0.917 | >0.053 | 230 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SPRGHL 5 | 0.9492 | 0.9133 | -0.0359 | 161 | 0.93 | 1.05 | 0.04245 | 84357: 541198 PECULR 7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 997752 STILWELL11 161 11 542968 STILWEL7 345 997751 STILWELL22 161 22 542968 STILWEL7 345 997759 STILWELL11 161 11 542968 STILWEL7 345 997758 STILWELL22 161 22 542968 STILWEL7 345 997755 STILWELL11 161 11 542968 STILWEL7 345 997754 STILWELL22 161 22 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ST-JOHN3 | 0.93 | 0.881 | -0.049 | 115 | 0.9 | 1.05 | 0.0609 | 8624: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | ST-JOHN3 | 0.93 | 0.881 | -0.049 | 115 | 0.9 | 1.05 | 0.0609 | 104292: 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 532872 EMCPHER6 230 532873 SUMMIT 6 230 1 532873 SUMMIT 6 230 532874 UNIONRG6 230 1 532873 SUMMIT 6 230 997944 SUMM TX-1 230 1 532873 SUMMIT 6 230 997916 SUMM TX-2 115 1 532873 SUMMIT 6 230 997915 SUMM TX-3 115 1 532873 SUMMIT 6 230 997950 SUMM TX-1 230 1 532873 SUMMIT 6 230 997923 SUMM TX-2 115 1 532873 SUMMIT 6 230 997922 SUMM TX-3 115 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997919 SUMM TX-2 115 1 532873 SUMMIT 6 230 997918 SUMM TX-3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EDUCATE3 | 0.931 | 0.8722 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EDUCATE3 | 0.931 | 0.8722 | -0.0588 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EUDORA 3 | 0.9447 | 0.9008 | -0.0439 | 115 | 0.93 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | EUDORA 3 | 0.9447 | 0.9008 | -0.0439 | 115 | 0.93 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-111-TAP | 0.9448 | 0.9019 | -0.0429 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | G16-111-TAP | 0.9448 | 0.9019 | -0.0429 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JEC N 7 | >0.97 | 0.919 | >0.051 | 345 | 0.95 | 1.05 | 0.05356 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | JEC N 7 | >0.97 | 0.919 | >0.051 | 345 | 0.95 | 1.05 | 0.05356 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | Internal

## Stability Analysis
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2
4 | 19W | Base | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_1_P1_SHAYS6 | Apply 3-phase fault on S HAYS6 to POSTROCK6 230kV transmission line CKT 1, near S HAYS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_2_P1_POSTROCK6 | Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_3_P1_HEIZER3 | Apply 3-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near HEIZER 3 115kV for 7 cycles.Open the faulted Three Winding. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_4_P1_RICE | Apply 3-phase fault on RICE 115kV/230kV/12.47kV transformer CKT 1, near RICE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 0.70s | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 0.72s | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 1.70s | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 0.36s | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 0.36s | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_5_P1_SPERVIL7 | Apply 3-phase fault on SPERVIL7 to BUCKNER7 345kV transmission line CKT 1, near SPERVIL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 10000.00pu, MaxDur: 0.36s | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_6_P1_CIRCLE6 | Apply 3-phase fault on CIRCLE 6 230kV/13.8kV/115kV transformer CKT 1, near CIRCLE 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes