4 | 21L | Sensitivity | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_7_P1_ELLSWTP3 | Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_8_P1_EHALLTP3 | Apply 3-phase fault on EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1, near EHALLTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_9_P1_24-FREY3 | Apply 3-phase fault on 24-FREY3 to 2ND-KS 3 115kV transmission line CKT 1, near 24-FREY3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_10_P1_GRTBEND3 | Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_11_P1_GRTBEND3 | Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_12_P1_GRTBEND3 | Apply 3-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_13_P1_GRTBEND6 | Apply 3-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_14_P1_GRTBEND6 | Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_15_P1_GRTBEND6 | Apply 3-phase fault on GRTBEND6 to SPEARVL6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_16_P1_N-GBEND3 | Apply 3-phase fault on 24-FREY3 to N-GBEND3 115kV transmission line CKT 1, near N-GBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_17_P1_SMITH-C3 | Apply 3-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_18_P1_SMITH-C3 | Apply 3-phase fault on PHLBURG3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_19_P1_SPEARVL6 | Apply 3-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_20_P1_SPEARVL6 | Apply 3-phase fault on SPEARVL3 115kV/230kV/13.8kV transformer CKT 1, near SPEARVL6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_21_P1_POI | Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.86pu | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_22_P1_POI | Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_23_P4_HEIZER3 | Apply single-phase fault on HEIZER 2 69kV/115kV/12.5kV transformer CKT 2, near HEIZER 3 115kV for 16 cycles with stuck breaker at HEIZER 3. Open the faulted Three Winding. Simultaneously open HEIZER 2 69kV/115kV/12.5kV transformer CKT 3 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_24_P4_SPERVIL7 | Apply single-phase fault on SPERVIL7 to CLARKCOUNTY7 345kV transmission line CKT 1, near SPERVIL7 345kV for 16 cycles with stuck breaker at SPERVIL7. Open the faulted Transmission Circuit. Simultaneously open SPERVIL7 to IRONWOOD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No - Min: 0.86pu | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_25_P4_ELLSWTP3 | Apply single-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 16 cycles with stuck breaker at ELLSWTP3. Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Simultaneously open ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_26_P4_GRTBEND3 | Apply single-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Three Winding. Simultaneously open HEIZER 3 to GRTBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_27_P4_GRTBEND3 | Apply single-phase fault on GBENDTP3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 16 cycles with stuck breaker at GRTBEND3. Open the faulted Transmission Circuit. Simultaneously open GBENDTP3 to SEWARD 3 115kV transmission line CKT 1.Simultaneously open GRTBEND3 to N-GBEND3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_28_P4_GRTBEND6 | Apply single-phase fault on HEIZER 3 115kV/12.5kV/230kV transformer CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Three Winding. Simultaneously open GRTBEND3 115kV/230kV/13.8kV transformer CKT 1.Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_29_P4_GRTBEND6 | Apply single-phase fault on S HAYS6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open GRTBEND6 to SPEARVL6 230kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_30_P4_GRTBEND6 | Apply single-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 16 cycles with stuck breaker at GRTBEND6. Open the faulted Transmission Circuit. Simultaneously open HEIZER 6 to GRTBEND6 230kV transmission line CKT 1.Simultaneously open HEIZER 3 115kV/12.5kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_31_P4_SMITH-C3 | Apply single-phase fault on GLENELD3 to SMITH-C3 115kV transmission line CKT 1, near SMITH-C3 115kV for 16 cycles with stuck breaker at SMITH-C3. Open the faulted Transmission Circuit. Simultaneously open IONIA to SMITH-C3 115kV transmission line CKT 1.Simultaneously open IONIA to JEWELL 3 115kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_32_P4_SPEARVL6 | Apply single-phase fault on SPERTER1 13.8kV/345kV/230kV transformer CKT 1, near SPEARVL6 230kV for 16 cycles with stuck breaker at SPEARVL6. Open the faulted Three Winding. Simultaneously open SPEARVL3 115kV/230kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_33_P6_POSTROCK6 | Prior Outage of SPERTER1 13.8kV/345kV/230kV transformer CKT 1Apply 3-phase fault on POSTROCK7 345kV/230kV/13.8kV transformer CKT 1, near POSTROCK6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_34_P6_ELLSWTP3 | Prior Outage of WALDO 3 to POI 115kV transmission line CKT 1Apply 3-phase fault on ROLLHLS3 to EHALLTP3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ELLSWTP3 to ROLLHLS3 115kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.84pu | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_35_P6_ELLSWTP3 | Prior Outage of EHALLTP3 to ELLSWTH3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1, near ELLSWTP3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_36_P6_GRTBEND3 | Prior Outage of HEIZER 3 115kV/12.5kV/230kV transformer CKT 1Prior Outage of HEIZER 6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_37_P6_GRTBEND3 | Prior Outage of HEIZER 3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on GRTBEND3 115kV/230kV/13.8kV transformer CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_38_P6_GRTBEND3 | Prior Outage of GRTBEND3 115kV/230kV/13.8kV transformer CKT 1Apply 3-phase fault on HEIZER 3 to GRTBEND3 115kV transmission line CKT 1, near GRTBEND3 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_39_P6_GRTBEND6 | Prior Outage of S HAYS6 to GRTBEND6 230kV transmission line CKT 1Apply 3-phase fault on CIRCLE 6 to GRTBEND6 230kV transmission line CKT 1, near GRTBEND6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_40_P6_POI | Prior Outage of ELLSWTP3 to GRTBEND3 115kV transmission line CKT 1Apply 3-phase fault on WALDO 3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Base | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Sensitivity | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 19W | Transfer | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Base | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Sensitivity | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21L | Transfer | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Base | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | Yes
4 | 21S | Sensitivity | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 21S | Transfer | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Base | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.82pu | Yes | Yes | Yes
4 | 28S | Sensitivity | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
4 | 28S | Transfer | FLT_41_P6_POI | Prior Outage of PHLBURG3 to SMITH-C3 115kV transmission line CKT 1Apply 3-phase fault on ELLSWTP3 to POI 115kV transmission line CKT 1, near POI 115kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | Yes

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
GEN-2020-056 | 539703 | Bus: 539703 ID: R1 Name: RUSSELL1 | 4 | ALL | 6.37
GEN-2020-056 | 539703 | Bus: 539703 ID: R2 Name: RUSSELL1 | 4 | ALL | 6.18
GEN-2020-056 | 539703 | Bus: 539703 ID: R7 Name: RUSSELL1 | 4 | ALL | 3.21
GEN-2020-056 | 539703 | Bus: 539703 ID: R8 Name: RUSSELL1 | 4 | ALL | 2.55
GEN-2020-056 | 539703 | Bus: 539703 ID: R9 Name: RUSSELL1 | 4 | ALL | 2.41
GEN-2020-056 | 539703 | Bus: 539703 ID: RA Name: RUSSELL1 | 4 | ALL | 3.08
GEN-2020-056 | 539757 | Bus: 539703 ID: RB Name: RUSSELL1 | 4 | ALL | 3.16
GEN-2020-056 | 539757 | Bus: 539757 ID: L1 Name: ESTHLL 1 | 4 | ALL | 1
GEN-2020-056 | 539757 | Bus: 539757 ID: L2 Name: ESTHLL 1 | 4 | ALL | 0.8
GEN-2020-056 | 539757 | Bus: 539757 ID: L4 Name: ESTHLL 1 | 4 | ALL | 0.6
GEN-2020-056 | 539757 | Bus: 539757 ID: L5 Name: ESTHLL 1 | 4 | ALL | 1
GEN-2020-056 | 539757 | Bus: 539757 ID: L6 Name: ESTHLL 1 | 4 | ALL | 1.5
GEN-2020-056 | 539731 | Bus: 539757 ID: L7 Name: ESTHLL 1 | 4 | ALL | 2.5
GEN-2020-056 | 539731 | Bus: 539731 ID: O1 Name: SMITH-C1 | 4 | ALL | 1.58
GEN-2020-056 | 539731 | Bus: 539731 ID: O2 Name: SMITH-C1 | 4 | ALL | 1.38
GEN-2020-056 | 539731 | Bus: 539731 ID: O3 Name: SMITH-C1 | 4 | ALL | 0.58
GEN-2020-056 | 539731 | Bus: 539731 ID: O4 Name: SMITH-C1 | 4 | ALL | 0.38
GEN-2020-056 | 539731 | Bus: 539731 ID: O5 Name: SMITH-C1 | 4 | ALL | 0.38
GEN-2020-056 | 539677 | Bus: 539731 ID: O6 Name: SMITH-C1 | 4 | ALL | 0.63
GEN-2020-056 | 539721 | Bus: 539677 ID: 3 Name: GRTBEND1 | 4 | ALL | 93
GEN-2020-056 | 539721 | Bus: 539721 ID: H2 Name: N-GBEND1 | 4 | ALL | 1
GEN-2020-056 | 539721 | Bus: 539721 ID: H6 Name: N-GBEND1 | 4 | ALL | 1.72
GEN-2020-056 | 539721 | Bus: 539721 ID: H7 Name: N-GBEND1 | 4 | ALL | 3.5
GEN-2020-056 | 530620 | Bus: 539721 ID: H8 Name: N-GBEND1 | 4 | ALL | 6.71
GEN-2020-056 | 530620 | Bus: 530620 ID: S1 Name: LYONS 3 | 4 | ALL | 1.3
GEN-2020-056 | 530620 | Bus: 530620 ID: S2 Name: LYONS 3 | 4 | ALL | 0.4
GEN-2020-056 | 530620 | Bus: 530620 ID: S3 Name: LYONS 3 | 4 | ALL | 2.4
GEN-2020-056 | 530620 | Bus: 530620 ID: S4 Name: LYONS 3 | 4 | ALL | 1
GEN-2020-056 | 530620 | Bus: 530620 ID: S5 Name: LYONS 3 | 4 | ALL | 1.3
GEN-2020-056 | 530620 | Bus: 530620 ID: S6 Name: LYONS 3 | 4 | ALL | 1.3
GEN-2020-056 | 530690 | Bus: 530620 ID: S7 Name: LYONS 3 | 4 | ALL | 1.3
GEN-2020-056 | 530603 | Bus: 530690 ID: 1 Name: PRWINDG1 | 4 | ALL | 201
GEN-2020-056 | 530603 | Bus: 530603 ID: L1 Name: LACROS 3 | 4 | ALL | 1.064
GEN-2020-056 | 530603 | Bus: 530603 ID: L2 Name: LACROS 3 | 4 | ALL | 1.064
GEN-2020-056 | 530603 | Bus: 530603 ID: L5 Name: LACROS 3 | 4 | ALL | 1.4
GEN-2020-056 | 530624 | Bus: 530603 ID: L6 Name: LACROS 3 | 4 | ALL | 1.4
GEN-2020-056 | 530624 | Bus: 530624 ID: S1 Name: ST JOHN3 | 4 | ALL | 0.4
GEN-2020-056 | 530624 | Bus: 530624 ID: S2 Name: ST JOHN3 | 4 | ALL | 0.5
GEN-2020-056 | 530624 | Bus: 530624 ID: S3 Name: ST JOHN3 | 4 | ALL | 0.5
GEN-2020-056 | 530624 | Bus: 530624 ID: S4 Name: ST JOHN3 | 4 | ALL | 0.7
GEN-2020-056 | 530624 | Bus: 530624 ID: S5 Name: ST JOHN3 | 4 | ALL | 0.7
GEN-2020-056 | 530624 | Bus: 530624 ID: J4 Name: ST JOHN3 | 4 | ALL | 0.7
GEN-2020-056 | 530624 | Bus: 530624 ID: J5 Name: ST JOHN3 | 4 | ALL | 1.2
GEN-2020-056 | 539774 | Bus: 530624 ID: J6 Name: ST JOHN3 | 4 | ALL | 0.766

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 28SP Fault Current 3-Phase (kA) | Request In Service 28SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2020-056 | 04 - Northwest Kansas | 531451 | MINGO 7 | 345 | 6.65 | 6.92 | 0.27
GEN-2020-056 | 04 - Northwest Kansas | 80998 | COLLECTORHV | 115 | 3.3807 | 3.4848 | 0.10411
GEN-2020-056 | 04 - Northwest Kansas | 530553 | S HAYS 3 | 115 | 9.0914 | 9.0973 | 0.0058965
GEN-2020-056 | 04 - Northwest Kansas | 530563 | HEIZER 2 | 69 | 10.41 | 10.4343 | 0.024272
GEN-2020-056 | 04 - Northwest Kansas | 530568 | GB NTH 2 | 69 | 7.5605 | 7.5765 | 0.015964
GEN-2020-056 | 04 - Northwest Kansas | 530582 | S HAYS6 | 230 | 9.6192 | 9.6268 | 0.0076494
GEN-2020-056 | 04 - Northwest Kansas | 530584 | POSTROCK6 | 230 | 12.6963 | 12.7036 | 0.0073662
GEN-2020-056 | 04 - Northwest Kansas | 530586 | ALBERT 2 | 69 | 3.7273 | 3.7342 | 0.0068254
GEN-2020-056 | 04 - Northwest Kansas | 530587 | WSPRTTP2 | 69 | 6.4938 | 6.5071 | 0.013302
GEN-2020-056 | 04 - Northwest Kansas | 530601 | HEIZER 3 | 115 | 12.2338 | 12.272 | 0.038163
GEN-2020-056 | 04 - Northwest Kansas | 530602 | LAXTAP 3 | 115 | 4.0807 | 4.0878 | 0.0070605
GEN-2020-056 | 04 - Northwest Kansas | 530603 | LACROS 3 | 115 | 3.5371 | 3.5431 | 0.0059875
GEN-2020-056 | 04 - Northwest Kansas | 530608 | NEKOMA 3 | 115 | 3.9528 | 3.9592 | 0.0063337
GEN-2020-056 | 04 - Northwest Kansas | 530609 | HZRNGPL3 | 115 | 7.8011 | 7.8214 | 0.020272
GEN-2020-056 | 04 - Northwest Kansas | 530610 | SHAYS_230 | 230 | 4.1438 | 4.1462 | 0.002376
GEN-2020-056 | 04 - Northwest Kansas | 530679 | SEWRDMW3 | 115 | 4.9235 | 4.9311 | 0.007585
GEN-2020-056 | 04 - Northwest Kansas | 530680 | HEIZER 6 | 230 | 8.3492 | 8.366 | 0.016747
GEN-2020-056 | 04 - Northwest Kansas | 530681 | BUSHTON3 | 115 | 4.9756 | 4.9976 | 0.021954
GEN-2020-056 | 04 - Northwest Kansas | 530686 | RICE 6 | 230 | 4.7334 | 4.7429 | 0.0095391
GEN-2020-056 | 04 - Northwest Kansas | 531373 | RHOADES3 | 115 | 3.1757 | 3.181 | 0.0052427
GEN-2020-056 | 04 - Northwest Kansas | 531469 | SPERVIL7 | 345 | 13.0586 | 13.0628 | 0.004168
GEN-2020-056 | 04 - Northwest Kansas | 532871 | CIRCLE 6 | 230 | 9.6819 | 9.6913 | 0.0093994
GEN-2020-056 | 04 - Northwest Kansas | 532872 | EMCPHER6 | 230 | 9.0632 | 9.0689 | 0.0057236
GEN-2020-056 | 04 - Northwest Kansas | 533413 | CIRCLE 3 | 115 | 22.8203 | 22.8326 | 0.012332
GEN-2020-056 | 04 - Northwest Kansas | 539117 | SPRVILL-EHVB | 230 | 11.9003 | 11.905 | 0.0047793
GEN-2020-056 | 04 - Northwest Kansas | 539642 | ELLSWTP3 | 115 | 3.8734 | 3.9676 | 0.094238
GEN-2020-056 | 04 - Northwest Kansas | 539643 | ROLLHLS3 | 115 | 3.5382 | 3.6104 | 0.072234
GEN-2020-056 | 04 - Northwest Kansas | 539644 | COVERT 3 | 115 | 2.5515 | 2.5929 | 0.041396
GEN-2020-056 | 04 - Northwest Kansas | 539647 | IONIA 3 | 115 | 2.8692 | 2.8795 | 0.010227
GEN-2020-056 | 04 - Northwest Kansas | 539650 | BELOIT 3 | 115 | 3.1082 | 3.1156 | 0.007345
GEN-2020-056 | 04 - Northwest Kansas | 539660 | EHALLTP3 | 115 | 3.198 | 3.2341 | 0.03604
GEN-2020-056 | 04 - Northwest Kansas | 539661 | 24-FREY3 | 115 | 5.5142 | 5.5274 | 0.013247
GEN-2020-056 | 04 - Northwest Kansas | 539662 | ELLSWTH3 | 115 | 3.4439 | 3.472 | 0.028129
GEN-2020-056 | 04 - Northwest Kansas | 539663 | GLENELD3 | 115 | 2.7323 | 2.7409 | 0.0086138
GEN-2020-056 | 04 - Northwest Kansas | 539666 | GBENDTP3 | 115 | 7.5056 | 7.5233 | 0.017648
GEN-2020-056 | 04 - Northwest Kansas | 539669 | JEWELL 3 | 115 | 3.043 | 3.051 | 0.0080344
GEN-2020-056 | 04 - Northwest Kansas | 539678 | GRTBEND3 | 115 | 12.3855 | 12.4256 | 0.040121
GEN-2020-056 | 04 - Northwest Kansas | 539679 | GRTBEND6 | 230 | 8.399 | 8.4159 | 0.016831
GEN-2020-056 | 04 - Northwest Kansas | 539681 | N-GBEND3 | 115 | 8.1187 | 8.1408 | 0.022091
GEN-2020-056 | 04 - Northwest Kansas | 539684 | OTISSUB3 | 115 | 2.9217 | 2.9278 | 0.0061121
GEN-2020-056 | 04 - Northwest Kansas | 539685 | PHLBURG3 | 115 | 3.445 | 3.4539 | 0.0089314
GEN-2020-056 | 04 - Northwest Kansas | 539686 | PLAINVL3 | 115 | 3.687 | 3.6919 | 0.004863
GEN-2020-056 | 04 - Northwest Kansas | 539689 | 2ND-KS 3 | 115 | 4.9575 | 4.969 | 0.011572
GEN-2020-056 | 04 - Northwest Kansas | 539692 | SEWARD 3 | 115 | 5.5445 | 5.5532 | 0.0086616
GEN-2020-056 | 04 - Northwest Kansas | 539693 | SMITH-C3 | 115 | 3.6875 | 3.7076 | 0.020066
GEN-2020-056 | 04 - Northwest Kansas | 539694 | SPEARVL3 | 115 | 10.3099 | 10.313 | 0.0031621
GEN-2020-056 | 04 - Northwest Kansas | 539695 | SPEARVL6 | 230 | 12.2114 | 12.2163 | 0.0049434
GEN-2020-056 | 04 - Northwest Kansas | 539696 | ST-JOHN3 | 115 | 5.2294 | 5.2337 | 0.004314
GEN-2020-056 | 04 - Northwest Kansas | 539698 | WALDO 3 | 115 | 2.676 | 2.7289 | 0.052931
GEN-2020-056 | 04 - Northwest Kansas | 539701 | RUSSELL3 | 115 | 3.3914 | 3.4955 | 0.10411
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X