## Executive Summary
Executive Summary: Group 7 Limited Operation & Interim Availability Interconnection System Impact Study
Interconnection Customer (GEN-2020-074 & GEN-2020-085) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by or within a three (3) year extension of the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades. This amount is a preliminary calculation which includes all pending higher queued Interconnection Requests and previously assigned upgrades that requires further study to substantiate. Interconnection Customers are notified of these preliminary Limited Operation amounts with the posting of the DISIS report.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Sensitivity Dispatch Tab; added to identify diapatch variations from DISIS manual
- Stability Analysis Tab; added to include Stability analysis events and results
- Short Circuit Analysis Tab; added to include Short Circuit analysis results for year 10 summer peak case only
Models Used in Study
Power Flow Analysis: 2019 ITP Series
Light: 2024 (24L)
Summer: 2020 (20SP), 2024 (24SP), 2029 (29SP)
Spring: 2020 (20G)
Winter: 2019 (19WP), 2024 (24WP)
Stability analysis: 2018 Series MDWG Dynamics
Light: 2021 (21L)
Summer: 2021 (21SP), 2028 (28SP)
Winter: 2019 (19WP)
Short Circuit Analysis: 2018 Series MDWG Dynamics
Summer: 2028 (28SP)
Author: SPP Generator Interconnection Department
Published: 11/18/2021

## Revision History
Revision History
Date | Author | Change Description
2021-10-21 | S&C | For SPP review
2021-10-28 | S&C | Final revision
2021-11-08 | S&C | Final revision - addressed contingency validation issue
2021-11-18 | SPP | SPP Review complete

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Service | Area | POI | Status | Reactive Compensation Requirements
GEN-2020-074 | 07 - Southwestern Oklahoma | NA | NA | Battery | 200 | 0 | ER/NR | AEPW/OKGE | Line Tap ~ 13 miles from Sunnyside 345kV substation on Lawton - Sunnyside 345kV | IASIS Stage | -0.7
GEN-2020-085 | 07 - Southwestern Oklahoma | NA | NA | Solar | 500 | 0 | ER/NR | AEPW/OKGE | Line Tap ~ 13 miles from Sunnyside 345kV substation on Lawton - Sunnyside 345kV | IASIS Stage | 1.95
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 2.5 | 0 | ER | SPS | Wolfforth 115kV | DISIS STAGE
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 4.2 | 0 | ER/NR | SPS | SPS Erskine 115kV | DISIS STAGE
GEN-2016-005 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | SUNC | Clark-Thistle 345kV | DISIS STAGE
GEN-2016-034 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 90 | 0 | ER | WAPA | Laramie River Station (GEN-2016-023 Tap)-Sidney 345kV | DISIS STAGE
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | 0 | ER | SPS | Swisher 115kV | Exclude
GEN-2016-049 | 03 - Spearville | 18 | DIS-17-1 | Wind | 310.2 | 55.8 | ER | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 300 | 0 | ER | OKGE | Renfrow 345kV | DISIS STAGE
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 54 | 0 | ER/NR | SPS | Lakeview-Brownfield 69kV line | DISIS STAGE
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 108 | 0 | ER/NR | SPS | Bailey County 115kV | DISIS STAGE
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | SPS | Yoakum-Seagraves 115kV circuit | DISIS STAGE
GEN-2016-093 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 70 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 250.7 | 0 | ER/NR | WAPA | Fort Thompson-Leland Olds 345kV | Exclude
GEN-2016-107 | 01 - Woodward | 18 | DIS-17-1 | Wind | 141.75 | 0 | ER/NR | WFEC | Okeene-Cederdale 138kV Line | DISIS STAGE
GEN-2016-109 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | NPPD | Fairbury 115kV | DISIS STAGE
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER/NR | AEPW | Shidler 138kV | DISIS STAGE
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | 0 | ER/NR | NPPD | Turtle Creek 345kV | Exclude
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 64 | 0 | ER | SPS | Hobbs-Yoakum 230kV | DISIS STAGE
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | 0 | ER | SPS | Newhart 115kV | Exclude
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 42 | 0 | ER/NR | WERE | Creswell 69kV Sub | DISIS STAGE
GEN-2017-001 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 250 | 0 | ER/NR | NPPD | Sweetwater 345kV | DISIS STAGE
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SUNC | Elm Creek - Summit 345kV | Exclude
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 195 | 0 | ER | WERE | Marmaton - Litchfield 161kV | Exclude
GEN-2017-006 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 73.6 | 0 | ER | NPPD | Moore (GEN-2015-088 Tap)-Pauline 345kV | DISIS STAGE
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | 0 | ER | SPS | Pleasant Hill 230kV sub | Exclude
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | 23 | ER | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | Exclude
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302.5 | 0 | ER | WERE | Neosho - Caney River 345kV | Exclude
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | WAPA | Rhame 230kV Sub | Exclude
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 0 | ER/NR | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | Exclude
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SPS | Newhart-Potter County 230kV | DISIS STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Mingo 345kV | Exclude
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Underwood - Philip Tap 230kV | Exclude
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 190 | 21.5 | ER/NR | SUNC | Thistle 345kV sub | Exclude
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 0 | ER/NR | WERE | Altoona- NE Parson 138kV | Exclude
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 0 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | Exclude
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | WFEC | Frogville 138kV sub | Exclude
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | 8 | ER/NR | SPS | Tolk 230kV | Exclude
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 0 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | Exclude
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | OKGE | El Reno SW 138kV switch station | Exclude
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | 0 | ER | NPPD | Wildhorse - Covalt 115kV | Exclude
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SPS | Finney - Lamar 345kV | Exclude
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | WFEC | Snyder 138kV | FACILITY STUDY STAGE
GEN-2017-037 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 20 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | SPS | Needmore 230kV sub | Exclude
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | SPS | Cole 115kV | DISIS STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Neset 230kV | Exclude
GEN-2017-049 | 03 - Spearville | 18 | DIS-17-1 | Solar | 50 | 0 | ER | MIDW | Tap Pawnee Valley - Hanston 69kV | DISIS STAGE
GEN-2017-050 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 25 | 0.6 | ER | WERE | Tap Neosho â€“ Crawford 69kV | DISIS STAGE
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | 2.6 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | Exclude
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | 0 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | Exclude
GEN-2017-053 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 50 | 8.9 | ER | WFEC | Tap Hollister SW - PSO Walters 69kV | Exclude
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | 0 | ER/NR | LES | Wagener 115kV Sub | Exclude
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Hosston 69kV | Exclude
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | 27 | ER | SPS | Hereford Northeast 115kV | DISIS STAGE
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | 0 | ER/NR | SPS | TUCO 230kV | Exclude
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 29.9 | ER | EMDE | LaRussell Energy Center 161kV | Exclude
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 0 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | Exclude
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 0 | ER/NR | WAPA | Underwood - Wayside 230kV | Exclude
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-066 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 150.75 | 0 | ER/NR | WFEC | Oney 138kV Sub | DISIS STAGE
GEN-2017-067 | 01 - Woodward | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | ER/NR | WERE | Wichita 345kV | Exclude
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 3.6 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude (-3.6)
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | GRDA | Dry Gulch 161kV sub | Exclude
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Pryor Junction 138kV sub | Exclude
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 0 | ER/NR | OKGE | Hugo-Sunnyside 345kV | Exclude
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | AEPW | Chamber Springs 161kV sub | Exclude
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | AEPW | Explorer Claremore Tap EXCLART4 | Exclude
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | Exclude
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 49.88 | 0 | ER | SPS | Hart Industrial 115kV sub | DISIS STAGE
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | 0 | ER | SPS | Tolk 230kV | Exclude
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 300 | 0 | ER | SPS | Amarillo South-Swisher 230kV | DISIS STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 28.8 | ER | EMDE | Asbury Plant 161kV | Exclude
GEN-2017-083 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 100 | 0 | ER/NR | SUNC | Mingo 115kV | WITHDRAWN
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 89.25 | 0 | ER | SPS | Newhart-Swisher 230kV | DISIS STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0 | ER/NR | NPPD | Friend 115kV | FACILITY STUDY STAGE
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | WERE | Viola 345kV | Exclude
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | SPS | Clovis Interchange 115kV | Exclude
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 150 | ER | KCPL | Adrian 161kV sub | Exclude
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 26.25 | 0 | ER | SPS | Lamton 115kV | DISIS STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | WAPA | Fort Thompson-Huron 230kV | Exclude
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | WAPA | Underwood 115kV Sub | Exclude
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 0 | ER/NR | SPS | Texas County 115kV | DISIS STAGE
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | 0 | ER/NR | SPS | Hobbs 230kV | Exclude
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
AshburyRetired | 08 - North Oklahoma/South Central Kansas | 17.5 | DIS-17-1-PQ | Retired Coal | 198 |  | ER | EMDE | Asbury Plant 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  | ER | WAPA
ASGI-2016-009 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 3 |  | ER | SPS | Wolfforth 12.47kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | WITHDRAWN
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | WITHDRAWN
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | WITHDRAWN
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-135 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-136 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-140 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-143 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-144 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-002 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.35 |  | ER | SPS | SP-Yuma 115kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 0 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | Exclude
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
ASGI-2015-006 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Solar | 9 |  | ER | SWPA | Tupelo 138kV
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Nelson 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  | ER/NR | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  | ER | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-029 | 01 - Woodward | 14 | DIS-15-1 | Wind | 161 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/ON SCHEDULE
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  | ER | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  | ER | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  | ER | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-030 | 02 - Hitchland | 11 | DIS-13-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  | ER | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 30 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  | ER | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  | ER | SPS | Pleasant Hill 69kV | Commerical Operation
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  | ER | SPS | Herring 115kV | Commerical Operation
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  | ER | SPS | Hendricks 69kV | Commerical Operation
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commerical Operation
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commerical Operation
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  | ER | WERE | Westar 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  | ER | AECI | Remington 138kV | GIA Executed
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  | ER | SPS | Martin 115kV | Commerical Operation
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  | ER | OTP

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Priority | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Capacity or Upgrade Details | Scenario 1: Status or Available MW | Scenario 2: Status or Available MW
GEN-2020-074 | DISIS-2020 | NA | NA | ERIS/NRIS | Line Tap ~ 13 miles from Sunnyside 345kV substation on Lawton - Sunnyside 345kV | Interim Study | 200 | 0 | 0
GEN-2020-085 | DISIS-2020 | NA | NA | ERIS/NRIS | Line Tap ~ 13 miles from Sunnyside 345kV substation on Lawton - Sunnyside 345kV | Interim Study | 500 | 0 | 0
132937 | DISIS-2017-001-P2 | NA | NA | NA | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | Not In-Service | Not In-Service
132903 | DISIS-2017-001-P2 | NA | NA | NA | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | Not In-Service | Not In-Service
143127 | DISIS-2017-001-P2 | NA | NA | NA | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | NA | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | Not In-Service | Not In-Service
132902 | DISIS-2017-001-P2 | NA | NA | NA | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | Not In-Service | Not In-Service
133005 | DISIS-2017-001-P2 | NA | NA | NA | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (Non-Shared NU) (WFEC) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | Not In-Service | Not In-Service
133004 | DISIS-2017-001-P2 | NA | NA | NA | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (TOIF) (WFEC) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | Not In-Service | Not In-Service
132985 | DISIS-2017-001-P2 | NA | NA | NA | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | Not In-Service | Not In-Service
132984 | DISIS-2017-001-P2 | NA | NA | NA | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | Not In-Service | Not In-Service
Note on J1: NRIS capacity is limited by ERIS Results. The highlighted available MW amount in Column I is the maximum LOIS or Interim Capacity.

## Constraints Summary
SCENARIO | Generation Interconnection Number | Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading % | TC Voltage | VMIN | VMAX | Impact Study Mitigation
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 514801 MINCO 7 345 514901 CIMARON7 345 1 | ALL | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 141.48 |  |  |  | Upgrade MINCO 7 - CIMARON7 345kV ckt 1 to minimum 1691MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | ALL | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | 143 | 143 | 149.41 |  |  |  | Upgrade S BROWN4 - RUSSETT4 138kV ckt 1 to minimum 214MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 20SP 29SP 20G | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | 353 | 353 | 145.37 |  |  |  | Upgrade WHEELER 6 - STLN-DEMARC6 230kV ckt 1 to minimum 514MVA RateB rating.
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 97000 POI 345 515136 SUNNYSD7 345 1 | ALL | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 1195 | 1195 | 133.35 |  |  |  | Upgrade POI - SUNNYSD7 345kV ckt 1 to minimum 1594MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 20SP 29SP 24WP 24SP 19WP 20G | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | 191 | 191 | 137.13 |  |  |  | Upgrade TUTCONT4 - CIMARON4 138kV ckt 1 to minimum 262MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 29SP 24WP 24SP 24L | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | 241 | 283 | 136.61 |  |  |  | Upgrade CLVLDSW4 - ANADARK4 138kV ckt 1 to minimum 387MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 20SP 29SP 24WP 24SP 19WP 24L | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | 287 | 287 | 135.32 |  |  |  | Upgrade VALIANT4 - HUGO PP4 138kV ckt 1 to minimum 389MVA RateB rating.
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 20SP 20G 24SP 24WP 19WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 128.53 |  |  |  | Upgrade MINCO 7 - G17-067-TAP 345kV ckt 1 to minimum 1536MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 29SP 24WP 24SP 24L | P42:345:OKGE:SB_CION7384 | 200 | 234 | 132.69 |  |  |  | Upgrade GRACMNT4 - ANADARK4 138kV ckt 1 to minimum 311MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 20SP 29SP | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | 349 | 395 | 131.3 |  |  |  | Upgrade SWEETWT6 - STLN-DEMARC6 230kV ckt 1 to minimum 519MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 97000 POI 345 515136 SUNNYSD7 345 1 | ALL | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 1195 | 1195 | 128.77 |  |  |  | Upgrade POI - SUNNYSD7 345kV ckt 1 to minimum 1539MVA RateB rating.
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 20SP 20G 24SP 24WP 19WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 125.95 |  |  |  | Upgrade GRACMNT7 - G17-067-TAP 345kV ckt 1 to minimum 1506MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | ALL | P42:345:OKGE:SB_JOCO7303 | 133 | 153 | 127.56 |  |  |  | Upgrade SPRNDAL4 - DRPSPRG4 138kV ckt 1 to minimum 196MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 20SP 24WP 24SP 19WP 20G 24L | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | 1195 | 1195 | 127.37 |  |  |  | Upgrade MINCO 7 - CIMARON7 345kV ckt 1 to minimum 1523MVA RateB rating.
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 515135 SUNNYSD4 138 998280 SUNNYSD2 138 1 | 20SP | P42:345:OKGE:SB_SUSD7383 | 478 | 478 | 100.9 |  |  |  | Upgrade SUNNYSD4 - SUNNYSD2 138kV ckt 1 to minimum 483MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 520814 ANADARK4 138 521031 POCASET4 138 1 | 20SP 20G | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 200 | 234 | 124.17 |  |  |  | Upgrade ANADARK4 - POCASET4 138kV ckt 1 to minimum 291MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508069 NNBOSTN4 138 508104 RIFFIN REC4 138 1 | 29SP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | 188 | 188 | 123.5 |  |  |  | Upgrade NNBOSTN4 - RIFFIN REC4 138kV ckt 1 to minimum 233MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 20SP 29SP 24WP 24SP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | 362 | 424 | 122.01 |  |  |  | Upgrade NWT-BNT4 - NWTXARK4 138kV ckt 1 to minimum 518MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | ALL | P42:345:OKGE:SB_JOCO7303 | 133 | 153 | 121.66 |  |  |  | Upgrade DRPSPRG4 - STIRLNG4 138kV ckt 1 to minimum 187MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 20SP 24WP 24SP 19WP 20G | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | 1195 | 1195 | 121.26 |  |  |  | Upgrade GRACMNT7 - G17-067-TAP 345kV ckt 1 to minimum 1450MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508050 ANDRSNC4 138 508104 RIFFIN REC4 138 1 | 29SP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | 187 | 188 | 121.21 |  |  |  | Upgrade ANDRSNC4 - RIFFIN REC4 138kV ckt 1 to minimum 228MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 20SP 24WP 24SP 19WP 20G | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 120.78 |  |  |  | Upgrade MINCO 7 - G17-067-TAP 345kV ckt 1 to minimum 1444MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 20SP 24SP 19WP | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | 209 | 212 | 120.02 |  |  |  | Upgrade TUTTLE4 - LEONARD4 138kV ckt 1 to minimum 255MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 | 29SP | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | 318.7 | 318.7 | 118.27 |  |  |  | Upgrade GRAPEVINE 6 - WHEELER 6 230kV ckt 1 to minimum 377MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 521031 POCASET4 138 521072 TUTLETP4 138 1 | 20SP 20G | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 200 | 234 | 116.14 |  |  |  | Upgrade POCASET4 - TUTLETP4 138kV ckt 1 to minimum 272MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 20SP | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | 209 | 212 | 115.25 |  |  |  | Upgrade TUTCONT4 - TUTTLE4 138kV ckt 1 to minimum 245MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 20SP 29SP 24WP 24SP 20G | P42:345:OKGE:SB_JOCO7303 | 133 | 153 | 115.18 |  |  |  | Upgrade RUSSET-4 - STIRLNG4 138kV ckt 1 to minimum 177MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 20SP 29SP 24WP 24SP 19WP | P23:345:AEPW:WELSH CB 11990 NBTB | 970 | 970 | 113 |  |  |  | Upgrade WELSH 7 - WILKES 7 345kV ckt 1 to minimum 1097MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 20SP 29SP 24WP 24SP 19WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | 776 | 776 | 112.1 |  |  |  | Upgrade LONGWD 7 - WILKES 7 345kV ckt 1 to minimum 870MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 20SP 24SP 20G | P42:345:OKGE:SB_JOCO7303 | 194 | 222 | 110.98 |  |  |  | Upgrade SUNNYSD4 - UNIROY 4 138kV ckt 1 to minimum 247MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508050 ANDRSNC4 138 508056 BRYANML4 138 1 | 29SP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | 176 | 188 | 109.76 |  |  |  | Upgrade ANDRSNC4 - BRYANML4 138kV ckt 1 to minimum 207MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 508056 BRYANML4 138 508064 MUNZCTY4 138 1 | 29SP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | 176 | 188 | 109.41 |  |  |  | Upgrade BRYANML4 - MUNZCTY4 138kV ckt 1 to minimum 206MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 20SP 20G | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 200 | 234 | 108.29 |  |  |  | Upgrade BRIDGCR4 - TUTLETP4 138kV ckt 1 to minimum 254MVA RateB rating.
S2 | G07_G077&G085 | 07NR | NRIS | Thermal | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 | 20G | P42:345:OKGE:SB_JOCO7303 | 194 | 222 | 106.02 |  |  |  | Upgrade UNIROY 4 - ARDWEST4 138kV ckt 1 to minimum 236MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 20SP 20G | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 200 | 234 | 104.07 |  |  |  | Upgrade BRIDGCR4 - SUNSHIN4 138kV ckt 1 to minimum 244MVA RateB rating.
S2 | G07_G077&G085 | 07NR | NRIS | Thermal | 515138 CARTER 4 138 515372 ARDWEST4 138 1 | 20G | P42:345:OKGE:SB_JOCO7303 | 194 | 222 | 103.7 |  |  |  | Upgrade CARTER 4 - ARDWEST4 138kV ckt 1 to minimum 231MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 29SP 24WP 24SP | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | 145 | 169 | 102.66 |  |  |  | Upgrade NAPLSTP4 - CORN TP4 138kV ckt 1 to minimum 174MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 20SP 24SP | 81374: 515135 SUNNYSD4 138 515144 LONEGRV4 138 1 515135 SUNNYSD4 138 515164 ROCKYPT4 138 1 | 191 | 191 | 102.57 |  |  |  | Upgrade CARTER 4 - CHIKSAW4 138kV ckt 1 to minimum 196MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 24WP 24SP 19WP | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | 121 | 158 | 102.17 |  |  |  | Upgrade DUNCAN-4 - OMDUNCN4 138kV ckt 1 to minimum 162MVA RateB rating.
S1 | G07_G077&G085 | 07ALL | ERIS | Thermal | 515136 SUNNYSD7 345 998280 SUNNYSD2 138 1 | 20SP | P42:345:OKGE:SB_SUSD7383 | 478 | 478 | 100.67 |  |  |  | Upgrade SUNNYSD7 345/138kV ckt 1 to minimum 482MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 504124 ASHDWN_W 4 138 510890 CRAIGJT4 138 1 | 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 | 287 | 287 | 100.51 |  |  |  | Upgrade ASHDWN_W 4 - CRAIGJT4 138kV ckt 1 to minimum 289MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 24SP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | 106 | 106 | 100.41 |  |  |  | Upgrade DUNCAN-4 - DUNCHERTP4 138kV ckt 1 to minimum 107MVA RateB rating.
S2 | G07_G077&G085 | 00NR | NRIS | Non-Converge | Non-Converge | 20SP 29SP 24L | NA |  |  | NConv
S1 | G07_G077&G085 | 07ALL | ERIS | Non-Converge | Non-Converge | 24L | NA |  |  | NConv
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NWTXARK4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8797 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GODFREYRDTP2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9055 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUGHLET2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9129 | 0.92 | 1.05
S2 | G07_G077&G085 | 07NR | NRIS | Voltage | GEN-2016-111 345.0kV | 20G | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 532771 RENO 7 345 997951 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-2 115 1 |  |  |  | 1.0503 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NASH 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8707 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GARVIN4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8533 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BODLE 4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8689 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COVEREC2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8977 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | AVENUECTY 5 161.0kV | 19WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8973 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KETCHEM7 345.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8963 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RYAN 2 69.0kV | 24WP 19WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 |  |  |  | 0.8967 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WYNWOOD2 69.0kV | 24WP 19WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8766 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ALAMANC2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8282 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLALOCK2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8353 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LEHIGH-4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.9094 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MENA 4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8438 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | BRADYJT2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8913 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MAUD 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8361 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | W-LIFTP2 69.0kV | 24WP 19WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 |  |  |  | 0.9191 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NW_TEXAR 2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9112 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CHICKASAW2 69.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8868 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COALGAT4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.9126 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S_TEXARK 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8984 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DALLAS 2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8907 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | BASELIN2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8953 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REBAR 4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8673 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HUGO---2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8907 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BROKNBW4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8445 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-030 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8769 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RICHMND2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9105 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SDIERKS4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9011 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDWATR2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8362 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IPC T 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8199 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NLINDEN2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8374 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | W CITY 2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8862 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PEARLHL2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8308 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HUGO---4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8802 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BARITERDTP 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9011 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | HARISBG2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.895 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BARITE-RD 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9004 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OSBORN7 345.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8964 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COOKVTP2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9104 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NE-TEXARK2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8892 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WATLANT2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9013 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LSORD 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9077 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EXPLRPL4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8756 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALIANT2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8829 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KU CAMP3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9258 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KRSYJCTN4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8731 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GRANNIS 2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9109 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TURK 7 345.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8969 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IDABEL 4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8459 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TXI4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8629 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FAIRGDS3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9259 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LTLCITY4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8903 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | USMOTOR2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8896 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANDRCKT2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8403 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BRKN BW4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.863 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEX12ST2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9064 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SFOREMAN 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8551 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MANDEVILTP4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8892 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KIERSEY4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.866 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FORMANR2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9184 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KINGHWY2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9125 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIMMS 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8368 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WDEKALB2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8233 | 0.92 | 1.05
S2 | G07_G077&G085 | 07NR | NRIS | Voltage | WSTBANK4 138.0kV | 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8874 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANDRSNC4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8215 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | FTOWSON2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.887 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NEKOOSA2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8654 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MINEOLA2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 1.0514 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIBLEY 7 345.0kV | 24WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8993 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BROWN 4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8768 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DOMINJCT4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8455 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | STRRDTP4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8769 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLEMNT4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8764 | 0.9 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | VALIANT4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9194 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDRVR-2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8973 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SCLMNJC4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8675 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEX-PUP2 69.0kV | 24WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 |  |  |  | 0.9198 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KRSYJCTS4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8745 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WASHST 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9045 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NWT-BNT4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8784 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DUGLASV4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.836 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MOCKBRD3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9297 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | UNGER 4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8699 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | V-WEYCO4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8716 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDLICK2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.912 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | IDABEL-4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9137 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SIB REA1 345.0kV | 24WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8993 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 19THSTJ3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9262 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ROACH 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8317 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IPC TAP2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8811 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 166TH 3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9262 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PATTERS2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8991 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOCHJCT4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8466 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SEAWAY4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8633 | 0.9 | 1.05
S2 | G07_G077&G085 | 07NR | NRIS | Voltage | WSBNKTP4 138.0kV | 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8874 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KEYSTNT4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8576 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WBURGE 5 161.0kV | 19WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8988 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NNBOSTN4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8347 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NORTONV2 69.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9247 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MENA 2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8914 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLOOMBG2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8775 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | B.BOW 4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9156 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | B.BOW 4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.842 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEXOPER2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9127 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BUTRFLD4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8674 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SNASHVL4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8991 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TAYLOR 2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9105 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | V-WEYCO4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9158 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | VELMA 2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8881 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SWLWRNC3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9278 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOLOX 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9015 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | W-RELIF2 69.0kV | 24WP 19WP | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 |  |  |  | 0.9187 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BLUEBRD4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8576 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COALGTP4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.9126 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PLEASHL2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8981 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ASHDOWN2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9001 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | BRADY 2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8828 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEX39ST2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9123 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ATLANTA2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8894 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | WAURIKA2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.9186 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DUGLASV2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8492 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ASHDWNR4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8963 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BENNGTN4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8591 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CRAIGJT4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8452 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | DEQUEEN4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9158 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALYTIM2 69.0kV | 24WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9109 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BUCHANN4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8503 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KI PMPS2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8857 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DURANTP4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.855 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLBERT4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8643 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 87TH 7 345.0kV | 24WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.924 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BANN 2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.913 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BUFORDR2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.896 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BRYANML4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8368 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IPC 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.881 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RIFFIN REC4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.832 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HAWTH 7 345.0kV | 19WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8982 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | 19THST 3 115.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9252 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SFORE_1 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.877 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | RODESSA2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9043 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MUNZCTY4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8416 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | CASSTP4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8385 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IDABEL-4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8456 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HAWORTH4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8446 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GA PAC 2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8751 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | SUGDEN 2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8999 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SDEKALB2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8265 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KI PMPN2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8842 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOCHTWN4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8568 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPRNGHL2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.822 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | OKAY 4 138.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9107 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILL6 230.0kV | 24WP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9459 | 0.95 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | THAKRVL2 69.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8914 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SCOLEMN4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8643 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DURANT 4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8535 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DEQUEEN4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8426 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | WYNWOOD2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8809 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | KIPUMPT2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8845 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BETHEL 4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8893 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MAUDT 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8361 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NEWBOST2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8916 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LYDIA 7 345.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9161 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLBRTP4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8692 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | S BROWN4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8763 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDSPRG4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.852 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LSORDTP2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9081 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DARENCO2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8308 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | CRAIGJT4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9185 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NAPLES 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8954 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUGARHL4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8821 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | B.BOWTP4 138.0kV | 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9157 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | PATTERS4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.892 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BIVINS 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8274 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LOCKSBRG 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8959 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NEKOSAT2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9015 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BANN 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8683 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | LINDEN 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9072 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DOMINAN4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.845 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SAWYER 2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8877 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SETEXAR4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.873 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANTLTAP2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9172 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUGARHL2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9139 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IPC 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8092 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WATLANT4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8433 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | YUBA4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8625 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GEN-2016-088 345.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.8964 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TEXARK 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9075 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BROWNTP4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8775 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | JIMTOWN2 69.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8976 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | TECHILL5 161.0kV | 29SP | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 |  |  |  | 0.9241 | 0.93 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOOKS 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9075 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | IPC-DOM4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8237 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | USMOTAP2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8908 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | LINDSAY2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8971 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOLYCRK4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8443 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | BENNSUB4 138.0kV | 24WP 19WP 24L | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8586 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DENISON4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.877 | 0.9 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | EOLA 2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8883 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NNBOSTN2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8914 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | DARENCT2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.831 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MTRIVER4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8451 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EOLA 2 69.0kV | 24WP 19WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8841 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WICKES 2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9075 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COLBRT-4 138.0kV | 24WP 19WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.8647 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NWTXARK7 345.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8934 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GORDON TAP 4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.843 | 0.92 | 1.05
S1 | G07_G077&G085 | 07ALL | ERIS | Voltage | RYAN 2 69.0kV | 24WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8994 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | MENA 2 69.0kV | 24WP 19WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8915 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SUGHLWT2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9133 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALIANT4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8754 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SETEXAR2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9085 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | NMINEOL2 69.0kV | 24WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 1.051 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | GOLDENSW4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8451 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ALUMAX 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8707 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COOKVIL2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9103 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EYLAU 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.851 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALLANT4 138.0kV | 24WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8909 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WCITYTP2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.883 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPECTRM4 138.0kV | 24WP 19WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8968 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ASHDWN_W 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8964 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ATOKA--4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.9063 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANTLERS2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9164 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDWATR4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8504 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | B.BOWTP4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8423 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | COOKVIL2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9103 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | EYLAU 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.851 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | VALLANT4 138.0kV | 24WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8909 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | WCITYTP2 69.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.883 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | SPECTRM4 138.0kV | 24WP 19WP | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 |  |  |  | 0.8968 | 0.9 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ASHDWN_W 4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8964 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ATOKA--4 138.0kV | 24WP | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 |  |  |  | 0.9063 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | ANTLERS2 69.0kV | 24WP | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.9164 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | REDWATR4 138.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.8504 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | B.BOWTP4 138.0kV | 24WP 19WP 24L | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 |  |  |  | 0.8423 | 0.92 | 1.05
S2 | G07_G077&G085 | 00NR | NRIS | Voltage | HOLOX 2 69.0kV | 24WP 19WP | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 |  |  |  | 0.9015 | 0.92 | 1.05

## All Thermal
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONITORED ELEMENT | RATEA (MVA) | RATEB (MVA) | TDF | TC% LOADING (% MVA) | CONTINGENCY | Footprint | BC LOADING (% MVA) | LOADING Diff (% MVA)
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00027 | 140.96 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.86 | 0.1
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.0001 | 103.78 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 103.73 | 0.05
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.65889 | 118.88 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00024 | 108.89 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 108.87 | 0.02
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66103 | 114.99 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66452 | 123.97 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66103 | 117.67 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.0001 | 103.69 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 103.64 | 0.05
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02573 | 101.71 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66103 | 118.2 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.65685 | 119.12 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.0002 | 142.03 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.65 | 0.38
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49584 | 128.53 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal | 101.52 | 27.01
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00385 | 123.22 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 118.3 | 4.92
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337846 3FOURCHE 115 337847 3LR.E 115 1 | 159 | 159 | 0.00449 | 103.38 | P23:500:EES-EAI:KEO:B4921 | External | 101.6 | 1.78
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00375 | 122.81 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.08 | 4.73
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 103.87 | P12:138:GRDA:CLEVLND-COLLINS | External | 103.52 | 0.35
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 115 | 115 | 0.00022 | 101.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.34 | 0.1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66886 | 108.56 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00072 | 100.33 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 100.31 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 103.49 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 512705 COLLINS4 138 998340 COLAUTO3 138 1 | External | 103.14 | 0.35
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0007 | 105.68 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 105.66 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00037 | 172.92 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 172.84 | 0.08
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 125.43 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 125.23 | 0.2
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00029 | 124.07 | P23:500:EES-EAI:WH_BLF:B7914 | External | 123.75 | 0.32
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00603 | 102.25 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 101.9 | 0.35
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 125.43 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 125.23 | 0.2
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 125.07 | P13:161-69:EES-EAI:HERGET:AT2 | External | 124.87 | 0.2
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0007 | 102.98 | Base Case | External | 102.96 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00073 | 102.1 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 101.87 | 0.23
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | 225 | 225 | 0.00041 | 105 | 67767: 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 303130 4N_CROWLEY 138 335378 4SCOTT_2! 138 1 | External | 104.9 | 0.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49584 | 125.95 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49581 | 125.9 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00271 | 100.38 | P12:230:CLEC:COCODR1:VLPLAT:1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 667048 LETELER4 230 1 | 478 | 478 | 0.0016 | 127.75 | P12:500:MH:M602F | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00375 | 122.81 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.08 | 4.73
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338421 5CONWAY.S 161 338423 5CONWAY IND 161 1 | 223 | 223 | 0.00817 | 102.7 | P23:500:EES-EAI:KEO:B4941 | External | 100.37 | 2.33
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336224 3AMCYAN! 115 1 | 174 | 174 | 0.00035 | 108.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.99 | 0.11
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336236 3PRSTAP 115 336406 3AVE C! 115 1 | 221 | 221 | 0.00024 | 100.06 | 336430 6MKTST! 230 336421 3MKTST_SP! 115 1: 336430 6MKTST! 230 336421 3MKTST_SP! 115 1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00029 | 105.96 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.65 | 0.31
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 125.07 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 124.87 | 0.2
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00897 | 106.52 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 104.71 | 1.81
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49584 | 141.48 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal | 112.97 | 28.51
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66744 | 110.25 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 103.87 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 103.52 | 0.35
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49581 | 128.48 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal | 101.48 | 27
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00029 | 100.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.48 | 0.29
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 100.87 | 608673 ARROWHD7 115 608679 GARY 7 115 1: 608673 ARROWHD7 115 608679 GARY 7 115 1 | External | 100.87 | 0
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00271 | 100.38 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00438 | 103.44 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 102.44 | 1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00603 | 125.62 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 125.33 | 0.29
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00073 | 102.1 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 101.87 | 0.23
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00017 | 104.09 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 103.92 | 0.17
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00072 | 100.33 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 100.31 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 667048 LETELER4 230 1 | 478 | 478 | 0.0016 | 127.75 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1 | External
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49581 | 141.43 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal | 112.93 | 28.5
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335391 4CECELIA! 138 502404 BONIN 4 138 1 | 145 | 145 | 0.00033 | 100.73 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 100.61 | 0.12
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00017 | 103.99 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 103.82 | 0.17
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 657755 PRAIRIE4 230 1 | 400 | 400 | 0.00124 | 126.25 | P12:500:MH:M602F | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00133 | 141.53 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 140.88 | 0.65
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00897 | 115.28 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 113.48 | 1.8
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00326 | 101.42 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 100.91 | 0.51
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337925 5GREENBRIER 161 337926 5QUITMAN! 161 1 | 223 | 223 | 0.0071 | 109.57 | P23:500:EES-EAI:KEO:B4941 | External | 107.67 | 1.9
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67089 | 107.5 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 657755 PRAIRIE4 230 1 | 400 | 400 | 0.00124 | 126.25 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336225 3WAGGMN 115 1 | 174 | 174 | 0.00044 | 125.36 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 125.22 | 0.14
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 2e-05 | 104.97 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.97 | 0
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 125.07 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 124.87 | 0.2
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48055 | 133.51 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal | 106.3 | 27.21
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00438 | 103.44 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 102.44 | 1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00068 | 112.95 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 112.89 | 0.06
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00438 | 103.44 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 102.44 | 1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335390 4BAYOU_WHSE! 138 1 | 112 | 112 | 0.00133 | 123.72 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 123.1 | 0.62
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00068 | 111.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.78 | 0.06
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00072 | 100.54 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 100.52 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336225 3WAGGMN 115 336280 39MILE% 115 1 | 174 | 174 | 0.00044 | 118.65 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.5 | 0.15
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 657755 PRAIRIE4 230 1 | 400 | 400 | 0.00124 | 126.25 | 601012 ROSEAUN2 500 667501 RIEL 2 500 1: 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0007 | 105.92 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 105.9 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67089 | 108.67 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.5001 | 121.26 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00129 | 101.73 | 336250 69MILE% 230 336428 6NAPOL 230 1: 336250 69MILE% 230 336428 6NAPOL 230 1 | External | 101.63 | 0.1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00043 | 108.33 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 108.22 | 0.11
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0007 | 105.68 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 105.66 | 0.02
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 515135 SUNNYSD4 138 998280 SUNNYSD2 138 1 | 478 | 478 | 0.2204 | 100.9 | P42:345:OKGE:SB_SUSD7383 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338421 5CONWAY.S 161 338423 5CONWAY IND 161 1 | 223 | 223 | 0.00865 | 110.42 | P23:500:EES-EAI:KEO:B4921 | External | 107.97 | 2.45
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48055 | 120.96 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00944 | 105.31 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 103.47 | 1.84
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00013 | 127.71 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 127.7 | 0.01
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 337925 5GREENBRIER 161 337926 5QUITMAN! 161 1 | 223 | 223 | 0.00727 | 112.07 | P23:500:EES-EAI:KEO:B4921 | External | 110.11 | 1.96
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00017 | 103.99 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 103.82 | 0.17
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00017 | 104.09 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 103.92 | 0.17
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00104 | 123.87 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 122.3 | 1.57
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 657752 DRAYTON4 230 667048 LETELER4 230 1 | 478 | 478 | 0.0016 | 127.75 | 601012 ROSEAUN2 500 667501 RIEL 2 500 1: 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 125.43 | P13:161-69:EES-EAI:HERGET:AT1 | External | 125.23 | 0.2
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0012 | 107.55 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 107 | 0.55
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336154 6WATFRD% 230 336250 69MILE% 230 1 | 1038 | 1038 | 0.00239 | 121.71 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 121.56 | 0.15
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00095 | 117.27 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 116.95 | 0.32
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00944 | 113.99 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 112.18 | 1.81
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67089 | 110.26 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00129 | 101.73 | P12:HV:EES::69MILE%:6NAPOL:1 | External | 101.63 | 0.1
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 233 | 233 | 0.00077 | 106.33 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 106.15 | 0.18
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.6766 | 115.37 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 336224 3AMCYAN! 115 336280 39MILE% 115 1 | 159 | 159 | 0.00035 | 101.63 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.5 | 0.13
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00068 | 107.95 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.9 | 0.05
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 2e-05 | 100.78 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.78 | 0
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00095 | 108.73 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 108.42 | 0.31
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 515136 SUNNYSD7 345 998280 SUNNYSD2 138 1 | 478 | 478 | 0.2204 | 100.67 | P42:345:OKGE:SB_SUSD7383 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 118.56 | P13:161-69:EES-EAI:HERGET:AT2 | External | 118.36 | 0.2
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.4809 | 120.94 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631114 NEWPORT5 161 630052 NEWPORT8 69.0 1 | 60 | 60 | 0.00043 | 119.87 | P12:161:MPW-MEC-ITC-CIPCO::9 SUB 5:HWY61 5:WEST 5:NEWPORT5:1 | External | 119.96 | -0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | 112 | 133.9 | 2e-05 | 107 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.02 | -0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | 209 | 209 | 0.00044 | 100.12 | 67767: 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 303130 4N_CROWLEY 138 335378 4SCOTT_2! 138 1 | External | 100.05 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00851 | 112.99 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 112.03 | 0.96
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00062 | 104.13 | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1: 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | External | 103.95 | 0.18
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00071 | 113.76 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 113.67 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631108 DENMARK5 161 631109 BRLGTN 5 161 1 | 210 | 210 | 0.00121 | 170.12 | 631108 DENMARK5 161 631109 BRLGTN 5 161 2: 631108 DENMARK5 161 631109 BRLGTN 5 161 2 | External | 170.89 | -0.77
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49975 | 120.78 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00039 | 172.74 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 172.68 | 0.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00071 | 113.98 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 113.89 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 191 | 191 | 0.04657 | 102.57 | 81374: 515135 SUNNYSD4 138 515144 LONEGRV4 138 1 515135 SUNNYSD4 138 515164 ROCKYPT4 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 214.77 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 215.26 | -0.49
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49975 | 121.24 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631203 SALE5 161 629194 SALE8 69.0 1 | 100 | 100 | 0.00038 | 101.12 | Base Case | External | 101.11 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.0011 | 125.11 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00851 | 120.26 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 119.29 | 0.97
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630249 WINDSOR8 69.0 613420 WINDSOR5 161 1 | 75 | 94 | 0.00019 | 105.46 | P13:069-161:ITCM-DPC:POSTVILLE 5 T1:IA-NE | External | 105.34 | 0.12
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | 112 | 133.9 | 0.00026 | 114.96 | 681543 ALMA 5 161 680173 ALMA 8 69 2: 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | External | 114.96 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636601 SB 39 5 161 636602 SB 39 8 69.0 1 | 125 | 152 | 7e-05 | 109.97 | Base Case | External | 109.96 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00035 | 107.28 | 615354 GRE-DICKNSN7 115 615590 GRE-CROWRIV7 115 1: 615354 GRE-DICKNSN7 115 615590 GRE-CROWRIV7 115 1 | External | 107.19 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03528 | 124.17 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 113.6 | 10.57
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00077 | 105.93 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 105.78 | 0.15
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615396 GRE-PRKWDB17 115 997566 PAR115-69-1 69.0 1 | 140 | 140 | 0.00029 | 169.83 | P13:12-115-69:GRE:AUTO-SINGLE:GRE-PRKWD2T:GRE-PRKWDB27:GRE-PRKWDB28:2 | External | 169.8 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00025 | 103.11 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1 | External | 103.05 | 0.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631099 WYOMING5 161 630022 WYOMING8 69.0 1 | 63 | 63 | 0.00031 | 114.87 | Base Case | External | 114.86 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 5e-05 | 173.21 | 63251: 348949 MERCER5 161 636636 OAKGROV5 161 1 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | External | 173.21 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00295 | 102.52 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.08259 | 100.72 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631109 BRLGTN 5 161 630037 BRLGTN18 69.0 1 | 112 | 112 | 0.00026 | 128.14 | P13:69-161:ALTW:AUTO-SINGLE:BRLGTN28:BRLGTN5:1 | External | 128.28 | -0.14
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.00025 | 131.47 | Base Case | External | 131.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00069 | 106.98 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 106.94 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04286 | 117.39 | P42:345:OKGE:SB_CION7384 | Internal | 102.99 | 14.4
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636671 SB18#2 8 69.0 3 | 125 | 152 | 0.00038 | 104.96 | 636670 SB 18 5 161 636669 SB18#1 8 69 1: 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | External | 104.9 | 0.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336225 3WAGGMN 115 336280 39MILE% 115 1 | 174 | 174 | 0.00046 | 123.28 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 123.16 | 0.12
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00044 | 114.67 | 631044 HAYWARD L2 5 161 631174 GLENWRTH5 161 1: 631044 HAYWARD L2 5 161 631174 GLENWRTH5 161 1 | External | 114.56 | 0.11
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 521031 POCASET4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03528 | 116.14 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 106.82 | 9.32
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.00012 | 184.29 | P23:345-161:XEL:ADAMS_I:681_S | External | 184.22 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615396 GRE-PRKWDB17 115 997566 PAR115-69-1 69.0 1 | 140 | 140 | 0.00016 | 168.91 | 615329 GRE-BNKRLK 8 69 3WXFMR 230-69 1: 615329 GRE-BNKRLK 8 69.0 997570 230-69.0 69.0 1 615328 GRE-BUNKER 4 230 997570 230-69.0 69.0 1 615331 GRE-BNKRLK T 12.5 997570 230-69.0 69.0 1 615329 GRE-BNKRLK 8 69.0 997574 230-69.0 69.0 1 615328 GRE-BUNKER 4 230 997574 230-69.0 69.0 1 615331 GRE-BNKRLK T 12.5 997574 230-69.0 69.0 1 | External | 168.89 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00046 | 109.81 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 109.74 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615433 GRE-BURNVIL7 115 997560 115/69 69.0 2 | 82.2 | 82.2 | 9e-05 | 118.56 | P13:115-69-13:XEL:AUTO-SINGLE:GRE-BURNVIL7:GRE-BURNVIL8:GRE-BURNVL1T:1 | External | 118.52 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335390 4BAYOU_WHSE! 138 500440 IVANHOE4 138 1 | 135 | 145 | 0.00142 | 100.63 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 100.32 | 0.31
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00014 | 126.4 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.39 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.00015 | 179.23 | Base Case | External | 179.13 | 0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.0011 | 105.28 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00142 | 108.48 | 80248: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500580 MORBHAN4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 107.99 | 0.49
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 118.9 | P13:161-69:EES-EAI:HERGET:AT1 | External | 118.7 | 0.2
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 0.00011 | 142.14 | Base Case | External | 142.15 | -0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66964 | 106.4 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00119 | 119.36 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 118.06 | 1.3
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336154 6WATFRD% 230 336250 69MILE% 230 1 | 1038 | 1038 | 0.00255 | 126.57 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.45 | 0.12
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 2 | 150 | 150 | 0.00028 | 109.91 | 631059 8TH ST.5 161 630290 DBQ 8TH8 69 1: 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 1 | External | 109.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615400 GRE-PRKWDB27 115 997565 PAR115-69-2 69.0 2 | 140 | 140 | 0.00029 | 168.47 | P13:115-69-12:GRE:AUTO-SINGLE:GRE-PRKWDB17:GRE-PRKWDB18:GRE-PRKWD1T:1 | External | 168.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 214.77 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 215.26 | -0.49
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | 225 | 225 | 0.00044 | 100.11 | 67767: 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 303130 4N_CROWLEY 138 335378 4SCOTT_2! 138 1 | External | 100.04 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 0.00011 | 144.33 | 615383 GRE-ELK RIV4 230 615021 GRE-ER 14G 16 1: 615383 GRE-ELK RIV4 230 615021 GRE-ER 14G 16.0 1 | External | 144.33 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681524 HLSBORO5 161 680095 HILLSBOR 69.0 1 | 112 | 136.6 | 7e-05 | 124.66 | Base Case | External | 124.66 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605662 LUFKIN 69.0 681545 LUFKIN 161 6 | 112 | 128.8 | 0.00015 | 107.62 | 681539 ELK MND5 161 681545 LUFKIN 161 1: 681539 ELK MND5 161 681545 LUFKIN 161 1 | External | 107.65 | -0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.07951 | 103.17 | P12:345:OKGE:BKRBKR21 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336224 3AMCYAN! 115 336280 39MILE% 115 1 | 159 | 159 | 0.00037 | 105.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.57 | 0.11
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605028 T CORNE8 69.0 603152 T-CRNRS7 115 2 | 112 | 128.8 | 0.00051 | 102.23 | Base Case | External | 102.2 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06275 | 119.68 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635870 BEACON 5 161 635871 BEACON 8 69.0 2 | 167 | 266 | 0.00085 | 164.49 | Base Case | External | 164.48 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 1e-05 | 100.49 | P13:161-69:ITCM:LIME CK5 T2:IA-NW- | External | 100.5 | -0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 101.36 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 512705 COLLINS4 138 998340 COLAUTO3 138 1 | External | 100.82 | 0.54
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03528 | 108.29 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 115 | 115 | 0.00023 | 105.55 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.47 | 0.08
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03778 | 130.03 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 116.73 | 13.3
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48055 | 118.17 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03778 | 129.93 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 116.6 | 13.33
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | 112 | 133.9 | 0.00026 | 113.8 | 681543 ALMA 5 161 680173 ALMA 8 69 1: 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | External | 113.8 | 0
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4809 | 133.47 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal | 106.25 | 27.22
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.00015 | 135.05 | Base Case | External | 135.02 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00374 | 104.83 | P12:230:CLEC::RODEMR 6:SHERWD 6:1 | External | 104.55 | 0.28
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.0003 | 106.05 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.78 | 0.27
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 2e-05 | 100.6 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.59 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.03778 | 120.02 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 108.95 | 11.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636601 SB 39 5 161 636602 SB 39 8 69.0 2 | 125 | 152 | 8e-05 | 114.92 | Base Case | External | 114.91 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00069 | 123.71 | Base Case | External | 123.61 | 0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 0.00015 | 117.57 | 603236 ORONO 7 115 615590 GRE-CROWRIV7 115 1: 603236 ORONO 7 115 615590 GRE-CROWRIV7 115 1 | External | 117.55 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00879 | 115.09 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 113.73 | 1.36
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.04005 | 114.46 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 103.41 | 11.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06275 | 106.17 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00025 | 107.22 | 601019 COON CK3 345 615353 GRE-DICKNSN3 345 1: 601019 COON CK3 345 615353 GRE-DICKNSN3 345 1 | External | 107.15 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.04286 | 105.53 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 521031 POCASET4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03109 | 103.89 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00879 | 105.95 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 104.56 | 1.39
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06115 | 103.28 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.00012 | 183.01 | P12:161:DPC:RCE-HAR5 | External | 182.94 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03109 | 108.68 | P42:345:OKGE:SB_MICO7301 | Internal | 100.06 | 8.62
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06275 | 111.94 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631108 DENMARK5 161 631109 BRLGTN 5 161 2 | 197 | 197 | 0.00121 | 181.35 | 631108 DENMARK5 161 631109 BRLGTN 5 161 1: 631108 DENMARK5 161 631109 BRLGTN 5 161 1 | External | 182.17 | -0.82
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02543 | 106.19 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06695 | 106.44 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00067 | 108.62 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00879 | 105.95 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 104.56 | 1.39
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336225 3WAGGMN 115 1 | 174 | 174 | 0.00046 | 129.86 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 129.75 | 0.11
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635870 BEACON 5 161 635871 BEACON 8 69.0 1 | 167 | 208.7 | 0.0008 | 153.17 | Base Case | External | 153.16 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 | 112 | 128.8 | 0.0005 | 100.01 | Base Case | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00915 | 106.75 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 105.75 | 1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.68552 | 108.01 | 926261: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03006 | 118.57 | 83956: 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 113.3 | 5.27
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | 112 | 133.9 | 0.00015 | 125.2 | Base Case | External | 125.2 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 118.9 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 118.7 | 0.2
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06275 | 113.18 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03006 | 130.35 | 83954: 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 524043 NICHOLS 3 115 524021 NICHOLS_1 1 13.8 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 125.61 | 4.74
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00915 | 113.44 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 112.52 | 0.92
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 0.00015 | 117.57 | P12:115:XEL:AUTO-SINGLE:ORONO7:GRE-CROWRIV7:1 | External | 117.55 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.03778 | 115.19 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 104.11 | 11.08
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.03528 | 104.07 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 0.0004 | 210.93 | Base Case | External | 210.9 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00069 | 123.38 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 123.28 | 0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00015 | 120.5 | Base Case | External | 120.58 | -0.08
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615400 GRE-PRKWDB27 115 997565 PAR115-69-2 69.0 2 | 140 | 140 | 0.00018 | 163.96 | Base Case | External | 163.95 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00915 | 120.74 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 119.81 | 0.93
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | 225 | 225 | 0.00044 | 105.34 | 67767: 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 303130 4N_CROWLEY 138 335378 4SCOTT_2! 138 1 | External | 105.27 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.04286 | 103.37 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 602003 BLUEETA5 161 631045 HUNTLEY5 161 1 | 197 | 200 | 0.00137 | 105.46 | P23:345:XEL:8S23 WLM | External | 105.1 | 0.36
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 118.56 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 118.36 | 0.2
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 0.00021 | 115.03 | Base Case | External | 115.01 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00101 | 122.72 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 122.48 | 0.24
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 3e-05 | 128.33 | Base Case | External | 128.33 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635004 SUB701 8 69.0 1 | 89.6 | 118.3 | 0.00418 | 124.27 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 121.64 | 2.63
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 0.00011 | 144.33 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1 | External | 144.33 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67755 | 112.64 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 0.00017 | 117.56 | 71576: 601022 PARKERS3 345 615353 GRE-DICKNSN3 345 1 601005 ELM CRK3 345 601022 PARKERS3 345 1 | External | 117.54 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04386 | 118.14 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00067 | 108.62 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00101 | 114.06 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 113.83 | 0.23
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 6e-05 | 148.96 | P23:345:XEL:8M40 CNC | External | 148.98 | -0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615590 GRE-CROWRIV7 115 997534 115-69 69.0 1 | 112 | 112 | 0.00011 | 117.13 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 117.12 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681541 WASHCO 5 161 680322 WASHCO 69.0 2 | 67.2 | 82 | 0.0001 | 111.28 | Base Case | External | 111.26 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631114 NEWPORT5 161 1 | 175 | 175 | 0.00132 | 105.45 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 105.53 | -0.08
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00398 | 122.39 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 117.22 | 5.17
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06115 | 103.28 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04631 | 120.18 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal | 103.71 | 16.47
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | 112 | 133.9 | 0.00026 | 113.8 | P13:69-161:DPC:AUTO-SINGLE:ALMA8:ALMA5:1 | External | 113.8 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.04005 | 109.2 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00374 | 104.83 | P12:230:CLEC:RODEMR1:SHRWD7:1 | External | 104.55 | 0.28
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 191 | 191 | 0.046 | 101.56 | P12:138:OKGE:BKRBKR257 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00021 | 103.46 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 103.41 | 0.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67176 | 105.55 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631101 DUNDEE 5 161 630024 DUNDEE 8 69.0 1 | 70 | 70 | 0.00012 | 184.29 | P23:345-161:XEL:ADAMS_I:680_S | External | 184.22 | 0.07
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605411 REDCDR 8 69.0 602016 REDCDR 5 161 6 | 70 | 80.5 | 6e-05 | 104.63 | Base Case | External | 104.6 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 362 | 424 | 0.04512 | 112.81 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 106 | 6.81
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | 112 | 133.9 | 2e-05 | 106.88 | P22:345:XEL:ADAMS 3 N1:MN | External | 106.9 | -0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 101.73 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 101.2 | 0.53
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00289 | 105.19 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 104.84 | 0.35
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681528 HARMONY5 161 680026 HARMNY 69.0 1 | 112 | 136.6 | 0.00027 | 125.77 | Base Case | External | 125.74 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03109 | 110.24 | P42:345:OKGE:SB_CION7384 | Internal | 101.65 | 8.59
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335391 4CECELIA! 138 502404 BONIN 4 138 1 | 145 | 145 | 0.00035 | 102.92 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 102.83 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00289 | 105.19 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 104.84 | 0.35
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631114 NEWPORT5 161 630052 NEWPORT8 69.0 1 | 60 | 60 | 0.00043 | 119.58 | 631114 NEWPORT5 161 633241 HWY61 5 161 1: 631114 NEWPORT5 161 633241 HWY61 5 161 1 | External | 119.68 | -0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00374 | 104.83 | 500770 RODEMR 6 230 500790 SHERWD 6 230 1: 500770 RODEMR 6 230 500790 SHERWD 6 230 1 | External | 104.55 | 0.28
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06496 | 102.91 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615400 GRE-PRKWDB27 115 997565 PAR115-69-2 69.0 2 | 140 | 140 | 0.00029 | 169.28 | P12:115:GRE:PKW-CRL | External | 169.24 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 2 | 150 | 150 | 0.00028 | 109.91 | P13:69-161:ALTW:AUTO-SINGLE:DBQ8TH8:8THST.5:1 | External | 109.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00142 | 151.96 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 151.47 | 0.49
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00851 | 130.49 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 129.54 | 0.95
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.04286 | 110.49 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605411 REDCDR 8 69.0 602016 REDCDR 5 161 5 | 70 | 80.5 | 6e-05 | 105.11 | Base Case | External | 105.09 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.0003 | 123.24 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 123.2 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 4e-05 | 107.83 | Base Case | External | 107.83 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00044 | 114.67 | P12:161:ALTW:AUTO-SINGLE:HAYWARDL25:GLENWRTH5:1 | External | 114.56 | 0.11
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00073 | 108.38 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 108.33 | 0.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.03006 | 117.79 | 83954: 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 524043 NICHOLS 3 115 524021 NICHOLS_1 1 13.8 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 113.41 | 4.38
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335390 4BAYOU_WHSE! 138 1 | 112 | 112 | 0.00142 | 133.59 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 133.1 | 0.49
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00073 | 107.28 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.24 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00069 | 123.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 123.53 | 0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67176 | 106.34 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.04286 | 108.31 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 2e-05 | 104.78 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.78 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.04631 | 107.6 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.00031 | 131.86 | P13:69-161:DPC:AUTO-SINGLE:GALENA8:GALENA5:2 | External | 131.77 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00067 | 109.21 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.00018 | 115.79 | P13:161-69:ITCM:LORE 5 T1:IA-NE | External | 115.75 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00879 | 115.09 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 113.73 | 1.36
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615400 GRE-PRKWDB27 115 997565 PAR115-69-2 69.0 2 | 140 | 140 | 0.00029 | 168.47 | 615397 GRE-PRKWDB18 69 3WXFMR PAR115-69-1 1: 615397 GRE-PRKWDB18 69.0 997559 PAR115-69-1 69.0 1 615396 GRE-PRKWDB17 115 997559 PAR115-69-1 69.0 1 615398 GRE-PRKWD 1T 12.8 997559 PAR115-69-1 69.0 1 615397 GRE-PRKWDB18 69.0 997563 PAR115-69-1 69.0 1 615396 GRE-PRKWDB17 115 997563 PAR115-69-1 69.0 1 615398 GRE-PRKWD 1T 12.8 997563 PAR115-69-1 69.0 1 | External | 168.44 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 1 | 67.2 | 82 | 0.00031 | 131.86 | 681520 GALENA 5 161 680441 GALENA8 69 2: 681520 GALENA 5 161 680441 GALENA8 69.0 2 | External | 131.77 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00071 | 115.85 | Base Case | External | 115.76 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04005 | 120.37 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 107.22 | 13.15
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06496 | 102.91 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04286 | 114.91 | P42:345:OKGE:SB_MICO7312 | Internal | 100.53 | 14.38
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00035 | 107.28 | P12:115:XEL:AUTO-SINGLE:GRE-DICKNSN7:GRE-CROWRIV7:1 | External | 107.19 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00063 | 102.89 | 631088 ARNOLD 5 161 631094 FAIRFAX5 161 1: 631088 ARNOLD 5 161 631094 FAIRFAX5 161 1 | External | 102.71 | 0.18
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 233 | 233 | 0.00082 | 109.58 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 109.45 | 0.13
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 209 | 212 | 0.03778 | 115.25 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 104.19 | 11.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631099 WYOMING5 161 630022 WYOMING8 69.0 1 | 63 | 63 | 2e-05 | 121.36 | P12:161:ALTW:AUTO-SINGLE:MQOKETA5:WYOMING5:1 | External | 121.36 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631108 DENMARK5 161 631109 BRLGTN 5 161 1 | 210 | 210 | 0.00121 | 170.12 | P12:161:ALTW:AUTO-SINGLE:DENMARK5:BRLGTN5:2 | External | 170.89 | -0.77
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631114 NEWPORT5 161 630052 NEWPORT8 69.0 1 | 60 | 60 | 0.00043 | 119.58 | P12:161:ALTW-MPW:AUTO-SINGLE:NEWPORT5:HWY615:1 | External | 119.68 | -0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00019 | 126.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 126.48 | 0.34
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 0.00052 | 179.16 | 636670 SB 18 5 161 636671 SB18#2 8 69 3: 636670 SB 18 5 161 636671 SB18#2 8 69.0 3 | External | 179.12 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.68552 | 108.03 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615396 GRE-PRKWDB17 115 997566 PAR115-69-1 69.0 1 | 140 | 140 | 0.00018 | 165.34 | Base Case | External | 165.32 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.0827 | 100.84 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00388 | 121.71 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 116.82 | 4.89
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636671 SB18#2 8 69.0 3 | 125 | 152 | 0.00038 | 104.96 | P13:69-161:MEC:AUTO-SINGLE:SB18#18:SB185:1 | External | 104.9 | 0.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 101.73 | P12:138:GRDA:CLEVLND-COLLINS | External | 101.2 | 0.53
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631108 DENMARK5 161 631109 BRLGTN 5 161 2 | 197 | 197 | 0.00069 | 103.36 | Base Case | External | 103.74 | -0.38
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631099 WYOMING5 161 630022 WYOMING8 69.0 1 | 63 | 63 | 2e-05 | 121.36 | 631098 MQOKETA5 161 631099 WYOMING5 161 1: 631098 MQOKETA5 161 631099 WYOMING5 161 1 | External | 121.36 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00069 | 123.38 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 123.28 | 0.1
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630679 ALTWTIF8 69.0 636421 TIFFIN 5 161 1 | 90 | 90 | 0.00062 | 104.13 | P12:161:ALTW:AUTO-SINGLE:ARNOLD5:DWNTWNIND5:1 | External | 103.95 | 0.18
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335378 4SCOTT_2! 138 502404 BONIN 4 138 1 | 225 | 225 | 5e-05 | 100.03 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00617 | 109.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.03006 | 106.62 | 83956: 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 101.81 | 4.81
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00077 | 105.93 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 105.78 | 0.15
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06275 | 125.53 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00851 | 106.17 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 105.14 | 1.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336224 3AMCYAN! 115 1 | 174 | 174 | 0.00037 | 111.73 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.64 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 0.00011 | 144.78 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1 | External | 144.8 | -0.02
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5084 | 131.8 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal | 104.01 | 27.79
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 0.00011 | 116.01 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 116 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 0.0004 | 171.43 | P11:15:MEC:AUTO-SINGLE:RIVSID5G:5 | External | 171.4 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00071 | 107.5 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 107.44 | 0.06
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 102.35 | 608673 ARROWHD7 115 608679 GARY 7 115 1: 608673 ARROWHD7 115 608679 GARY 7 115 1 | External | 102.35 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 214.77 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 215.26 | -0.49
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615396 GRE-PRKWDB17 115 997566 PAR115-69-1 69.0 1 | 140 | 140 | 0.00029 | 169.83 | 615401 GRE-PRKWDB28 69 3WXFMR PAR115-69-2 2: 615401 GRE-PRKWDB28 69.0 997558 PAR115-69-2 69.0 2 615400 GRE-PRKWDB27 115 997558 PAR115-69-2 69.0 2 615399 GRE-PRKWD 2T 12.8 997558 PAR115-69-2 69.0 2 615401 GRE-PRKWDB28 69.0 997562 PAR115-69-2 69.0 2 615400 GRE-PRKWDB27 115 997562 PAR115-69-2 69.0 2 615399 GRE-PRKWD 2T 12.8 997562 PAR115-69-2 69.0 2 | External | 169.8 | 0.03
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 0.00014 | 114.82 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 114.81 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615572 GRE-MEDINA 7 115 997537 115/69 69.0 1 | 84 | 84 | 0.00013 | 113.52 | Base Case | External | 113.52 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 619854 GRE-DICKNSN8 69.0 615354 GRE-DICKNSN7 115 1 | 84 | 84 | 0.00025 | 100.99 | Base Case | External | 100.94 | 0.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04386 | 133.05 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 112.57 | 20.48
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.04631 | 112.49 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00071 | 113.76 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 113.67 | 0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00132 | 125.32 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 125.41 | -0.09
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.0827 | 100.84 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.00036 | 126.32 | P13:69-161:DPC:AUTO-SINGLE:GALENA8:GALENA5:1 | External | 126.27 | 0.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 630249 WINDSOR8 69.0 613420 WINDSOR5 161 1 | 75 | 94 | 0.00019 | 105.46 | P13:161-69:ITCM-DPC:POSTVILLE 5 T1:IA-NE | External | 105.34 | 0.12
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 1 | 150 | 150 | 0.00028 | 109.91 | P13:69-161:ALTW:AUTO-SINGLE:DBQ8TH8:8THST.5:2 | External | 109.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.03778 | 119.96 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 108.88 | 11.08
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00347 | 106.76 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 106.4 | 0.36
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615433 GRE-BURNVIL7 115 997560 115/69 69.0 2 | 82.2 | 82.2 | 1e-05 | 112.01 | P12:115:XEL:CAR-SCO-GND | External | 112 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.00051 | 108.53 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 108.4 | 0.13
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 2 | 112 | 133.9 | 0.00015 | 125.06 | Base Case | External | 125.06 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631108 DENMARK5 161 631109 BRLGTN 5 161 2 | 197 | 197 | 0.00121 | 181.35 | P12:161:ALTW:AUTO-SINGLE:DENMARK5:BRLGTN5:1 | External | 182.17 | -0.82
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 | 222 | 0.10194 | 106.27 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681543 ALMA 5 161 680173 ALMA 8 69.0 1 | 112 | 133.9 | 0.00026 | 114.96 | P13:69-161:DPC:AUTO-SINGLE:ALMA8:ALMA5:2 | External | 114.96 | 0
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 680001 STONE 69.0 1 | 67.2 | 81.4 | 0.00011 | 116.01 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 116 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04386 | 133.05 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 112.57 | 20.48
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615403 GRE-LIBERTY7 115 997564 LIB115-69-1 69.0 1 | 140 | 140 | 6e-05 | 149.21 | 71569: 601019 COON CK3 345 997666 90199-A 115 10 603068 COON CK7 115 997666 90199-A 115 10 605017 CNCTER29 34.5 997666 90199-A 115 10 601011 SHERCO 3 345 601019 COON CK3 345 1 601011 SHERCO 3 345 615327 GRE-BUNKER 3 345 2 601019 COON CK3 345 615327 GRE-BUNKER 3 345 2 615327 GRE-BUNKER 3 345 997571 345/230 230 1 601019 COON CK3 345 997667 90199-A 115 10 603068 COON CK7 115 997667 90199-A 115 10 605017 CNCTER29 34.5 997667 90199-A 115 10 615327 GRE-BUNKER 3 345 997575 345/230 230 1 | External | 149.23 | -0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 1 | 150 | 150 | 0.00028 | 109.91 | 631059 8TH ST.5 161 630290 DBQ 8TH8 69 2: 631059 8TH ST.5 161 630290 DBQ 8TH8 69.0 2 | External | 109.87 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 118.9 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 118.7 | 0.2
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615433 GRE-BURNVIL7 115 997560 115/69 69.0 2 | 82.2 | 82.2 | 9e-05 | 118.56 | 615434 GRE-BURNVIL8 69 3WXFMR 115/69 1: 615434 GRE-BURNVIL8 69.0 997552 115/69 69.0 1 615433 GRE-BURNVIL7 115 997552 115/69 69.0 1 615435 GRE-BURNVL1T 13.8 997552 115/69 69.0 1 615434 GRE-BURNVIL8 69.0 997557 115/69 69.0 1 615433 GRE-BURNVIL7 115 997557 115/69 69.0 1 615435 GRE-BURNVL1T 13.8 997557 115/69 69.0 1 | External | 118.52 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 118.56 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 118.36 | 0.2
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 605662 LUFKIN 69.0 681545 LUFKIN 161 6 | 112 | 128.8 | 2e-05 | 111.45 | Base Case | External | 111.47 | -0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681530 POSTVIL5 161 680048 POST 69.0 1 | 67.2 | 82 | 1e-05 | 109.34 | P22:345:XEL:ADAMS 3 N1:MN | External | 109.33 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00388 | 121.71 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 116.82 | 4.89
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00073 | 103.47 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 103.43 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 521031 POCASET4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03109 | 102.5 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631109 BRLGTN 5 161 630037 BRLGTN18 69.0 1 | 112 | 112 | 0.00026 | 128.14 | 631109 BRLGTN 5 161 630038 BRLGTN28 69 1: 631109 BRLGTN 5 161 630038 BRLGTN28 69.0 1 | External | 128.28 | -0.14
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00915 | 130.79 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 129.91 | 0.88
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 636670 SB 18 5 161 636669 SB18#1 8 69.0 1 | 167 | 208 | 0.00052 | 179.16 | P13:161-69:MEC:AUTO-SINGLE:SB185:SB18#28:3 | External | 179.12 | 0.04
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615390 GRE-LINWOOD4 230 997567 230/69 69.0 1 | 112 | 112 | 9e-05 | 101.33 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1 | External | 101.31 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 615433 GRE-BURNVIL7 115 997560 115/69 69.0 2 | 82.2 | 82.2 | 5e-05 | 105.19 | Base Case | External | 105.18 | 0.01
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.0011 | 118.43 | Base Case | External | 118.56 | -0.13
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 631174 GLENWRTH5 161 680542 GLENWTH8 69.0 1 | 107 | 139 | 0.0001 | 111.38 | Base Case | External | 111.36 | 0.02
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 681520 GALENA 5 161 680441 GALENA8 69.0 2 | 112 | 125 | 0.00036 | 126.32 | 681520 GALENA 5 161 680441 GALENA8 69 1: 681520 GALENA 5 161 680441 GALENA8 69.0 1 | External | 126.27 | 0.05
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00074 | 103.19 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 103.98 | -0.79
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00701 | 128.91 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 128.6 | 0.31
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00082 | 101.79 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 101.64 | 0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00022 | 143.44 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 143.41 | 0.03
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00382 | 102.54 | P12:230:CLEC::RODEMR 6:SHERWD 6:1 | External | 102.28 | 0.26
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 227.84 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 227.77 | 0.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 120.96 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 120.77 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06359 | 102.68 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 176 | 176 | 0.00223 | 109.76 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 109.15 | 0.61
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00879 | 166.13 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 165.04 | 1.09
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00701 | 137.8 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 137.47 | 0.33
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04124 | 100.01 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00026 | 123.14 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 123.58 | -0.44
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508056 BRYANML4 138 508064 MUNZCTY4 138 1 | 176 | 188 | 0.03056 | 109.41 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00082 | 110.85 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 110.7 | 0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00035 | 105.39 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 105.54 | -0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03278 | 127.2 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 119.3 | 7.9
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03278 | 127.21 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 119.33 | 7.88
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00281 | 111.64 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 111.25 | 0.39
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00015 | 100.37 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 100.35 | 0.02
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.08511 | 104.32 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 120.96 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.77 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 | 318.7 | 318.7 | 0.03307 | 118.27 | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | Internal | 111.64 | 6.63
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00031 | 114.91 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 115.29 | -0.38
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00742 | 103.22 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 102 | 1.22
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00046 | 104.64 | P12:69:GRDA:PAWNEEGR-CLEVDSTK | External | 103.99 | 0.65
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00879 | 147.19 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 145.96 | 1.23
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00045 | 113.69 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 113.63 | 0.06
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00015 | 134.45 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 134.44 | 0.01
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0391 | 131.3 | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | Internal | 123.6 | 7.7
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00304 | 105.09 | 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1: 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1 | External | 104.24 | 0.85
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00121 | 124.23 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 122.85 | 1.38
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 227.84 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 227.77 | 0.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672538 BEATTY 6 138 672547 HUMBOLDT 6 138 1 | 115.8 | 115.8 | 1e-05 | 100.36 | 672639 ABERDEEN 4 230 672644 ALLAN 4 230 1: 672639 ABERDEEN 4 230 672644 ALLAN 4 230 1 | External | 100.42 | -0.06
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00304 | 105.03 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 104.18 | 0.85
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508050 ANDRSNC4 138 508056 BRYANML4 138 1 | 176 | 188 | 0.03056 | 109.76 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 1 | 101.15 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06304 | 120.49 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00082 | 101.79 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 101.64 | 0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 176 | 176 | 0.0025 | 103.65 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 103.01 | 0.64
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03454 | 104.61 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 120.96 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.77 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03454 | 104.55 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 620263 FORMN 7 115 997497 230/115 115 1 | 112 | 132 | 0.00064 | 100.86 | 620327 HANKSON4 230 620329 WAHPETN4 230 1: 620327 HANKSON4 230 620329 WAHPETN4 230 1 | External | 100.78 | 0.08
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03693 | 101.91 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00732 | 111.36 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 110.29 | 1.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 25 | 31 | 0.00021 | 112.99 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 112.54 | 0.45
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 3e-05 | 104.28 | P11:345:MEC:GDMEC ST | External | 104.51 | -0.23
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06304 | 126.43 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00742 | 129.16 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 128.14 | 1.02
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635002 CBLUFFS8 69.0 1 | 125 | 156.3 | 0.00158 | 104.17 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 103.67 | 0.5
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00031 | 114.91 | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 115.29 | -0.38
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.04345 | 104.08 | P13:138-345:OKGE:BKRBKR_3W013 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03552 | 100.41 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 603016 SPLT RK7 115 997675 SPLT 11 115 11 | 358.5 | 358.5 | 0.00174 | 107.72 | P23:345:XEL:492 BKR SPK AS | External | 107.46 | 0.26
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06304 | 107.17 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06168 | 112.1 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 107.02 | 5.08
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06304 | 113 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00304 | 113.23 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 112.41 | 0.82
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04353 | 114.12 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 104.04 | 10.08
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.06477 | 114.68 | 926261: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500540 MANUEL 4 138 1 | 268 | 287 | 0.00021 | 106.67 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 106.65 | 0.02
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00755 | 121.67 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 120.84 | 0.83
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00304 | 113.23 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 112.41 | 0.82
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 1e-05 | 126.7 | P13:69-161:AECI-ALTW:AUTO-SINGLE:2HENRY:HENRYCO5:1 | External | 126.77 | -0.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631078 WNTRST 5 161 635645 MCKSBRG 5 161 1 | 154 | 154 | 3e-05 | 100.86 | P23:345:MEC:GDMEC 908 | External | 100.94 | -0.08
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06304 | 114.09 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.05014 | 123.05 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 110.57 | 12.48
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.03693 | 101.91 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00015 | 109.3 | Base Case | External | 109.4 | -0.1
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00755 | 138.06 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 137.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04465 | 110.99 | P42:345:OKGE:SB_MICO7301 | Internal | 100.47 | 10.52
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 601006 SPLT RK3 345 997675 SPLT 11 115 11 | 358.5 | 358.5 | 0.00174 | 106.92 | P23:345:XEL:492 BKR SPK AS | External | 106.63 | 0.29
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00104 | 130.81 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 130.62 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00068 | 117.68 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 117.86 | -0.18
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635004 SUB701 8 69.0 1 | 89.6 | 118.3 | 0.00347 | 139.5 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 136.81 | 2.69
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00015 | 100.44 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 100.43 | 0.01
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05399 | 106.63 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04426 | 123.19 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal | 101.41 | 21.78
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00071 | 102.96 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 102.93 | 0.03
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00104 | 121.13 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 120.94 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00171 | 104.68 | P23:500:AEPW-EES:ABF_HTBG-A | External | 104.39 | 0.29
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 4e-05 | 102.76 | Base Case | External | 102.8 | -0.04
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00406 | 124.18 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 119.33 | 4.85
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06168 | 112.1 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 107.02 | 5.08
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00755 | 129.15 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 128.39 | 0.76
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00382 | 102.54 | P12:230:CLEC:RODEMR1:SHRWD7:1 | External | 102.28 | 0.26
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00038 | 106.79 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 106.92 | -0.13
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00732 | 103.63 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 102.45 | 1.18
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 106.2 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 106.04 | 0.16
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | 56 | 56 | 1e-05 | 126.7 | 300439 2HENRY 69 631106 HENRYCO5 161 1: 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | External | 126.77 | -0.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 362 | 424 | 0.04614 | 114.87 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 108.13 | 6.74
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508050 ANDRSNC4 138 508104 RIFFIN REC4 138 1 | 187 | 188 | 0.03056 | 121.21 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 111.42 | 9.79
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 2e-05 | 102.76 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 102.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00742 | 119.82 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 118.72 | 1.1
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00732 | 120.21 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 119.15 | 1.06
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0004 | 104.56 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 103.83 | 0.73
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00304 | 106.4 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 106.07 | 0.33
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00304 | 106.4 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 106.07 | 0.33
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 1 | 101.15 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00382 | 102.54 | 500770 RODEMR 6 230 500790 SHERWD 6 230 1: 500770 RODEMR 6 230 500790 SHERWD 6 230 1 | External | 102.28 | 0.26
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 | 382 | 382 | 0.00348 | 103.48 | 67888: 334072 4LEWIS% 138 334090 4ALDEN! 138 1 334087 4PONDEROSA% 138 334105 4WDHAVN 138 1 334087 4PONDEROSA% 138 334104 4CONROE1! 138 1 | External | 103.2 | 0.28
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06562 | 100.3 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00015 | 100.44 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 100.43 | 0.01
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00074 | 103.11 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 103.95 | -0.84
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00701 | 148.65 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 148.43 | 0.22
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00036 | 102.4 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External | 102.58 | -0.18
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00304 | 113.23 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 112.41 | 0.82
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05399 | 109.62 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00071 | 106.82 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.79 | 0.03
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04465 | 112.78 | P42:345:OKGE:SB_CION7384 | Internal | 102.28 | 10.5
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 106.2 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 106.04 | 0.16
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00879 | 156.13 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 154.91 | 1.22
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 1 | 101.15 | P12:345:AEPW:L.E.S7:TERRYRD7 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0391 | 145.37 | 83860: 525811 LH-HARMONY 2 69.0 525874 LH-PETERBRG2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525867 ALLMON 2 69.0 525874 LH-PETERBRG2 69.0 1 525779 FLOYD_CNTY 2 69.0 525811 LH-HARMONY 2 69.0 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | Internal | 137.09 | 8.28
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06562 | 100.3 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00079 | 139.7 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 139.61 | 0.09
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.08528 | 104.49 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00395 | 123.58 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.44 | 5.14
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.0004 | 104.56 | P12:138:GRDA:CLEVLND-COLLINS | External | 103.83 | 0.73
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.00021 | 118.89 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 118.86 | 0.03
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 176 | 176 | 0.0025 | 103.65 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 103.01 | 0.64
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508069 NNBOSTN4 138 508104 RIFFIN REC4 138 1 | 188 | 188 | 0.03056 | 123.5 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 113.67 | 9.83
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00082 | 110.85 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 110.7 | 0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 335455 4CHAMPAGNE! 138 500720 PLAISAN4 138 1 | 268 | 287 | 0.00341 | 101.63 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 101.25 | 0.38
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00701 | 121.29 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 120.9 | 0.39
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00026 | 123.14 | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | External | 123.58 | -0.44
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 121.32 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 121.13 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 1e-05 | 153.01 | 300439 2HENRY 69 631106 HENRYCO5 161 2: 300439 2HENRY 69.0 631106 HENRYCO5 161 2 | External | 153.07 | -0.06
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 121.32 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.13 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 227.84 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 227.77 | 0.07
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04426 | 138.09 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 117.42 | 20.67
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 2e-05 | 102.76 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 102.71 | 0.05
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.08528 | 104.49 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00053 | 109.56 | P23:345:ITCM:HCKRYCK:FUT2 | External | 110.05 | -0.49
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00052 | 115.96 | P23:345:ITCM:HCKRYCK:FUT2 | External | 116.51 | -0.55
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00071 | 107.93 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.9 | 0.03
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05212 | 111.11 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00304 | 105.03 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 104.18 | 0.85
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00341 | 114.03 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 113.7 | 0.33
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635002 CBLUFFS8 69.0 2 | 125 | 156.3 | 0.00158 | 104.17 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 103.67 | 0.5
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06767 | 103.99 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 121.32 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.13 | 0.19
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00019 | 110.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.14 | 0.15
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04426 | 138.09 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 117.42 | 20.67
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00035 | 105.32 | 92409: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 541158 GRNWD#4 13.2 997783 GREENWOOD 1 13.2 1 541155 GRNWD#1 13.2 997784 GREENWOOD 1 13.2 1 541156 GRNWD#2 13.2 997784 GREENWOOD 1 13.2 1 541157 GRNWD#3 13.2 997783 GREENWOOD 1 13.2 1 | External | 105.46 | -0.14
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06304 | 100.92 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00732 | 129.56 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 128.56 | 1
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 105.14 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 104.73 | 0.41
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00395 | 123.58 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.44 | 5.14
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00755 | 148.66 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 147.94 | 0.72
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00879 | 141.16 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 139.78 | 1.38
Thermal | 00NR | S2 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00742 | 110.96 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 109.86 | 1.1
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.5001 | 120.76 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00403 | 109.1 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 104.65 | 4.45
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07803 | 107.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 103 | 4.58
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00392 | 108.75 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 104.19 | 4.56
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.0639 | 109.59 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 104.43 | 5.16
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03322 | 121.71 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 109.69 | 12.02
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00334 | 103.07 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 102.07 | 1
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03322 | 121.6 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 109.59 | 12.01
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04792 | 132.8 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 121.05 | 11.75
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 603020 MAPLE R7 115 997618 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00083 | 127.09 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997179 FA KV1A 115 1 652436 FARGO 7 115 997179 FA KV1A 115 1 652434 FARGOSVC 13.2 997179 FA KV1A 115 1 652435 FARGO 4 230 997178 FA KV2A 115 2 652436 FARGO 7 115 997178 FA KV2A 115 2 652434 FARGOSVC 13.2 997178 FA KV2A 115 2 | External | 128.08 | -0.99
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 183 | 201 | 0.03583 | 100.96 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50869 | 131.79 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal | 103.99 | 27.8
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.0564 | 101.87 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00023 | 131.05 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 131.01 | 0.04
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.0009 | 107.8 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 107.61 | 0.19
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66281 | 119.14 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.0009 | 107.8 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 107.61 | 0.19
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 423 | 474 | 0.04473 | 121.22 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 119.83 | 1.39
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.01054 | 107.27 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 106.5 | 0.77
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00017 | 235.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.94 | 0.09
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00048 | 121.85 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 121.67 | 0.18
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 171 | 185 | 0.06273 | 107.44 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.65904 | 121.97 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 484 | 484 | 0.01003 | 103.77 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 103.74 | 0.03
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00332 | 104.83 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 104.44 | 0.39
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48051 | 118.14 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 491 | 491 | 0.01003 | 111.73 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 111.88 | -0.15
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00415 | 102.26 | P12:230:CLEC::RODEMR 6:SHERWD 6:1 | External | 101.95 | 0.31
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00048 | 122.2 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 122.02 | 0.18
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00048 | 122.2 | P13:161-69:EES-EAI:HERGET:AT1 | External | 122.02 | 0.18
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.01688 | 101.63 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | External
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.00031 | 113.19 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 112.7 | 0.49
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635004 SUB701 8 69.0 1 | 89.6 | 128.8 | 0.00409 | 105.49 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 103.06 | 2.43
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.0009 | 100.24 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 100.07 | 0.17
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00415 | 102.26 | 500770 RODEMR 6 230 500790 SHERWD 6 230 1: 500770 RODEMR 6 230 500790 SHERWD 6 230 1 | External | 101.95 | 0.31
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00017 | 235.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.94 | 0.09
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.0639 | 109.59 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 104.43 | 5.16
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06353 | 129.16 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal | 114.25 | 14.91
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0373 | 109.65 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00415 | 102.26 | P12:230:CLEC:RODEMR1:SHRWD7:1 | External | 101.95 | 0.31
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04425 | 149.41 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 133.08 | 16.33
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.01054 | 124.27 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 123.7 | 0.57
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 253 | 279 | 0.05265 | 102.33 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00048 | 121.85 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.67 | 0.18
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.4823 | 117.38 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07803 | 107.58 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 103 | 4.58
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0373 | 109.57 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02577 | 134.82 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 126.12 | 8.7
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03056 | 136.57 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 129.15 | 7.42
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00334 | 103.07 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 102.07 | 1
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00012 | 108.92 | Base Case | External | 108.85 | 0.07
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03056 | 136.61 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 129.2 | 7.41
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.0002 | 110.02 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 109.99 | 0.03
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 620263 FORMN 7 115 997498 230/115 115 1 | 112 | 140 | 0.00074 | 110.98 | 620327 HANKSON4 230 620329 WAHPETN4 230 1: 620327 HANKSON4 230 620329 WAHPETN4 230 1 | External | 110.95 | 0.03
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04138 | 120.72 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 111.43 | 9.29
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 253 | 279 | 0.05105 | 108.53 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.00023 | 111.17 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 111.12 | 0.05
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00306 | 107.62 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 107.14 | 0.48
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07792 | 107.3 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal | 102.73 | 4.57
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00372 | 109.97 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 109.53 | 0.44
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00332 | 104.83 | 500190 COCODR 6 230 500880 VILPLT 6 230 1: 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 104.44 | 0.39
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06554 | 135.32 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal | 119.84 | 15.48
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00048 | 121.85 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.67 | 0.18
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00048 | 122.2 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 122.02 | 0.18
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50029 | 129 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal | 100.58 | 28.42
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.0564 | 101.88 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 253 | 279 | 0.05298 | 107.67 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 171 | 185 | 0.06273 | 100.38 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0373 | 111.45 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 620263 FORMN 7 115 997498 230/115 115 1 | 112 | 140 | 0.00074 | 110.98 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External | 110.95 | 0.03
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 253 | 279 | 0.05298 | 105.21 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 183 | 201 | 0.03583 | 100.96 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04251 | 120.24 | P42:345:OKGE:SB_CION7384 | Internal | 110.63 | 9.61
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04425 | 149.41 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 133.08 | 16.33
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 337502 3COUCH% 115 338874 3LEWISVILLE# 115 1 | 159 | 159 | 0.02577 | 124.87 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 113.52 | 11.35
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66281 | 119.95 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00016 | 117.34 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 117.32 | 0.02
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.0005 | 108.71 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 108.63 | 0.08
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.01688 | 101.63 | P23:345:AEPW:WELSH CB 11990 NBTB | External
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.0373 | 113.59 | P12:345:OKGE:BKRBKR24 | Internal | 100.55 | 13.04
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00334 | 103.07 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 102.07 | 1
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04251 | 118.65 | P42:345:OKGE:SB_MICO7301 | Internal | 109 | 9.65
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.4823 | 116.93 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66082 | 120.97 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.00151 | 109.63 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 108.23 | 1.4
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00017 | 235.03 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 234.94 | 0.09
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00114 | 123.64 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 123.39 | 0.25
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00392 | 108.75 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 104.19 | 4.56
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00078 | 103.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 103.63 | 0.05
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.0002 | 110.02 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 109.99 | 0.03
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50026 | 128.98 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal | 100.56 | 28.42
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 176 | 176 | 0.00241 | 100.12 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.0009 | 100.24 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 100.07 | 0.17
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06353 | 129.16 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal | 114.25 | 14.91
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00078 | 102.63 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 102.58 | 0.05
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.0564 | 101.88 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66281 | 120.87 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 171 | 185 | 0.06273 | 104.11 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66649 | 125.99 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00086 | 136.27 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 136.1 | 0.17
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04425 | 137.57 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal | 118.66 | 18.91
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00114 | 116.02 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 115.77 | 0.25
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00186 | 100.8 | P23:500:AEPW-EES:ABF_HTBG-A | External | 100.46 | 0.34
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50029 | 116.92 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00884 | 113.55 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 110.52 | 3.03
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00083 | 103.07 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 103.03 | 0.04
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48196 | 116.91 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00022 | 138.73 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 138.74 | -0.01
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 191 | 191 | 0.04664 | 100.73 | 81374: 515135 SUNNYSD4 138 515144 LONEGRV4 138 1 515135 SUNNYSD4 138 515164 ROCKYPT4 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00385 | 109.76 | P12:230:CLEC::RODEMR 6:SHERWD 6:1 | External | 109.69 | 0.07
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 234.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.67 | -0.54
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 121.58 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 121.15 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06381 | 101.01 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335455 4CHAMPAGNE! 138 500720 PLAISAN4 138 1 | 268 | 287 | 0.00308 | 103.58 | 500190 COCODR 6 230 500880 VILPLT 6 230 1: 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 103.49 | 0.09
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.01002 | 160.01 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 156.48 | 3.53
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00884 | 121.46 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 118.39 | 3.07
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04086 | 102.23 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0402 | 100.41 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00083 | 111.82 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 111.76 | 0.06
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04021 | 100.4 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03236 | 125.95 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 118.04 | 7.91
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03236 | 125.95 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 118.07 | 7.88
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500540 MANUEL 4 138 1 | 268 | 287 | 0.0024 | 104.45 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 104.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00284 | 118.04 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 117.89 | 0.15
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.08174 | 112.82 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal | 108.13 | 4.69
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 121.58 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.15 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00079 | 111.59 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 110.84 | 0.75
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03816 | 100.65 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05236 | 127.3 | P42:345:OKGE:SB_MICO7301 | Internal | 112.68 | 14.62
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.0087 | 103.9 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 100.34 | 3.56
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.01002 | 137.38 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 133.16 | 4.22
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.01002 | 142.54 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 138.73 | 3.81
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00046 | 115.16 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 115.13 | 0.03
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335390 4BAYOU_WHSE! 138 500440 IVANHOE4 138 1 | 135 | 145 | 0.00145 | 100.18 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 100.1 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00015 | 129.17 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 129.17 | 0
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00145 | 110.6 | 80248: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500580 MORBHAN4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 110.49 | 0.11
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66488 | 104.07 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00125 | 121.76 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 122.02 | -0.26
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 234.13 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 234.67 | -0.54
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06286 | 107.87 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 2e-05 | 113.41 | 608676 HIBBARD7 115 608680 WNTR ST7 115 1: 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.05663 | 102.17 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.07954 | 104.96 | P12:345:OKGE:BKRBKR21 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04021 | 100.4 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06286 | 121.66 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00034 | 103.23 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 512705 COLLINS4 138 998340 COLAUTO3 138 1 | External | 103.05 | 0.18
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00083 | 103.07 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 103.03 | 0.04
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03412 | 107.93 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48196 | 117.35 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03412 | 107.85 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.0366 | 102.66 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50026 | 128.98 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal | 100.56 | 28.42
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.0002 | 106.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.56 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00063 | 116.69 | Base Case | External | 114.58 | 2.11
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06286 | 127.56 | P42:345:OKGE:SB_JOCO7303 | Internal | 100.95 | 26.61
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.0087 | 120.91 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 117.55 | 3.36
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50029 | 114.06 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03507 | 103.28 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.0087 | 111.77 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 108.23 | 3.54
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06181 | 110.5 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 106.79 | 3.71
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00052 | 109.27 | P23:345-161:XEL:ADAMS_I:681_S | External | 107.11 | 2.16
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06286 | 113.73 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 176 | 176 | 0.00225 | 101.01 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 100.82 | 0.19
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0005 | 116.38 | P23:345-161:XEL:ADAMS_I:681_S | External | 114.4 | 1.98
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02534 | 111.53 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 104.3 | 7.23
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00308 | 107.58 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 107.12 | 0.46
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04307 | 113.9 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 104.01 | 9.89
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.05663 | 102.16 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.0634 | 129.15 | 926261: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | Internal | 112.52 | 16.63
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500540 MANUEL 4 138 1 | 268 | 287 | 0.00021 | 108.87 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 108.91 | -0.04
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00925 | 107.67 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 104.19 | 3.48
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00308 | 107.58 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 107.12 | 0.46
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67861 | 105.4 | 926261: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06286 | 115.18 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 | 100 | 112 | 0.00042 | 121.58 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.15 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00925 | 114.71 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 111.49 | 3.22
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00925 | 122.63 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 119.39 | 3.24
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.0087 | 120.91 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 117.55 | 3.36
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04419 | 110.84 | P42:345:OKGE:SB_MICO7301 | Internal | 100.54 | 10.3
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00105 | 128.98 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 128.87 | 0.11
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5001 | 127.37 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00082 | 112.26 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 111.06 | 1.2
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635004 SUB701 8 69.0 1 | 89.6 | 118.3 | 0.00412 | 131.08 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 125.01 | 6.07
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67073 | 109.05 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04381 | 129 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal | 110.22 | 18.78
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00072 | 101.99 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.98 | 0.01
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00105 | 119.81 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 119.7 | 0.11
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00173 | 104.58 | P23:500:AEPW-EES:ABF_HTBG-A | External | 104.5 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 7e-05 | 104.41 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00403 | 122.92 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 118.63 | 4.29
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.03412 | 101.85 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 2e-05 | 104.68 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.12 | -9.44
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06181 | 110.5 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 106.79 | 3.71
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00042 | 104.05 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 104.18 | -0.13
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500540 MANUEL 4 138 1 | 268 | 287 | 0.0024 | 104.45 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 104.37 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 362 | 424 | 0.04487 | 122.01 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 116.93 | 5.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 2e-05 | 104.68 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.12 | -9.44
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.0087 | 111.77 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 108.23 | 3.54
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00034 | 103.63 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 104.27 | -0.64
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00308 | 112.47 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 112.39 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00385 | 109.76 | 500770 RODEMR 6 230 500790 SHERWD 6 230 1: 500770 RODEMR 6 230 500790 SHERWD 6 230 1 | External | 109.69 | 0.07
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06476 | 108.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00308 | 112.47 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 112.39 | 0.08
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00385 | 109.76 | P12:230:CLEC:RODEMR1:SHRWD7:1 | External | 109.69 | 0.07
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00839 | 128.92 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00038 | 102.63 | 92373: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | External | 102.87 | -0.24
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00145 | 154.4 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 154.28 | 0.12
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00884 | 131.45 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 128.49 | 2.96
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 145 | 169 | 0.0366 | 102.66 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.71044 | 103.51 | 92676: 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 563270 G15093_1 345 1 515800 GRACMNT7 345 587744 G16-091-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 515800 GRACMNT7 345 998204 GRACMNT3 138 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00072 | 106.87 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.86 | 0.01
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00039 | 100.25 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335390 4BAYOU_WHSE! 138 1 | 112 | 112 | 0.00145 | 133.93 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 133.82 | 0.11
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00308 | 107.58 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 107.12 | 0.46
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05236 | 130.35 | P42:345:OKGE:SB_CION7384 | Internal | 115.76 | 14.59
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00072 | 105.78 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.77 | 0.01
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04419 | 112.56 | P42:345:OKGE:SB_CION7384 | Internal | 102.3 | 10.26
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00063 | 115.06 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 112.94 | 2.12
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.01002 | 150.49 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 146.7 | 3.79
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66656 | 104.06 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00066 | 111.56 | Base Case | External | 109.25 | 2.31
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335455 4CHAMPAGNE! 138 500720 PLAISAN4 138 1 | 268 | 287 | 0.00308 | 103.58 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 103.49 | 0.09
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 233 | 233 | 0.00081 | 104.94 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 104.91 | 0.03
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.0008 | 137.69 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 137.74 | -0.05
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 133.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.59 | 0.31
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.67861 | 105.42 | 926260: 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.0819 | 113 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 108.29 | 4.71
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00392 | 122.42 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.02 | 4.4
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00034 | 103.63 | P12:138:GRDA:CLEVLND-COLLINS | External | 104.27 | -0.64
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00079 | 104.07 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 103.63 | 0.44
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.00021 | 117.53 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 117.51 | 0.02
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0005 | 116.38 | P23:345-161:XEL:ADAMS_I:680_S | External | 114.4 | 1.98
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00839 | 107.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00083 | 111.82 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 111.76 | 0.06
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 335455 4CHAMPAGNE! 138 500720 PLAISAN4 138 1 | 268 | 287 | 0.00345 | 110.94 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 110.88 | 0.06
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00884 | 106.35 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 103.08 | 3.27
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 121.93 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 121.5 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 121.93 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.5 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 | 185 | 185 | 0.00046 | 101.28 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 101.27 | 0.01
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 105.2 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 104.8 | 0.4
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 3e-05 | 234.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 234.67 | -0.54
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 2e-05 | 104.14 | 608633 FAIRMPK7 115 608683 STIN-MN7 115 1: 608633 FAIRMPK7 115 608683 STIN-MN7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04381 | 143.6 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 125.67 | 17.93
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 970 | 970 | 0.0819 | 113 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 108.29 | 4.71
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05048 | 132.16 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 118.29 | 13.87
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 209 | 212 | 0.03412 | 101.8 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00345 | 120.17 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 120.11 | 0.06
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06676 | 113.16 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 | 100 | 112 | 0.00042 | 121.93 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.5 | 0.43
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 158 | 0.05663 | 102.17 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04964 | 123.15 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 110.78 | 12.37
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 | 222 | 0.10194 | 101.87 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00066 | 108.22 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 106.03 | 2.19
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04381 | 143.6 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 125.67 | 17.93
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 608673 ARROWHD7 115 608679 GARY 7 115 1 | 217 | 217 | 2e-05 | 107.1 | 608633 FAIRMPK7 115 608680 WNTR ST7 115 1: 608633 FAIRMPK7 115 608680 WNTR ST7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06286 | 101.47 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06476 | 108.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00392 | 122.42 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.02 | 4.4
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00925 | 132.48 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 129.35 | 3.13
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.0087 | 103.9 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 100.34 | 3.56
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00052 | 109.27 | P23:345-161:XEL:ADAMS_I:680_S | External | 107.11 | 2.16
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00022 | 147.49 | P23:500:EES-EAI:WH_BLF:B7914 | External | 147.32 | 0.17
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.0041 | 103.8 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50026 | 116.91 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07806 | 105.01 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 100.45 | 4.56
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06323 | 105.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | Internal | 100.44 | 5.14
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03697 | 137.13 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 124.19 | 12.94
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50026 | 114.05 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997063 GLENHAM TR1 115 1 | 25 | 31 | 0.00031 | 105.29 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 104.8 | 0.49
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49975 | 127.35 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00041 | 168.55 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 168.47 | 0.08
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66945 | 120.86 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00399 | 101.84 | P12:230:CLEC::RODEMR 6:SHERWD 6:1 | External | 101.55 | 0.29
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00771 | 109.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 109.03 | 0.8
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00083 | 105.23 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 105.07 | 0.16
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 221.04 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 220.95 | 0.09
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 248 | 263 | 0.03697 | 100.11 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50026 | 114.05 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334026 4GRIMES% 138 334060 4MT.ZION 138 1 | 206 | 206 | 0.00445 | 100.51 | P23:500:AEPW-EES:ABF_HTBG-A | External
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66555 | 124 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334087 4PONDEROSA% 138 1 | 112 | 112 | 0.00576 | 120.36 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 118.6 | 1.76
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 9e-05 | 101.02 | Base Case | External | 100.83 | 0.19
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 128.39 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 126.64 | 1.75
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 484 | 484 | 0.00937 | 111.83 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 110.8 | 1.03
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00308 | 103.87 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 103.51 | 0.36
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00399 | 103.43 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06593 | 135.27 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal | 119.05 | 16.22
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 491 | 491 | 0.00937 | 119.86 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 118.99 | 0.87
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.05627 | 100.73 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00371 | 103.93 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 103.5 | 0.43
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 114.43 | P13:161-69:EES-EAI:HERGET:AT2 | External | 114.23 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635004 SUB701 8 69.0 1 | 89.6 | 128.8 | 0.00368 | 119.61 | 82312: 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 118.05 | 1.56
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00014 | 119.21 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 119.2 | 0.01
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00399 | 101.84 | 500770 RODEMR 6 230 500790 SHERWD 6 230 1: 500770 RODEMR 6 230 500790 SHERWD 6 230 1 | External | 101.55 | 0.29
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 221.04 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 220.95 | 0.09
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.06323 | 105.58 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 100.44 | 5.14
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06392 | 129.19 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal | 113.85 | 15.34
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04199 | 120.04 | P42:345:OKGE:SB_MICO7312 | Internal | 106.16 | 13.88
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 128.39 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 126.64 | 1.75
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500760 RAPIDES6 230 500770 RODEMR 6 230 1 | 680 | 690 | 0.00399 | 101.84 | P12:230:CLEC:RODEMR1:SHRWD7:1 | External | 101.55 | 0.29
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00083 | 105.23 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 105.07 | 0.16
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04434 | 146.89 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 129.32 | 17.57
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07806 | 105.01 | P23:345:AEPW:WELSH CB 11990 NBTB | Internal | 100.45 | 4.56
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04199 | 119.94 | P42:345:OKGE:SB_MICO7301 | Internal | 106.03 | 13.91
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03697 | 136.99 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 124.12 | 12.87
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02577 | 133.16 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 124.18 | 8.98
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00576 | 148.43 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 146.65 | 1.78
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336224 3AMCYAN! 115 1 | 174 | 174 | 0.0004 | 110.32 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.22 | 0.1
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00314 | 108.2 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 107.72 | 0.48
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1220 | 1220 | 0.07798 | 104.69 | 84117: 507760 SW SHV 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508563 PIRKEY 7 345 508832 DIANA 7 345 1 508832 DIANA 7 345 998444 DIANA 1 138 1 508832 DIANA 7 345 998443 DIANA 2 138 2 508832 DIANA 7 345 998442 DIANA 3 138 3 508832 DIANA 7 345 998441 DIANA 1 138 1 508832 DIANA 7 345 998440 DIANA 2 138 2 508832 DIANA 7 345 998439 DIANA 3 138 3 | Internal | 100.16 | 4.53
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00771 | 131.03 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 130.63 | 0.4
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336225 3WAGGMN 115 1 | 174 | 174 | 0.00049 | 126.24 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.11 | 0.13
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 171 | 185 | 0.06275 | 100.55 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00077 | 106.36 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.31 | 0.05
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.4823 | 123.31 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.05627 | 100.75 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00576 | 148.43 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 146.65 | 1.78
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00308 | 103.87 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 103.51 | 0.36
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00576 | 148.43 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 146.65 | 1.78
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 114.76 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 114.56 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04199 | 122.05 | P42:345:OKGE:SB_CION7384 | Internal | 108.18 | 13.87
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00077 | 105.3 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.25 | 0.05
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 128.52 | 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1: 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1 | External | 126.78 | 1.74
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334087 4PONDEROSA% 138 1 | 112 | 112 | 0.00576 | 120.36 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 118.6 | 1.76
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04434 | 146.89 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 129.32 | 17.57
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336225 3WAGGMN 115 336280 39MILE% 115 1 | 174 | 174 | 0.00049 | 120.24 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.11 | 0.13
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 337502 3COUCH% 115 338874 3LEWISVILLE# 115 1 | 159 | 159 | 0.02577 | 123.3 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External | 111.86 | 11.44
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 508070 NWT-BNT4 138 508071 NWTXARK4 138 1 | 423 | 474 | 0.04499 | 121.53 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | Internal | 120.12 | 1.41
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66945 | 121.72 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00305 | 104.2 | P23:500:AEPW-EES:ABF_HTBG-A | External | 103.4 | 0.8
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 114.76 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 114.56 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 404 | 484 | 0.00937 | 107.94 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 106.91 | 1.03
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 603020 MAPLE R7 115 997621 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00079 | 120.27 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997179 FA KV1A 115 1 652436 FARGO 7 115 997179 FA KV1A 115 1 652434 FARGOSVC 13.2 997179 FA KV1A 115 1 652435 FARGO 4 230 997178 FA KV2A 115 2 652436 FARGO 7 115 997178 FA KV2A 115 2 652434 FARGOSVC 13.2 997178 FA KV2A 115 2 | External | 119.84 | 0.43
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 115 | 115 | 0.00025 | 104.61 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 104.51 | 0.1
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00049 | 103.45 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 103.37 | 0.08
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 248 | 263 | 0.03697 | 100.17 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04199 | 125.28 | P12:345:OKGE:BKRBKR24 | Internal | 110.23 | 15.05
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 114.43 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 114.23 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 171 | 185 | 0.06275 | 103.99 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50869 | 111.42 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 114.76 | P13:161-69:EES-EAI:HERGET:AT1 | External | 114.56 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 139.69 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 137.93 | 1.76
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 114.43 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 114.23 | 0.2
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 139.69 | 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1: 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1 | External | 137.94 | 1.75
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50026 | 116.91 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66722 | 122.74 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.00144 | 103.18 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 102.09 | 1.09
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336154 6WATFRD% 230 336250 69MILE% 230 1 | 1038 | 1038 | 0.00271 | 121.28 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 121.14 | 0.14
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00027 | 221.04 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 220.95 | 0.09
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00108 | 121.31 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 121.07 | 0.24
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00399 | 103.43 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00576 | 139.69 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 137.93 | 1.76
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48196 | 123.3 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06392 | 129.19 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal | 113.85 | 15.34
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00108 | 113.51 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 113.28 | 0.23
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 142 | 158 | 0.05627 | 100.75 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66945 | 122.95 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 335378 4SCOTT_2! 138 502404 BONIN 4 138 1 | 225 | 225 | 6e-05 | 114.97 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 114.96 | 0.01
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67464 | 128.77 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 404 | 470 | 0.00937 | 104.62 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 103.49 | 1.13
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00081 | 125.38 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 125.23 | 0.15
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 336224 3AMCYAN! 115 336280 39MILE% 115 1 | 159 | 159 | 0.0004 | 102.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.99 | 0.11
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 504124 ASHDWN_W 4 138 510890 CRAIGJT4 138 1 | 287 | 287 | 0.04537 | 100.51 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1 | Internal
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 143 | 143 | 0.04434 | 134.95 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal | 115.63 | 19.32
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00077 | 101.62 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.57 | 0.05
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 500220 COOPER 4 138 500480 LEESV 4 138 1 | 268 | 287 | 0.00205 | 101.54 | P23:500:AEPW-EES:ABF_HTBG-A | External | 101.16 | 0.38
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 334045 4FISHCRK 138 334087 4PONDEROSA% 138 1 | 112 | 112 | 0.00576 | 120.61 | 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1: 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1 | External | 118.86 | 1.75
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00042 | 164.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 164.5 | 0.27
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.5084 | 114.34 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67133 | 120.33 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 337950 3JAXNVLE.N! 115 338016 3HOLND BTM! 115 1 | 266 | 266 | 0.0155 | 100.6 | P23:500:EES-EAI:KEO:B4921 | External
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.0037 | 105.24 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 100.1 | 5.14
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00359 | 104.67 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50133 | 122.66 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.5084 | 111.42 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50131 | 122.62 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66898 | 123.14 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00359 | 104.67 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.0015 | 112.66 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 112.05 | 0.61
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50131 | 122.62 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00132 | 101.13 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 100.14 | 0.99
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.6675 | 124.56 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67133 | 123.46 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67745 | 128.66 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67133 | 122.33 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50133 | 110.73 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00043 | 105.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.05 | 0.24
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50869 | 114.33 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 3e-05 | 148.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 148.61 | 0.21
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300101 5MORGAN 161 300045 7MORGAN 345 2 | 400 | 400 | 0.00481 | 100.19 | P42:345:SPRM-AECI:STUCK BKR SIM17 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.0022 | 102.77 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1: 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | External | 101.64 | 1.13
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00386 | 126.27 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 120.75 | 5.52
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00835 | 112.81 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 111.08 | 1.73
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00376 | 125.25 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 120.83 | 4.42
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00037 | 109.37 | P12:138:GRDA:CLEVLND-COLLINS | External | 109 | 0.37
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 125.38 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 125.22 | 0.16
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00042 | 100.93 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 100.94 | -0.01
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00014 | 103.25 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 103.18 | 0.07
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00037 | 108.98 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 512705 COLLINS4 138 998340 COLAUTO3 138 1 | External | 108.62 | 0.36
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 109.56 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 109.56 | 0
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.0002 | 144.02 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 143.98 | 0.04
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.0002 | 124.22 | P23:500:EES-EAI:WH_BLF:B7914 | External | 124.03 | 0.19
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00739 | 101.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 101.07 | 0.41
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300101 5MORGAN 161 300045 7MORGAN 345 2 | 400 | 400 | 0.00481 | 100.19 | P52:345:SPRM-AECI:STUCK BKR SIM17 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00079 | 106.86 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 106.6 | 0.26
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00835 | 105.44 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 103.61 | 1.83
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00825 | 107.83 | 65119: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External | 106.04 | 1.79
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300763 2WASHBRN 69.0 300129 5WASHBRN 161 1 | 56 | 56 | 0.00104 | 105.38 | P12:161:SWPA:BEAVER-EUREKA SPRINGS::506932 | External | 103.96 | 1.42
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00015 | 102.92 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.02 | -0.1
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00376 | 125.25 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 120.83 | 4.42
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0006 | 108.62 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.47 | 0.15
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00925 | 111.9 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 109.72 | 2.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00835 | 121.62 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 119.89 | 1.73
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00037 | 109.37 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 109 | 0.37
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00325 | 106.85 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 106.34 | 0.51
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.0002 | 100.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.08 | 0.17
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 1 | 101.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300618 2BARNET 69.0 300057 5BARNET 161 1 | 56 | 56 | 0.00048 | 107.54 | 300063 5CALIF 161 344233 5CALIF UE 161 1: 300063 5CALIF 161 344233 5CALIF UE 161 1 | External | 107.19 | 0.35
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.0002 | 105.67 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.49 | 0.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00507 | 100.84 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300763 2WASHBRN 69.0 300129 5WASHBRN 161 1 | 56 | 56 | 0.00104 | 105.04 | P12:161:SWPA-AEPW:BEAVER5:EUREKA5 | External | 104.61 | 0.43
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.0029 | 100.08 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00507 | 100.84 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00015 | 102.92 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 103.02 | -0.1
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00079 | 106.86 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 106.6 | 0.26
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48118 | 120.13 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00835 | 130.64 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 128.9 | 1.74
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.0002 | 113.6 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 113.55 | 0.05
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997057 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 113.01 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 113 | 0.01
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300101 5MORGAN 161 300045 7MORGAN 345 2 | 400 | 400 | 0.00481 | 100.19 | P22:345:SPRM-AECI:17 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00132 | 103.55 | P12:HV:EES::69MILE%:6NAPOL:1 | External | 103.53 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48115 | 120.09 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.0029 | 100.08 | 500190 COCODR 6 230 500880 VILPLT 6 230 1: 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00878 | 103.92 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 102.05 | 1.87
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00068 | 112.13 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 112.08 | 0.05
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00507 | 100.84 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 0.0008 | 103.59 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 103.41 | 0.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 125.38 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 125.22 | 0.16
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 125.02 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 124.85 | 0.17
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 125.02 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 124.85 | 0.17
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00232 | 100.29 | 300070 5CLARK 161 300794 5LAMAR 161 1: 300070 5CLARK 161 300794 5LAMAR 161 1 | External
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00878 | 111.22 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 109.44 | 1.78
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00068 | 111.01 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.95 | 0.06
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 109.56 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 109.56 | 0
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00925 | 103.47 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 101.25 | 2.22
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.0022 | 103.03 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | External | 101.9 | 1.13
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00043 | 125.38 | P13:161-69:EES-EAI:HERGET:AT1 | External | 125.22 | 0.16
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00043 | 110.35 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 110.25 | 0.1
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00878 | 120 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 118.23 | 1.77
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300618 2BARNET 69.0 300057 5BARNET 161 1 | 56 | 56 | 0.00048 | 107.54 | 300550 2CALIF 69 300063 5CALIF 161 1: 300550 2CALIF 69.0 300063 5CALIF 161 1 | External | 107.2 | 0.34
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00132 | 103.55 | 336250 69MILE% 230 336428 6NAPOL 230 1: 336250 69MILE% 230 336428 6NAPOL 230 1 | External | 103.53 | 0.02
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00014 | 135.62 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 135.61 | 0.01
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.0022 | 103.03 | 338108 5ST JOE 161 338110 5HILLTOP% 161 1: 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | External | 101.9 | 1.13
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00823 | 108.31 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 106.54 | 1.77
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.001 | 137.27 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 135.62 | 1.65
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00043 | 125.02 | P13:161-69:EES-EAI:HERGET:AT2 | External | 124.85 | 0.17
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 2e-05 | 110.15 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 110.14 | 0.01
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00124 | 113.66 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 113.34 | 0.32
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00099 | 125.5 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 125.17 | 0.33
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48115 | 120.09 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00878 | 128.84 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 127.07 | 1.77
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00015 | 102.92 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.02 | -0.1
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300763 2WASHBRN 69.0 300129 5WASHBRN 161 1 | 56 | 56 | 0.00104 | 105.07 | 93218: 338099 5GRANDVIEW% 161 506932 EUREKA 5 161 1 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | External | 104.63 | 0.44
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0006 | 108.62 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.47 | 0.15
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 1 | 101.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00075 | 111.51 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 111.33 | 0.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 0.0008 | 103.59 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 103.41 | 0.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66991 | 101.59 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00068 | 107.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.04 | 0.06
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00099 | 115.96 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 115.63 | 0.33
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00033 | 167.54 | P23:500:EES-EAI:WH_BLF:B7914 | External | 167.28 | 0.26
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50133 | 110.68 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50131 | 110.64 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 337950 3JAXNVLE.N! 115 338016 3HOLND BTM! 115 1 | 266 | 266 | 0.01509 | 103.67 | P23:500:EES-EAI:KEO:B4921 | External | 100.06 | 3.61
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03135 | 104.47 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 200 | 234 | 0.03561 | 101.68 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04359 | 106.49 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03561 | 104.41 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49584 | 119.1 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50131 | 110.64 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03849 | 112.48 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50344 | 115.85 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03355 | 117.06 | 83954: 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 524043 NICHOLS 3 115 524021 NICHOLS_1 1 13.8 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 111.44 | 5.62
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03355 | 108.35 | 83940: 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 102.32 | 6.03
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66511 | 108.17 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.03355 | 116.99 | 83956: 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | Internal | 111.37 | 5.62
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66752 | 109.12 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0001 | 125.48 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 125.32 | 0.16
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 | 222 | 0.10186 | 110.98 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00142 | 111.3 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 110.7 | 0.6
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50378 | 115.79 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04105 | 102.27 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03561 | 116.5 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 106.49 | 10.01
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06242 | 103.14 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.04359 | 104.66 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06242 | 112.12 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66752 | 106.11 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 520814 ANADARK4 138 521031 POCASET4 138 1 | 200 | 234 | 0.03135 | 101.34 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66367 | 109.32 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04266 | 121.24 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 100.7 | 20.54
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 109.3 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.07 | 0.23
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06242 | 116.57 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 | 194 | 222 | 0.10186 | 103.7 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04266 | 121.24 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 100.7 | 20.54
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 191 | 191 | 0.03849 | 112.48 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06242 | 106.95 | P42:345:OKGE:SB_JOCO7383 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0001 | 125.48 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 125.32 | 0.16
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0306 | 108.34 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 102.03 | 6.31
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67326 | 113.55 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.0001 | 125.48 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 125.32 | 0.16
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 521031 POCASET4 138 521072 TUTLETP4 138 1 | 200 | 234 | 0.03561 | 110.34 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 101.33 | 9.01
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66752 | 108 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06242 | 120.47 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48055 | 112.35 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50131 | 110.7 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50131 | 110.7 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50344 | 110.4 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 | 194 | 222 | 0.10186 | 106.02 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04266 | 105.69 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 4e-05 | 145.58 | P23:500:EES-EAI:WH_BLF:B7914 | External | 145.32 | 0.26
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50344 | 110.16 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00385 | 123.03 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 118.34 | 4.69
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00856 | 107.74 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 105.99 | 1.75
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 2e-05 | 114.35 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.35 | 0
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00374 | 122.8 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.15 | 4.65
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 108.27 | P12:138:GRDA:CLEVLND-COLLINS | External | 107.93 | 0.34
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00041 | 127.62 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 127.44 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 107.04 | 92115: 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300165 4SFORKK 138 301339 4SFORKKTP 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 512705 COLLINS4 138 1 512705 COLLINS4 138 998343 COLAUTO3 138 1 512705 COLLINS4 138 998340 COLAUTO3 138 1 | External | 107.55 | -0.51
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00058 | 104.32 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 104.3 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 112 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 111.98 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00021 | 139.67 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 139.63 | 0.04
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00021 | 121.43 | P23:500:EES-EAI:WH_BLF:B7914 | External | 121.21 | 0.22
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 112 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 111.98 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00781 | 104.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 104.03 | 0.41
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335455 4CHAMPAGNE! 138 500720 PLAISAN4 138 1 | 268 | 287 | 0.00332 | 104.3 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 103.67 | 0.63
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00058 | 105.08 | Base Case | External | 105.06 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.0008 | 106.48 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 106.22 | 0.26
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50378 | 110.34 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00296 | 107.27 | P12:230:CLEC:COCODR1:VLPLAT:1 | External | 106.77 | 0.5
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635003 SUB701 5 161 635005 SUB702 5 161 1 | 335 | 339 | 0.00856 | 100.93 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00017 | 103.41 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.54 | -0.13
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0006 | 109.24 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.08 | 0.16
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00962 | 103.61 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External | 101.37 | 2.24
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00856 | 115.61 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 113.85 | 1.76
Thermal | 07ALL | S1 | 24L0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48798 | 110.82 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.65913 | 107.17 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 233 | 233 | 0.00078 | 102.07 | 80252: 500773 SEGURA 6 230 500776 SELLRD6 230 1 500774 SEGURA4 138 500773 SEGURA 6 230 1 335388 4MORIL! 138 500774 SEGURA4 138 1 335413 4YOUNGSVIL% 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External | 101.9 | 0.17
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00332 | 113.99 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 113.43 | 0.56
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300618 2BARNET 69.0 300057 5BARNET 161 1 | 56 | 56 | 0.0005 | 104.27 | 300063 5CALIF 161 344233 5CALIF UE 161 1: 300063 5CALIF 161 344233 5CALIF UE 161 1 | External | 103.59 | 0.68
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997058 GLENHAM TR1 115 1 | 25 | 31 | 0.00023 | 105.1 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 105.08 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00484 | 100.72 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00296 | 107.27 | P12:230:CLEC::COCODR 6:VILPLT 6:1 | External | 106.77 | 0.5
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.0008 | 106.48 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 106.22 | 0.26
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00018 | 104.65 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 104.47 | 0.18
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48468 | 110.77 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00018 | 104.55 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 104.37 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00139 | 144.05 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 143.38 | 0.67
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00856 | 124.64 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | External | 122.88 | 1.76
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 2e-05 | 114.35 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.35 | 0
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66257 | 105.01 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.0002 | 111.66 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 111.61 | 0.05
Thermal | 00NR | S2 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.50378 | 110.1 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00134 | 100.39 | P12:HV:EES::69MILE%:6NAPOL:1 | External | 100.29 | 0.1
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335390 4BAYOU_WHSE! 138 1 | 112 | 112 | 0.00139 | 124.13 | 80171: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 | External | 123.49 | 0.64
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48465 | 110.74 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00484 | 100.72 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 0.00031 | 108.27 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 107.93 | 0.34
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00069 | 111.34 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.28 | 0.06
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00484 | 100.72 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00021 | 103.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 103.04 | 0.21
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00041 | 127.62 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 127.44 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00041 | 127.26 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 127.08 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 0.00081 | 104.53 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 104.33 | 0.2
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00018 | 104.55 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 104.37 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00069 | 110.23 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.18 | 0.05
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0006 | 109.24 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.08 | 0.16
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00041 | 127.26 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 127.08 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00225 | 100.44 | 300070 5CLARK 161 300794 5LAMAR 161 1: 300070 5CLARK 161 300794 5LAMAR 161 1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635005 SUB702 5 161 635010 MANAWA 5 161 1 | 335 | 360 | 0.00903 | 106.03 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 104.23 | 1.8
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00058 | 104.59 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 104.58 | 0.01
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336500 3NATCHEZSES% 115 337327 3RED_GUM! 115 1 | 87 | 87 | 0.00141 | 103.82 | P12:HV:EES::3PLANTATION!:3VIDALIA_LA:1 | External | 102.8 | 1.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66257 | 106.02 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48118 | 105.3 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00041 | 127.62 | P13:161-69:EES-EAI:HERGET:AT1 | External | 127.44 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00044 | 114.32 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 114.22 | 0.1
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00058 | 104.32 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 104.3 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48118 | 108.36 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635010 MANAWA 5 161 635011 INDNCRK5 161 1 | 360 | 360 | 0.00903 | 113.87 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 112.06 | 1.81
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300618 2BARNET 69.0 300057 5BARNET 161 1 | 56 | 56 | 0.0005 | 104.27 | 300550 2CALIF 69 300063 5CALIF 161 1: 300550 2CALIF 69.0 300063 5CALIF 161 1 | External | 103.59 | 0.68
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00134 | 100.39 | 336250 69MILE% 230 336428 6NAPOL 230 1: 336250 69MILE% 230 336428 6NAPOL 230 1 | External | 100.29 | 0.1
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00014 | 130.39 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 130.37 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00852 | 101.53 | 83252: 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335389 4DUBOIN! 138 335394 4MORILSPLT! 138 1 | 112 | 112 | 0.00139 | 100.06 | 80248: 335394 4MORILSPLT! 138 500410 HOPKINS4 138 1 500410 HOPKINS4 138 500580 MORBHAN4 138 1 500410 HOPKINS4 138 500660 PATOUT 4 138 1 500410 HOPKINS4 138 500774 SEGURA4 138 1 | External
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00018 | 104.65 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 104.47 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00103 | 139.4 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 137.69 | 1.71
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00041 | 127.26 | P13:161-69:EES-EAI:HERGET:AT2 | External | 127.08 | 0.18
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 3e-05 | 112.63 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 112.61 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66086 | 105.9 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00118 | 110.5 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 109.95 | 0.55
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00061 | 101.78 | Base Case | External | 101.76 | 0.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00101 | 123.4 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 123.06 | 0.34
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48115 | 105.26 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 336500 3NATCHEZSES% 115 337327 3RED_GUM! 115 1 | 87 | 87 | 0.00141 | 103.82 | 337320 3PLANTATION! 115 337321 3VIDALIA_LA 115 1: 337320 3PLANTATION! 115 337321 3VIDALIA_LA 115 1 | External | 102.8 | 1.02
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00903 | 122.75 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | External | 120.94 | 1.81
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00017 | 103.41 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.54 | -0.13
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 0.00017 | 103.41 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 103.54 | -0.13
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66257 | 107.03 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00374 | 122.8 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 118.15 | 4.65
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1058 | 1195 | 0.66658 | 110.89 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00077 | 108.24 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 108.08 | 0.16
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 0.00081 | 104.53 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 104.33 | 0.2
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 635001 CBLUFFS5 161 635011 INDNCRK5 161 1 | 371 | 371 | 0.00849 | 102.06 | 82314: 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 | External | 100.24 | 1.82
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00069 | 106.37 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.32 | 0.05
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00101 | 114.36 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 114.03 | 0.33
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00029 | 137.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.28 | 0.31
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.0446 | 110.02 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 103.12 | 6.9
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.05867 | 131.27 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 118.35 | 12.92
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00396 | 103.45 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00378 | 102.11 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06717 | 108.83 | P12:345:AEPW-WFEC:VALIANT7:HUGO7 | Internal
Thermal | 07ALL | S1 | 29SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48465 | 110.74 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04574 | 105.55 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03362 | 117.92 | 809751: 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 113.29 | 4.63
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66769 | 118.93 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06535 | 102.74 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.05141 | 119.98 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal | 110.89 | 9.09
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06535 | 102.74 | P23:345:AEPW:VALLIANT CB 3413A NBTB | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.0606 | 132.69 | P42:345:OKGE:SB_CION7384 | Internal | 118.68 | 14.01
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00026 | 108.52 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 108.47 | 0.05
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66954 | 115 | P42:345:OKGE:SB_MICO7312 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.04574 | 110.97 | P42:345:OKGE:SB_CION7384 | Internal | 103.64 | 7.33
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 133 | 153 | 0.06334 | 100.53 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04119 | 135.88 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 120.25 | 15.63
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.06028 | 124.61 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal | 111.53 | 13.08
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | 77.2 | 95.6 | 0.00011 | 104.43 | 345222 2MOBERLY 69 345221 5MOBERLY 161 2: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | External | 104.39 | 0.04
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67394 | 122.91 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04119 | 135.88 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | Internal | 120.25 | 15.63
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 200 | 234 | 0.0606 | 123.3 | P42:345:OKGE:SB_MICO7312 | Internal | 109.85 | 13.45
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66954 | 117.47 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 133 | 153 | 0.06334 | 102.17 | P42:345:OKGE:SB_JOCO7303 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 345222 2MOBERLY 69.0 345221 5MOBERLY 161 2 | 78 | 95.6 | 0.00011 | 104.35 | 345222 2MOBERLY 69 345221 5MOBERLY 161 1: 345222 2MOBERLY 69.0 345221 5MOBERLY 161 1 | External | 104.31 | 0.04
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.02578 | 107.47 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 56 | 56 | 0.00383 | 102.78 | 104917: 512710 KINZEGR4 138 515008 KINZE 4 138 1 | External
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 117 | 136 | 0.04119 | 122.94 | 817230: 510907 PITTSB-7 345 510911 VALIANT7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | Internal | 105.23 | 17.71
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66954 | 117.83 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03362 | 117.92 | 809753: 514801 MINCO 7 345 589054 G17-067-TAP 345 1 511468 L.E.S.-7 345 587744 G16-091-TAP 345 1 | Internal | 113.19 | 4.73
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66587 | 118.89 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 1e-05 | 152.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 152.28 | 0.22
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48115 | 108.32 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00393 | 109 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 104.45 | 4.55
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00382 | 108.65 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 104.27 | 4.38
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 127.94 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 127.77 | 0.17
Thermal | 07ALL | S1 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5084 | 109.88 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00022 | 131.91 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 131.87 | 0.04
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.0002 | 103.03 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.85 | 0.18
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00985 | 115.87 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 115.33 | 0.54
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48115 | 108.32 | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00086 | 104.3 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 104.08 | 0.22
Thermal | 07ALL | S1 | 24SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48115 | 105.26 | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.65983 | 122.35 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 603020 MAPLE R7 115 997619 MAPLE RIVER 69.0 1 | 129 | 140 | 0.0007 | 128.77 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997179 FA KV1A 115 1 652436 FARGO 7 115 997179 FA KV1A 115 1 652434 FARGOSVC 13.2 997179 FA KV1A 115 1 652435 FARGO 4 230 997178 FA KV2A 115 2 652436 FARGO 7 115 997178 FA KV2A 115 2 652434 FARGOSVC 13.2 997178 FA KV2A 115 2 | External | 128.85 | -0.08
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997058 GLENHAM TR1 115 1 | 25 | 31 | 0.00035 | 113 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 112.98 | 0.02
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00086 | 104.3 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 104.08 | 0.22
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 127.94 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 127.77 | 0.17
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00013 | 109.84 | Base Case | External | 109.68 | 0.16
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 104.28 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 104.09 | 0.19
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.6635 | 119.19 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 335361 4CANKTON% 138 335452 4BLOOMFLD% 138 1 | 225 | 225 | 0.00021 | 105.1 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 105.06 | 0.04
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00985 | 135.63 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 135.16 | 0.47
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335 | 360 | 0.00353 | 103.2 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 500940 WELLS 6 230 502421 LABBE 230 1 | External | 102.71 | 0.49
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00074 | 108.49 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 108.43 | 0.06
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48691 | 109.42 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 127.57 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 127.4 | 0.17
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00074 | 107.42 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 107.36 | 0.06
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 127.57 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 127.4 | 0.17
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 336500 3NATCHEZSES% 115 337327 3RED_GUM! 115 1 | 87 | 87 | 0.0015 | 107.61 | P12:HV:EES::3PLANTATION!:3VIDALIA_LA:1 | External | 106.66 | 0.95
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.6635 | 120.25 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49584 | 104.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00015 | 118.65 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.64 | 0.01
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998893 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 127.94 | P13:161-69:EES-EAI:HERGET:AT1 | External | 127.77 | 0.17
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00047 | 105.42 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 105.32 | 0.1
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00098 | 114.22 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 112.93 | 1.29
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998892 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 127.57 | P13:161-69:EES-EAI:HERGET:AT2 | External | 127.4 | 0.17
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49584 | 107.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66156 | 121.01 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.00137 | 100.66 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48658 | 109.41 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00109 | 118.69 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 118.37 | 0.32
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00382 | 108.65 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 104.27 | 4.38
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 104.28 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 104.09 | 0.19
Thermal | 07NR | S2 | 24L0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49738 | 107.73 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 336500 3NATCHEZSES% 115 337327 3RED_GUM! 115 1 | 87 | 87 | 0.0015 | 107.61 | 337320 3PLANTATION! 115 337321 3VIDALIA_LA 115 1: 337320 3PLANTATION! 115 337321 3VIDALIA_LA 115 1 | External | 106.66 | 0.95
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.6635 | 121.56 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66715 | 126.55 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 337312 3JENA 115 337340 3STANDARD! 115 1 | 95 | 95 | 0.00082 | 106.35 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 106.19 | 0.16
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00074 | 103.71 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 103.66 | 0.05
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00109 | 111.17 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 110.85 | 0.32
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00023 | 157.73 | P23:500:EES-EAI:WH_BLF:B7914 | External | 157.47 | 0.26
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48691 | 103.93 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00393 | 105.46 | 104916: 514827 CTNWOOD4 138 514829 PINE ST4 138 1 515008 KINZE 4 138 515181 UNVRSTY4 138 1 514829 PINE ST4 138 514830 FITZGRD4 138 1 515009 MCELROY4 138 515181 UNVRSTY4 138 1 514830 FITZGRD4 138 515008 KINZE 4 138 1 | External | 100.99 | 4.47
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00383 | 104.89 | 81807: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 100.69 | 4.2
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 603020 MAPLE R7 115 997622 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00068 | 121.64 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 997179 FA KV1A 115 1 652436 FARGO 7 115 997179 FA KV1A 115 1 652434 FARGOSVC 13.2 997179 FA KV1A 115 1 652435 FARGO 4 230 997178 FA KV2A 115 2 652436 FARGO 7 115 997178 FA KV2A 115 2 652434 FARGOSVC 13.2 997178 FA KV2A 115 2 | External | 121.54 | 0.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 608673 ARROWHD7 115 608688 COLBYVL7 115 1 | 126 | 126 | 0.00027 | 101.04 | 608673 ARROWHD7 115 608674 HANESRD7 115 1: 608673 ARROWHD7 115 608674 HANESRD7 115 1 | External | 100.92 | 0.12
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336220 3GYPSY% 115 336223 3LULING! 115 1 | 290 | 290 | 0.00039 | 168.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 168.45 | 0.08
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00032 | 110.31 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.08 | 0.23
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 335378 4SCOTT_2! 138 502404 BONIN 4 138 1 | 225 | 225 | 6e-05 | 116.46 | 80256: 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 1 303014 4BAYOU_COVE% 138 335366 4RICHARD% 138 2 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 335366 4RICHARD% 138 335369 4ACADIA% 138 3 335366 4RICHARD% 138 335369 4ACADIA% 138 4 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 335366 4RICHARD% 138 500300 EUNICE 4 138 1 335366 4RICHARD% 138 500400 HABETZ 4 138 1 335367 8RICHARD% 500 335366 4RICHARD% 138 1 | External | 116.44 | 0.02
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 109.66 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 109.32 | 0.34
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48658 | 103.92 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 337926 5QUITMAN! 161 337940 5HAMLET% 161 1 | 223 | 223 | 0.00575 | 101.82 | 337919 5BONO 161 337923 5P.HILL% 161 1: 337919 5BONO 161 337923 5P.HILL% 161 1 | External | 100.43 | 1.39
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 120.3 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 338351 2JB HERGETT! 69.0 998886 HGT X2 69.0 1 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 338374 1HGT X2 13.8 998886 HGT X2 69.0 1 | External | 120.12 | 0.18
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 119.96 | P13:161-69:EES-EAI:HERGET:AT2 | External | 119.77 | 0.19
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 120.3 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 120.12 | 0.18
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00079 | 102.23 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1: 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | External | 102.03 | 0.2
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66855 | 125.59 | P42:345:OKGE:SB_CION7384 | Internal
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48691 | 103.99 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66475 | 128.21 | 81384: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514801 MINCO 7 345 514901 CIMARON7 345 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336224 3AMCYAN! 115 1 | 174 | 174 | 0.00038 | 106.92 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.82 | 0.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.0001 | 104.45 | Base Case | External | 104.3 | 0.15
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 119.96 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 119.77 | 0.19
Thermal | 00NR | S2 | 24SP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48658 | 103.99 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 115 | 115 | 0.00023 | 100.82 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 100.74 | 0.08
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00079 | 102.23 | P12:HV:EES::4CLVELND!:4JACINTO%:1 | External | 102.03 | 0.2
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.0074 | 128.72 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 128.46 | 0.26
Thermal | 07ALL | S1 | 20SP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50029 | 107.19 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 159 | 159 | 0.0249 | 100.28 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1 | External
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00549 | 115.61 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 113.51 | 2.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66855 | 124.44 | P42:345:OKGE:SB_MICO7301 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00549 | 107.16 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 105.08 | 2.08
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336223 3LULING! 115 336225 3WAGGMN 115 1 | 174 | 174 | 0.00047 | 121.96 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 121.84 | 0.12
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 335569 6ST_GABRIEL% 230 335573 6AAC_CORP 230 1 | 685 | 685 | 0.00073 | 111.02 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.97 | 0.05
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.49975 | 105.17 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00549 | 115.61 | P13:230-138:EES:ND:6PONDEROSA!:1 | External | 113.51 | 2.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334044 4DOBBIN% 138 334046 4SPRINGBRNCH 138 1 | 112 | 112 | 0.00549 | 115.61 | 334088 6PONDEROSA! 230 3WXFMR 6PONDEROSA! 1: 334088 6PONDEROSA! 230 998907 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998907 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998907 6PONDEROSA! 138 1 334088 6PONDEROSA! 230 998902 6PONDEROSA! 138 1 334087 4PONDEROSA% 138 998902 6PONDEROSA! 138 1 334094 1PONDEROSA 13.8 998902 6PONDEROSA! 138 1 | External | 113.51 | 2.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 335573 6AAC_CORP 230 335574 6LICAR% 230 1 | 685 | 685 | 0.00073 | 109.94 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 109.89 | 0.05
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336225 3WAGGMN 115 336280 39MILE% 115 1 | 174 | 174 | 0.00047 | 115.81 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 115.69 | 0.12
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 661035 GLENHAM7 115 997064 GLENHAM TR1 115 1 | 25 | 31 | 0.00035 | 105.17 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 661038 GLENHAM4 230 997062 GLENHAM TR2 115 2 661035 GLENHAM7 115 997062 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997062 GLENHAM TR2 115 2 | External | 105.15 | 0.02
Thermal | 00NR | S2 | 19WP0 | G07_G077&G085 | FROM -> TO | 515800 GRACMNT7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.49975 | 100.29 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 337926 5QUITMAN! 161 337940 5HAMLET% 161 1 | 223 | 223 | 0.00575 | 101.82 | P12:HV:EES::5BONO:5P.HILL%:1 | External | 100.43 | 1.39
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336196 6LABARE! 230 336198 6SPORT% 230 1 | 641 | 641 | 0.00014 | 120.51 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.5 | 0.01
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | 241 | 241 | 0.00046 | 100.22 | 80253: 335381 6MEAUX! 230 500776 SELLRD6 230 1 500765 RORK 6 230 500776 SELLRD6 230 1 500773 SEGURA 6 230 500776 SELLRD6 230 1 500776 SELLRD6 230 502421 LABBE 230 1 | External | 100.13 | 0.09
Thermal | 07ALL | S1 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 589054 G17-067-TAP 345 1 | 1195 | 1195 | 0.48055 | 100.85 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00139 | 100.26 | 336250 69MILE% 230 336428 6NAPOL 230 1: 336250 69MILE% 230 336428 6NAPOL 230 1 | External | 100.16 | 0.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00549 | 107.16 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1 | External | 105.08 | 2.08
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334046 4SPRINGBRNCH 138 334048 4DEERLAKE 138 1 | 112 | 112 | 0.00549 | 107.2 | 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1: 334038 6DOBBIN% 230 334088 6PONDEROSA! 230 1 | External | 105.11 | 2.09
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66637 | 126.39 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998888 HGT X1 69.0 1 | 100 | 112 | 0.00049 | 120.3 | P13:161-69:EES-EAI:HERGET:AT1 | External | 120.12 | 0.18
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336154 6WATFRD% 230 336250 69MILE% 230 1 | 1038 | 1038 | 0.00257 | 116.62 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 116.49 | 0.13
Thermal | 00NR | S2 | 24WP0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.48196 | 102.26 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334072 4LEWIS% 138 334078 4SHEAWIL 138 1 | 145 | 145 | 0.00103 | 116.84 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 116.55 | 0.29
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 300856 2LUTHER 69.0 300135 4LUTHER 138 1 | 64 | 64 | 0.00383 | 104.89 | 92109: 512710 KINZEGR4 138 512712 19TH ST4 138 1 512710 KINZEGR4 138 512731 NORTHTP4 138 1 512710 KINZEGR4 138 515008 KINZE 4 138 1 512710 KINZEGR4 138 512713 KINZEGR2 69.0 1 | External | 100.69 | 4.2
Thermal | 07NR | S2 | 20G0 | G07_G077&G085 | FROM -> TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.50133 | 101.12 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.66855 | 127.44 | P12:345:OKGE:BKRBKR24 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 336250 69MILE% 230 336432 6DERBI! 230 1 | 757 | 757 | 0.00139 | 100.26 | P12:HV:EES::69MILE%:6NAPOL:1 | External | 100.16 | 0.1
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 97000 POI 345 515136 SUNNYSD7 345 1 | 1195 | 1195 | 0.67355 | 133.35 | 81726: 514901 CIMARON7 345 514934 DRAPER 7 345 1 514820 JENSENT4 138 514898 CIMARON4 138 1 514895 SARA 4 138 514898 CIMARON4 138 1 511425 TUTCONT4 138 514898 CIMARON4 138 1 514801 MINCO 7 345 514901 CIMARON7 345 1 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Internal
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X2 69.0 1 | 100 | 112 | 0.00049 | 119.96 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 338351 2JB HERGETT! 69.0 998887 HGT X1 69.0 1 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 338373 1HGT X1 13.8 998887 HGT X1 69.0 1 | External | 119.77 | 0.19
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 335574 6LICAR% 230 335575 6BELL_HEL! 230 1 | 685 | 685 | 0.00073 | 106.2 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.15 | 0.05
Thermal | 07ALL | S1 | 19WP0 | G07_G077&G085 | FROM -> TO | 334078 4SHEAWIL 138 334079 4FWPIPE 138 1 | 145 | 145 | 0.00103 | 109.13 | 67906: 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 334084 4CLVELND! 138 334208 4JACINTO% 138 1 334100 4PORTER% 138 334117 4APOLLO! 138 1 334100 4PORTER% 138 334111 4NEWCANY! 138 1 334100 4PORTER% 138 334117 4APOLLO 138 1 | External | 108.85 | 0.28
Non-Converge | 07ALL | S1 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.60393 | NConv | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07ALL | S1 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.60393 | NConv | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07ALL | S1 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.60393 | NConv | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07ALL | S1 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.60393 | NConv | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.0322 | NConv | P23:500:EES-EAI:INDEP2:B6126 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.03166 | NConv | P23:500:EES-EAI:WH_BLF:B7942 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | 84133: 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | 105459: 525824 TUCO_TR1 1 13.2 998067 UPDATE LATER 230 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | P23:345:AEPW:OKLAUNION CB 3409A NBTB | NA
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | 83857: 525853 LH-WIL&ELN+2 69.0 525860 SP-BECTON +2 69.0 1 511456 O.K.U.-7 345 525832 TUCO_INT 7 345 1 525826 TUCO_INT 2 69.0 525853 LH-WIL&ELN+2 69.0 1 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1 525780 FLOYD_CNTY 3 115 525828 TUCO_INT 3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | G07_G077&G085 |  | Non-Converge |  |  | 0.07169 | NConv | P23:345:AEPW:OKLAUNION CB 3401A NBTB | NA
Non-Converge | 07NR | S2 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.61057 | NConv | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07NR | S2 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.61057 | NConv | 81383: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07NR | S2 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.61057 | NConv | 94450: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 | NA
Non-Converge | 07NR | S2 | 24L0 | G07_G077&G085 |  | Non-Converge |  |  | 0.61057 | NConv | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1 | NA

## All Voltage
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | MONITORED ELEMENT | BC Voltage (PU) | TC Voltage (PU) | Voltage Differ (PU) | VINIT (PU) | VMIN (PU) | VMAX(PU) | TDF | CONTINGENCY
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | V-WEYCO4 | >0.94 | 0.9158 | >0.0242 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | CRAIGJT4 | >0.94 | 0.9185 | >0.0215 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | B.BOW 4 | >0.94 | 0.9156 | >0.0244 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | DEQUEEN4 | 0.9388 | 0.9158 | 0.023 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | B.BOWTP4 | >0.94 | 0.9157 | >0.0243 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | IDABEL-4 | >0.94 | 0.9137 | >0.0263 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
ERIS | 07ALL | S1 | 24L0 | G07_G077&G085 | VALIANT4 | >0.94 | 0.9194 | >0.0206 | 138 | 0.92 | 1.05 | 0.15256 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | NORTONV2 | >0.95 | 0.9247 | >0.0253 | 69 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THST 3 | >0.95 | 0.9252 | >0.0248 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | FAIRGDS3 | >0.95 | 0.9259 | >0.0241 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KETCHEM7 | 0.9534 | 0.8963 | -0.0571 | 345 | 0.9 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | SWLWRNC3 | >0.95 | 0.9278 | >0.0222 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | OSBORN7 | 0.9535 | 0.8964 | -0.0571 | 345 | 0.9 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | TECHILL5 | 0.9661 | 0.9241 | -0.042 | 161 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | GEN-2016-088 | 0.9535 | 0.8964 | -0.0571 | 345 | 0.9 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | MOCKBRD3 | >0.95 | 0.9297 | >0.0203 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | KU CAMP3 | >0.95 | 0.9258 | >0.0242 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 19THSTJ3 | >0.95 | 0.9262 | >0.0238 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 29SP0 | G07_G077&G085 | 166TH 3 | >0.95 | 0.9262 | >0.0238 | 115 | 0.93 | 1.05 | 0.04395 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COALGTP4 | >0.94 | 0.9126 | >0.0274 | 138 | 0.92 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COALGTP4 | >0.94 | 0.9126 | >0.0274 | 138 | 0.92 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SUGDEN 2 | 0.9595 | 0.8973 | -0.0622 | 69 | 0.9 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ANTLERS2 | >0.94 | 0.9164 | >0.0236 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | V-WEYCO4 | 0.9258 | 0.8716 | 0.0542 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GORDON TAP 4 | 0.8992 | 0.843 | 0.0562 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ALUMAX 4 | 0.9256 | 0.8707 | 0.0549 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ATOKA--4 | 0.936 | 0.9063 | 0.0297 | 138 | 0.92 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ATOKA--4 | 0.936 | 0.9063 | 0.0297 | 138 | 0.92 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | USMOTOR2 | >0.94 | 0.8896 | >0.0504 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SUGHLET2 | 1.0342 | 0.9129 | -0.1213 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KIPUMPT2 | 0.9382 | 0.8845 | 0.0537 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REDRVR-2 | 1.0334 | 0.8973 | -0.1361 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DURANT 4 | 0.9013 | 0.8535 | 0.0478 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DURANT 4 | 0.9013 | 0.8535 | 0.0478 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBERT4 | 0.9066 | 0.8643 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBERT4 | 0.9066 | 0.8643 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HOOKS 2 | 1.0378 | 0.9075 | -0.1303 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SPECTRM4 | 0.9574 | 0.8968 | -0.0606 | 138 | 0.9 | 1.05 | 0.60821 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | CASSTP4 | 0.8863 | 0.8385 | 0.0478 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NWTXARK4 | 0.9334 | 0.8797 | 0.0537 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NWTXARK7 | >0.94 | 0.8934 | >0.0466 | 345 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BODLE 4 | 0.9108 | 0.8689 | 0.0419 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BODLE 4 | 0.9108 | 0.8689 | 0.0419 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WICKES 2 | >0.94 | 0.9075 | >0.0325 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ALAMANC2 | 0.8786 | 0.8282 | 0.0504 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | THAKRVL2 | 0.9196 | 0.8914 | 0.0282 | 69 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | THAKRVL2 | 0.9196 | 0.8914 | 0.0282 | 69 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | CRAIGJT4 | 0.9007 | 0.8452 | 0.0555 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BARITE-RD 4 | >0.94 | 0.9004 | >0.0396 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | EYLAU 4 | 0.9076 | 0.851 | 0.0566 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BUFORDR2 | 0.933 | 0.8993 | 0.0337 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SCOLEMN4 | 0.9082 | 0.8643 | 0.0439 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SCOLEMN4 | 0.9082 | 0.8643 | 0.0439 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SFOREMAN 4 | 0.9105 | 0.8551 | 0.0554 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TEX12ST2 | 1.0311 | 0.9064 | -0.1247 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NW_TEXAR 2 | 1.0354 | 0.9112 | -0.1242 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | RICHMND2 | 1.0355 | 0.9105 | -0.125 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | RODESSA2 | 0.9375 | 0.9043 | 0.0332 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | B.BOW 4 | 0.8994 | 0.842 | 0.0574 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BENNSUB4 | 0.9068 | 0.8586 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BENNSUB4 | 0.9068 | 0.8586 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IDABEL 4 | 0.9036 | 0.8459 | 0.0577 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ANDRCKT2 | 0.8972 | 0.8403 | 0.0569 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLEMNT4 | 0.9178 | 0.8764 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLEMNT4 | 0.9178 | 0.8764 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IPC TAP2 | 0.9379 | 0.8811 | 0.0568 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | W-RELIF2 | >0.94 | 0.9187 | >0.0213 | 69 | 0.92 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HOCHJCT4 | 0.9026 | 0.8466 | 0.056 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TXI4 | 0.9053 | 0.8629 | 0.0424 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TXI4 | 0.9053 | 0.8629 | 0.0424 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | EXPLRPL4 | 0.9169 | 0.8756 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | EXPLRPL4 | 0.9169 | 0.8756 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HOLYCRK4 | 0.9018 | 0.8443 | 0.0575 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TURK 7 | >0.94 | 0.8969 | >0.0431 | 345 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BIVINS 2 | 0.8778 | 0.8274 | 0.0504 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IPC-DOM4 | 0.8811 | 0.8237 | 0.0574 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MTRIVER4 | 0.9007 | 0.8451 | 0.0556 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NASH 4 | 0.9257 | 0.8707 | 0.055 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BROKNBW4 | 0.9014 | 0.8445 | 0.0569 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GRANNIS 2 | >0.94 | 0.9109 | >0.0291 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NEKOOSA2 | 0.9227 | 0.8654 | 0.0573 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBRT-4 | 0.907 | 0.8647 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBRT-4 | 0.907 | 0.8647 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ASHDWNR4 | >0.94 | 0.8963 | >0.0437 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NEWBOST2 | 1.0338 | 0.8916 | -0.1422 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BUCHANN4 | 0.907 | 0.8503 | 0.0567 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DARENCT2 | 0.8812 | 0.831 | 0.0502 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NWT-BNT4 | 0.9324 | 0.8784 | 0.054 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ASHDOWN2 | >0.94 | 0.9001 | >0.0399 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TEXOPER2 | 1.0361 | 0.9127 | -0.1234 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | FORMANR2 | >0.94 | 0.9184 | >0.0216 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ATLANTA2 | 0.9359 | 0.8894 | 0.0465 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BLOOMBG2 | 0.9258 | 0.8775 | 0.0483 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LTLCITY4 | >0.92 | 0.8903 | >0.0297 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LTLCITY4 | >0.92 | 0.8903 | >0.0297 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | W-LIFTP2 | >0.94 | 0.9191 | >0.0209 | 69 | 0.92 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COVEREC2 | >0.94 | 0.8977 | >0.0423 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SEAWAY4 | 0.9056 | 0.8633 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SEAWAY4 | 0.9056 | 0.8633 | 0.0423 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BENNGTN4 | 0.9073 | 0.8591 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BENNGTN4 | 0.9073 | 0.8591 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KI PMPN2 | 0.9379 | 0.8842 | 0.0537 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SIB REA1 | 0.9247 | 0.8993 | -0.0254 | 345 | 0.9 | 1.05 | 0.04123 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DOMINJCT4 | 0.9018 | 0.8455 | 0.0563 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TEX-PUP2 | >0.94 | 0.9198 | >0.0202 | 69 | 0.92 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SDEKALB2 | 0.8845 | 0.8265 | 0.058 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MAUDT 2 | 0.8934 | 0.8361 | 0.0573 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | PLEASHL2 | 1.0335 | 0.8981 | -0.1354 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NE-TEXARK2 | >0.94 | 0.8892 | >0.0508 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SCLMNJC4 | 0.9112 | 0.8675 | 0.0437 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SCLMNJC4 | 0.9112 | 0.8675 | 0.0437 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DEQUEEN4 | 0.8969 | 0.8426 | 0.0543 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DUGLASV2 | 0.8981 | 0.8492 | 0.0489 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ROACH 2 | 0.8818 | 0.8317 | 0.0501 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DUGLASV4 | 0.8828 | 0.836 | 0.0468 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IPC 4 | 0.867 | 0.8092 | 0.0578 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MENA 2 | >0.94 | 0.8915 | >0.0485 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SUGHLWT2 | 1.0355 | 0.9133 | -0.1222 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MINEOLA2 | <1.03 | 1.0514 | >0.0214 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | W CITY 2 | >0.94 | 0.8862 | >0.0538 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BUTRFLD4 | 0.9095 | 0.8674 | 0.0421 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BUTRFLD4 | 0.9095 | 0.8674 | 0.0421 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WATLANT4 | 0.8896 | 0.8433 | 0.0463 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HOCHTWN4 | 0.9105 | 0.8568 | 0.0537 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WATLANT2 | 1.0393 | 0.9013 | -0.138 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GARVIN4 | 0.91 | 0.8533 | 0.0567 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TECHILL6 | 0.9683 | 0.9459 | -0.0224 | 230 | 0.95 | 1.05 | 0.04123 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WASHST 2 | 1.0306 | 0.9045 | -0.1261 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | OKAY 4 | >0.94 | 0.9107 | >0.0293 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SAWYER 2 | 0.9397 | 0.8877 | 0.052 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SIMMS 2 | 0.894 | 0.8368 | 0.0572 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REDSPRG4 | 0.9085 | 0.852 | 0.0565 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DURANTP4 | 0.9026 | 0.855 | 0.0476 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DURANTP4 | 0.9026 | 0.855 | 0.0476 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SUGARHL2 | 1.0353 | 0.9139 | -0.1214 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SUGARHL4 | 0.9371 | 0.8821 | 0.055 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COOKVIL2 | 0.9392 | 0.9149 | 0.0243 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TEXARK 2 | 1.0347 | 0.9075 | -0.1272 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | 87TH 7 | 0.9576 | 0.924 | -0.0336 | 345 | 0.95 | 1.05 | 0.04123 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SDIERKS4 | >0.94 | 0.9011 | >0.0389 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NAPLES 2 | 0.9324 | 0.8987 | 0.0337 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | S BROWN4 | 0.9177 | 0.8763 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | S BROWN4 | 0.9177 | 0.8763 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MUNZCTY4 | 0.8879 | 0.8416 | 0.0463 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KRSYJCTS4 | 0.916 | 0.8745 | 0.0415 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KRSYJCTS4 | 0.916 | 0.8745 | 0.0415 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SNASHVL4 | >0.94 | 0.8991 | >0.0409 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GA PAC 2 | 0.93 | 0.8751 | 0.0549 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | S_TEXARK 2 | 1.0336 | 0.8984 | -0.1352 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | B.BOWTP4 | 0.8996 | 0.8423 | 0.0573 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TEX39ST2 | 1.0347 | 0.9123 | -0.1224 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | CHICKASAW2 | 0.9151 | 0.8868 | 0.0283 | 69 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | CHICKASAW2 | 0.9151 | 0.8868 | 0.0283 | 69 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | VALLANT4 | >0.92 | 0.8909 | >0.0291 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NLINDEN2 | 0.8872 | 0.8374 | 0.0498 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REDWATR4 | 0.9071 | 0.8504 | 0.0567 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REDWATR2 | 0.8935 | 0.8362 | 0.0573 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SIBLEY 7 | 0.9247 | 0.8993 | -0.0254 | 345 | 0.9 | 1.05 | 0.04123 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MENA 2 | >0.94 | 0.8914 | >0.0486 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MENA 4 | 0.8998 | 0.8438 | 0.056 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BRKN BW4 | 0.9154 | 0.863 | 0.0524 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | EOLA 2 | 0.9189 | 0.8841 | 0.0348 | 69 | 0.9 | 1.05 | 0.60821 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | JIMTOWN2 | 0.9603 | 0.8976 | -0.0627 | 69 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | JIMTOWN2 | 0.9603 | 0.8976 | -0.0627 | 69 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ASHDWN_W 4 | >0.94 | 0.8964 | >0.0436 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KINGHWY2 | 1.0375 | 0.9125 | -0.125 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KRSYJCTN4 | 0.9153 | 0.8731 | 0.0422 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KRSYJCTN4 | 0.9153 | 0.8731 | 0.0422 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IPC T 4 | 0.877 | 0.8199 | 0.0571 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | STRRDTP4 | 0.9182 | 0.8769 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | STRRDTP4 | 0.9182 | 0.8769 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BLALOCK2 | 0.8851 | 0.8353 | 0.0498 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HOLOX 2 | >0.94 | 0.9015 | >0.0385 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COOKVTP2 | 0.9393 | 0.915 | 0.0243 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BARITERDTP 4 | >0.94 | 0.9011 | >0.0389 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WCITYTP2 | 0.9374 | 0.883 | 0.0544 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SPRNGHL2 | 0.8804 | 0.822 | 0.0584 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WDEKALB2 | 0.8816 | 0.8233 | 0.0583 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DALLAS 2 | >0.94 | 0.8907 | >0.0493 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BROWNTP4 | 0.9186 | 0.8775 | 0.0411 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BROWNTP4 | 0.9186 | 0.8775 | 0.0411 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REBAR 4 | 0.9093 | 0.8673 | 0.042 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REBAR 4 | 0.9093 | 0.8673 | 0.042 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | TAYLOR 2 | 1.0342 | 0.9105 | -0.1237 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | RIFFIN REC4 | 0.8892 | 0.832 | 0.0572 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LSORD 2 | 1.0378 | 0.9077 | -0.1301 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LEHIGH-4 | 0.9389 | 0.9094 | 0.0295 | 138 | 0.92 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LEHIGH-4 | 0.9389 | 0.9094 | 0.0295 | 138 | 0.92 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | FTOWSON2 | 0.9398 | 0.887 | 0.0528 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HAWORTH4 | 0.9023 | 0.8446 | 0.0577 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BRYANML4 | 0.8847 | 0.8368 | 0.0479 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KEYSTNT4 | 0.9058 | 0.8576 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KEYSTNT4 | 0.9058 | 0.8576 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBRTP4 | 0.9111 | 0.8692 | 0.0419 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COLBRTP4 | 0.9111 | 0.8692 | 0.0419 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DARENCO2 | 0.8809 | 0.8308 | 0.0501 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IPC 2 | 0.9377 | 0.881 | 0.0567 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | YUBA4 | 0.9049 | 0.8625 | 0.0424 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | YUBA4 | 0.9049 | 0.8625 | 0.0424 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BROWN 4 | 0.9182 | 0.8768 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BROWN 4 | 0.9182 | 0.8768 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LSORDTP2 | 1.0383 | 0.9081 | -0.1302 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | IDABEL-4 | 0.904 | 0.8456 | 0.0584 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GODFREYRDTP2 | 0.9383 | 0.9055 | 0.0328 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LOCKSBRG 4 | >0.94 | 0.8959 | >0.0441 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DOMINAN4 | 0.9014 | 0.845 | 0.0564 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HUGO---4 | 0.9325 | 0.8802 | 0.0523 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | HUGO---2 | >0.94 | 0.8907 | >0.0493 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LINDEN 2 | 1.0378 | 0.9072 | -0.1306 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | VALYTIM2 | >0.94 | 0.9109 | >0.0291 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | USMOTAP2 | >0.94 | 0.8908 | >0.0492 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NNBOSTN2 | 1.0346 | 0.8914 | -0.1432 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BANN 4 | 0.9236 | 0.8683 | 0.0553 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | LYDIA 7 | >0.94 | 0.9161 | >0.0239 | 345 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BANN 2 | 1.0403 | 0.913 | -0.1273 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NNBOSTN4 | 0.8919 | 0.8347 | 0.0572 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MAUD 2 | 0.8933 | 0.8361 | 0.0572 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | MANDEVILTP4 | >0.94 | 0.8892 | >0.0508 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BETHEL 4 | 0.9313 | 0.8893 | 0.042 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SETEXAR2 | 1.0355 | 0.9085 | -0.127 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | PATTERS2 | >0.94 | 0.8991 | >0.0409 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | REDLICK2 | 1.0387 | 0.912 | -0.1267 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | PATTERS4 | >0.94 | 0.892 | >0.048 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SETEXAR4 | 0.9291 | 0.873 | 0.0561 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WAURIKA2 | >0.94 | 0.916 | >0.024 | 69 | 0.92 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | PEARLHL2 | 0.881 | 0.8308 | 0.0502 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KIERSEY4 | 0.908 | 0.866 | 0.042 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KIERSEY4 | 0.908 | 0.866 | 0.042 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GEN-2016-030 | 0.9182 | 0.8769 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GEN-2016-030 | 0.9182 | 0.8769 | 0.0413 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | WYNWOOD2 | 0.9435 | 0.8766 | -0.0669 | 69 | 0.9 | 1.05 | 0.60821 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | VALIANT2 | 0.9371 | 0.8829 | 0.0542 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | VALIANT4 | 0.9292 | 0.8754 | 0.0538 | 138 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | GOLDENSW4 | 0.9017 | 0.8451 | 0.0566 | 138 | 0.9 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | UNGER 4 | >0.92 | 0.879 | >0.041 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | UNGER 4 | >0.92 | 0.879 | >0.041 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ANTLTAP2 | >0.94 | 0.9172 | >0.0228 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BLUEBRD4 | 0.9058 | 0.8576 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | BLUEBRD4 | 0.9058 | 0.8576 | 0.0482 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NEKOSAT2 | >0.94 | 0.9015 | >0.0385 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DENISON4 | 0.9184 | 0.877 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | DENISON4 | 0.9184 | 0.877 | 0.0414 | 138 | 0.9 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | NMINEOL2 | <1.03 | 1.051 | >0.021 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | ANDRSNC4 | 0.8767 | 0.8215 | 0.0552 | 138 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | RYAN 2 | 0.959 | 0.8967 | -0.0623 | 69 | 0.9 | 1.05 | 0.60821 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COALGAT4 | >0.94 | 0.9126 | >0.0274 | 138 | 0.92 | 1.05 | 0.17881 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | COALGAT4 | >0.94 | 0.9126 | >0.0274 | 138 | 0.92 | 1.05 | 0.17881 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | SFORE_1 2 | 0.9339 | 0.877 | 0.0569 | 69 | 0.92 | 1.05 | 0.08575 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 24WP0 | G07_G077&G085 | KI PMPS2 | >0.94 | 0.8857 | >0.0543 | 69 | 0.92 | 1.05 | 0.15041 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUGDEN 2 | 0.9624 | 0.8988 | -0.0636 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GODFREYRDTP2 | >0.94 | 0.9077 | >0.0323 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | V-WEYCO4 | >0.94 | 0.8913 | >0.0487 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ALUMAX 4 | 0.9323 | 0.8798 | 0.0525 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | USMOTOR2 | >0.94 | 0.9038 | >0.0362 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KIPUMPT2 | >0.94 | 0.9042 | >0.0358 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDRVR-2 | 1.033 | 0.905 | -0.128 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DURANT 4 | 0.9055 | 0.8667 | 0.0388 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DURANT 4 | 0.9055 | 0.8667 | 0.0388 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DOMINAN4 | 0.9131 | 0.8609 | 0.0522 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBERT4 | 0.9103 | 0.8782 | 0.0321 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBERT4 | 0.9103 | 0.8782 | 0.0321 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOOKS 2 | 1.0376 | 0.9159 | -0.1217 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CASSTP4 | 0.8894 | 0.8415 | 0.0479 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NWTXARK4 | >0.94 | 0.8888 | >0.0512 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NWTXARK7 | >0.94 | 0.9024 | >0.0376 | 345 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BODLE 4 | 0.914 | 0.8822 | 0.0318 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BODLE 4 | 0.914 | 0.8822 | 0.0318 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ALAMANC2 | 0.8837 | 0.8335 | 0.0502 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CRAIGJT4 | 0.9113 | 0.8599 | 0.0514 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BARITE-RD 4 | >0.94 | 0.9127 | >0.0273 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | EYLAU 4 | 0.914 | 0.8596 | 0.0544 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BUFORDR2 | 0.9366 | 0.896 | 0.0406 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SCOLEMN4 | 0.9116 | 0.8774 | 0.0342 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SCOLEMN4 | 0.9116 | 0.8774 | 0.0342 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SFOREMAN 4 | 0.9171 | 0.8644 | 0.0527 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TEX12ST2 | 1.0312 | 0.9166 | -0.1146 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | RODESSA2 | 0.9393 | 0.9065 | 0.0328 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | B.BOW 4 | 0.9111 | 0.8579 | 0.0532 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BENNSUB4 | 0.9128 | 0.8719 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BENNSUB4 | 0.9128 | 0.8719 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BENNGTN4 | 0.9132 | 0.8724 | 0.0408 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BENNGTN4 | 0.9132 | 0.8724 | 0.0408 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | VELMA 2 | 0.9571 | 0.8863 | -0.0708 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BASELIN2 | 0.9643 | 0.8927 | -0.0716 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ANDRCKT2 | 0.9025 | 0.847 | 0.0555 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLEMNT4 | >0.92 | 0.8888 | >0.0312 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLEMNT4 | >0.92 | 0.8888 | >0.0312 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IPC TAP2 | 1.0302 | 0.8881 | -0.1421 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | W-RELIF2 | >0.94 | 0.9193 | >0.0207 | 69 | 0.92 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOCHJCT4 | 0.914 | 0.8622 | 0.0518 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WBURGE 5 | 0.9209 | 0.8988 | -0.0221 | 161 | 0.9 | 1.05 | 0.04554 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TXI4 | 0.9091 | 0.8769 | 0.0322 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TXI4 | 0.9091 | 0.8769 | 0.0322 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | EXPLRPL4 | 0.9193 | 0.8879 | 0.0314 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | EXPLRPL4 | 0.9193 | 0.8879 | 0.0314 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOLYCRK4 | 0.9145 | 0.8612 | 0.0533 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GORDON TAP 4 | 0.9099 | 0.8579 | 0.052 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TURK 7 | >0.94 | 0.9064 | >0.0336 | 345 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BIVINS 2 | 0.8829 | 0.8327 | 0.0502 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | AVENUECTY 5 | 0.9225 | 0.8973 | -0.0252 | 161 | 0.9 | 1.05 | 0.04554 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IPC-DOM4 | 0.8864 | 0.8306 | 0.0558 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MTRIVER4 | 0.9115 | 0.8599 | 0.0516 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NASH 4 | 0.9324 | 0.8799 | 0.0525 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BROKNBW4 | 0.9135 | 0.8607 | 0.0528 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NEKOOSA2 | 0.9307 | 0.8775 | 0.0532 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBRT-4 | 0.9106 | 0.8786 | 0.032 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBRT-4 | 0.9106 | 0.8786 | 0.032 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ASHDWNR4 | >0.94 | 0.9073 | >0.0327 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NEWBOST2 | 1.0333 | 0.8984 | -0.1349 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BUCHANN4 | 0.9134 | 0.8589 | 0.0545 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BRADLEY2 | 0.9666 | 0.8996 | -0.067 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NNBOSTN2 | 1.0342 | 0.8983 | -0.1359 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DARENCT2 | 0.8862 | 0.8362 | 0.05 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ASHDOWN2 | >0.94 | 0.9116 | >0.0284 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLUEBRD4 | 0.9117 | 0.8708 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLUEBRD4 | 0.9117 | 0.8708 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ATLANTA2 | 0.939 | 0.8922 | 0.0468 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLOOMBG2 | 0.9292 | 0.8814 | 0.0478 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MANDEVILTP4 | >0.94 | 0.8992 | >0.0408 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COVEREC2 | >0.94 | 0.9123 | >0.0277 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IDABEL 4 | 0.9168 | 0.8634 | 0.0534 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SEAWAY4 | 0.9094 | 0.8772 | 0.0322 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SEAWAY4 | 0.9094 | 0.8772 | 0.0322 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KI PMPN2 | >0.94 | 0.9039 | >0.0361 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DOMINJCT4 | 0.9135 | 0.8613 | 0.0522 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SDEKALB2 | 0.8903 | 0.8338 | 0.0565 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MAUDT 2 | 0.8988 | 0.843 | 0.0558 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MENA 2 | >0.94 | 0.9059 | >0.0341 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PLEASHL2 | 1.0339 | 0.9069 | -0.127 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NE-TEXARK2 | >0.94 | 0.8992 | >0.0408 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SCLMNJC4 | 0.9142 | 0.8801 | 0.0341 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SCLMNJC4 | 0.9142 | 0.8801 | 0.0341 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HARISBG2 | 0.9616 | 0.8939 | -0.0677 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DUGLASV2 | 0.9024 | 0.8536 | 0.0488 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BARITERDTP 4 | >0.94 | 0.9134 | >0.0266 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ROACH 2 | 0.8867 | 0.8368 | 0.0499 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DUGLASV4 | 0.8866 | 0.8398 | 0.0468 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IPC 4 | 0.8721 | 0.8158 | 0.0563 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IPC 2 | 1.0301 | 0.888 | -0.1421 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KIERSEY4 | 0.9117 | 0.8798 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KIERSEY4 | 0.9117 | 0.8798 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | W CITY 2 | >0.94 | 0.9062 | >0.0338 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BUTRFLD4 | 0.9128 | 0.8809 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BUTRFLD4 | 0.9128 | 0.8809 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WATLANT4 | 0.8925 | 0.846 | 0.0465 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOCHTWN4 | >0.92 | 0.8717 | >0.0483 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WATLANT2 | 1.0387 | 0.903 | -0.1357 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GARVIN4 | >0.92 | 0.8717 | >0.0483 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WASHST 2 | 1.0307 | 0.9146 | -0.1161 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DEQUEEN4 | 0.9076 | 0.8572 | 0.0504 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SAWYER 2 | >0.94 | 0.907 | >0.033 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SIMMS 2 | 0.8994 | 0.8436 | 0.0558 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | W-LIFTP2 | >0.94 | 0.9198 | >0.0202 | 69 | 0.92 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDSPRG4 | 0.9148 | 0.8605 | 0.0543 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DURANTP4 | 0.9067 | 0.8679 | 0.0388 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DURANTP4 | 0.9067 | 0.8679 | 0.0388 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SUGARHL4 | >0.94 | 0.8919 | >0.0481 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COOKVIL2 | >0.94 | 0.9103 | >0.0297 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | TEXARK 2 | 1.0348 | 0.9174 | -0.1174 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SDIERKS4 | >0.94 | 0.9134 | >0.0266 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NAPLES 2 | 0.936 | 0.8954 | 0.0406 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S BROWN4 | >0.92 | 0.8887 | >0.0313 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S BROWN4 | >0.92 | 0.8887 | >0.0313 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MUNZCTY4 | 0.8914 | 0.8451 | 0.0463 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KRSYJCTS4 | 0.9187 | 0.8871 | 0.0316 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KRSYJCTS4 | 0.9187 | 0.8871 | 0.0316 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GA PAC 2 | >0.94 | 0.8952 | >0.0448 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | S_TEXARK 2 | 1.034 | 0.9072 | -0.1268 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CHICKASAW2 | 0.9163 | 0.8963 | 0.02 | 69 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | CHICKASAW2 | 0.9163 | 0.8963 | 0.02 | 69 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NLINDEN2 | 0.8919 | 0.8423 | 0.0496 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDWATR4 | 0.9135 | 0.859 | 0.0545 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REDWATR2 | 0.8989 | 0.8431 | 0.0558 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MENA 2 | >0.94 | 0.9058 | >0.0342 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MENA 4 | 0.9105 | 0.8587 | 0.0518 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BRKN BW4 | >0.92 | 0.8775 | >0.0425 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | EOLA 2 | 0.9565 | 0.8876 | -0.0689 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ASHDWN_W 4 | >0.94 | 0.9078 | >0.0322 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KRSYJCTN4 | 0.9179 | 0.8855 | 0.0324 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KRSYJCTN4 | 0.9179 | 0.8855 | 0.0324 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | B.BOWTP4 | 0.9113 | 0.8582 | 0.0531 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IPC T 4 | 0.882 | 0.8264 | 0.0556 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | STRRDTP4 | >0.92 | 0.8893 | >0.0307 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | STRRDTP4 | >0.92 | 0.8893 | >0.0307 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BLALOCK2 | 0.8899 | 0.8403 | 0.0496 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LINDSAY2 | 0.9665 | 0.8986 | -0.0679 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HOLOX 2 | >0.94 | 0.9127 | >0.0273 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SPECTRM4 | 0.9603 | 0.8979 | -0.0624 | 138 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COOKVTP2 | >0.94 | 0.9104 | >0.0296 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WCITYTP2 | >0.94 | 0.9029 | >0.0371 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SPRNGHL2 | 0.8864 | 0.8295 | 0.0569 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WDEKALB2 | 0.8875 | 0.8308 | 0.0567 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BROWNTP4 | >0.92 | 0.8898 | >0.0302 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BROWNTP4 | >0.92 | 0.8898 | >0.0302 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NEKOSAT2 | >0.94 | 0.9128 | >0.0272 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REBAR 4 | 0.9126 | 0.8807 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | REBAR 4 | 0.9126 | 0.8807 | 0.0319 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | RIFFIN REC4 | 0.8951 | 0.8401 | 0.055 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LSORD 2 | 1.0375 | 0.9164 | -0.1211 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | FTOWSON2 | >0.94 | 0.9065 | >0.0335 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BRYANML4 | 0.8884 | 0.8407 | 0.0477 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KEYSTNT4 | 0.9118 | 0.8709 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KEYSTNT4 | 0.9118 | 0.8709 | 0.0409 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HAWORTH4 | 0.9156 | 0.8621 | 0.0535 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBRTP4 | 0.9143 | 0.8825 | 0.0318 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | COLBRTP4 | 0.9143 | 0.8825 | 0.0318 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DARENCO2 | 0.8859 | 0.8359 | 0.05 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | YUBA4 | 0.9087 | 0.8766 | 0.0321 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | YUBA4 | 0.9087 | 0.8766 | 0.0321 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BROWN 4 | >0.92 | 0.8892 | >0.0308 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BROWN 4 | >0.92 | 0.8892 | >0.0308 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LSORDTP2 | 1.038 | 0.9168 | -0.1212 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LOCKSBRG 4 | >0.94 | 0.9075 | >0.0325 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | ANDRSNC4 | 0.8817 | 0.8278 | 0.0539 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HUGO---4 | >0.94 | 0.8995 | >0.0405 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HUGO---2 | >0.94 | 0.9098 | >0.0302 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | HAWTH 7 | 0.932 | 0.8982 | -0.0338 | 345 | 0.9 | 1.05 | 0.04554 | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | LINDEN 2 | 1.0365 | 0.9072 | -0.1293 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | USMOTAP2 | >0.94 | 0.905 | >0.035 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BANN 4 | 0.9302 | 0.8774 | 0.0528 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NWT-BNT4 | 0.9391 | 0.8876 | 0.0515 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | NNBOSTN4 | 0.8979 | 0.843 | 0.0549 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | MAUD 2 | 0.8988 | 0.8429 | 0.0559 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DALLAS 2 | >0.94 | 0.9046 | >0.0354 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | BETHEL 4 | 0.9395 | 0.902 | 0.0375 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SETEXAR2 | 1.0356 | 0.9185 | -0.1171 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PATTERS2 | >0.94 | 0.9106 | >0.0294 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PATTERS4 | >0.94 | 0.9029 | >0.0371 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SETEXAR4 | 0.9361 | 0.8826 | 0.0535 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | WAURIKA2 | >0.94 | 0.9166 | >0.0234 | 69 | 0.92 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | PEARLHL2 | 0.886 | 0.836 | 0.05 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | IDABEL-4 | 0.9171 | 0.8633 | 0.0538 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-030 | >0.92 | 0.8892 | >0.0308 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GEN-2016-030 | >0.92 | 0.8892 | >0.0308 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | VALIANT2 | >0.94 | 0.9028 | >0.0372 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | VALIANT4 | >0.94 | 0.8951 | >0.0449 | 138 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | GOLDENSW4 | 0.9135 | 0.8611 | 0.0524 | 138 | 0.9 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SNASHVL4 | >0.94 | 0.9089 | >0.0311 | 138 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | UNGER 4 | >0.92 | 0.8928 | >0.0272 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | UNGER 4 | >0.92 | 0.8928 | >0.0272 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DENISON4 | >0.92 | 0.8894 | >0.0306 | 138 | 0.9 | 1.05 | 0.17908 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | DENISON4 | >0.92 | 0.8894 | >0.0306 | 138 | 0.9 | 1.05 | 0.17908 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | RYAN 2 | 0.962 | 0.8983 | -0.0637 | 69 | 0.9 | 1.05 | 0.60952 | POI-SUNNYSD7: 97000 POI 345 515136 SUNNYSD7 345 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | SFORE_1 2 | >0.94 | 0.8866 | >0.0534 | 69 | 0.92 | 1.05 | 0.08565 | 84111: 508072 NWTXARK7 345 508359 WELSH 7 345 1 508298 LYDIA 7 345 508359 WELSH 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 1 508359 WELSH 7 345 508832 DIANA 7 345 2 508359 WELSH 7 345 508841 WILKES 7 345 1 508359 WELSH 7 345 509404 WELSH1-1 18.0 1 508359 WELSH 7 345 509406 WELSH3-1 18.0 1
NRIS | 00NR | S2 | 19WP0 | G07_G077&G085 | KI PMPS2 | >0.94 | 0.9058 | >0.0342 | 69 | 0.92 | 1.05 | 0.15098 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 20G0 | G07_G077&G085 | GEN-2016-111 | 1.0301 | 1.0503 | 0.0202 | 345 | 0.95 | 1.05 | 0.04296 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 532771 RENO 7 345 997951 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-2 115 1
NRIS | 07NR | S2 | 20G0 | G07_G077&G085 | GEN-2016-111 | 1.0301 | 1.0503 | 0.0202 | 345 | 0.95 | 1.05 | 0.04296 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 532771 RENO 7 345 997951 RENO TX-1 115 1 532771 RENO 7 345 997950 RENO TX-2 115 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | V-WEYCO4 | 0.9147 | 0.8844 | 0.0303 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | KIPUMPT2 | 0.9293 | 0.8996 | 0.0297 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DURANT 4 | 0.9116 | 0.885 | 0.0266 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DURANT 4 | 0.9116 | 0.885 | 0.0266 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HOCHTWN4 | >0.92 | 0.8916 | >0.0284 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | CRAIGJT4 | 0.9187 | 0.8898 | 0.0289 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | WCITYTP2 | 0.9295 | 0.8994 | 0.0301 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | KI PMPS2 | 0.9336 | 0.9033 | 0.0303 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | B.BOW 4 | 0.9151 | 0.8848 | 0.0303 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BENNSUB4 | 0.8988 | 0.8695 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BENNSUB4 | 0.8988 | 0.8695 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BENNGTN4 | 0.8989 | 0.8697 | 0.0292 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BENNGTN4 | 0.8989 | 0.8697 | 0.0292 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HOCHJCT4 | 0.9164 | 0.8865 | 0.0299 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HOLYCRK4 | 0.9129 | 0.8817 | 0.0312 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | GORDON TAP 4 | 0.9326 | 0.9105 | 0.0221 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | MTRIVER4 | 0.9183 | 0.8892 | 0.0291 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BROKNBW4 | 0.9144 | 0.8838 | 0.0306 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BLUEBRD4 | 0.8985 | 0.8692 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BLUEBRD4 | 0.8985 | 0.8692 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | IDABEL 4 | 0.9124 | 0.8809 | 0.0315 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DOMINJCT4 | 0.9155 | 0.8853 | 0.0302 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | VALLANT4 | 0.9199 | 0.8917 | 0.0282 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DEQUEEN4 | 0.9269 | 0.9002 | 0.0267 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | W CITY 2 | 0.9338 | 0.9035 | 0.0303 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | GARVIN4 | 0.9115 | 0.88 | 0.0315 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | SAWYER 2 | 0.9287 | 0.8999 | 0.0288 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | KI PMPN2 | 0.9292 | 0.8995 | 0.0297 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DURANTP4 | 0.9117 | 0.8852 | 0.0265 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DURANTP4 | 0.9117 | 0.8852 | 0.0265 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | WSTBANK4 | 0.9099 | 0.8874 | 0.0225 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | WSTBANK4 | 0.9099 | 0.8874 | 0.0225 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | GA PAC 2 | 0.9266 | 0.8964 | 0.0302 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | B.BOWTP4 | 0.9152 | 0.8849 | 0.0303 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | MENA 4 | 0.9335 | 0.912 | 0.0215 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | FTOWSON2 | 0.9299 | 0.9008 | 0.0291 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | KEYSTNT4 | 0.8985 | 0.8692 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | KEYSTNT4 | 0.8985 | 0.8692 | 0.0293 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HAWORTH4 | 0.9123 | 0.8809 | 0.0314 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | WSBNKTP4 | 0.9099 | 0.8874 | 0.0225 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | WSBNKTP4 | 0.9099 | 0.8874 | 0.0225 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BRKN BW4 | >0.92 | 0.8944 | >0.0256 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | DOMINAN4 | 0.9154 | 0.8852 | 0.0302 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HUGO---4 | 0.9211 | 0.892 | 0.0291 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | HUGO---2 | 0.9283 | 0.9002 | 0.0281 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | VALYTIM2 | >0.94 | 0.9163 | >0.0237 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | BETHEL 4 | 0.9377 | 0.913 | 0.0247 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | IDABEL-4 | 0.9125 | 0.881 | 0.0315 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | VALIANT2 | 0.9288 | 0.8987 | 0.0301 | 69 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | VALIANT4 | 0.9182 | 0.8881 | 0.0301 | 138 | 0.92 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | GOLDENSW4 | 0.9151 | 0.8848 | 0.0303 | 138 | 0.9 | 1.05 | 0.1505 | 84131: 508072 NWTXARK7 345 510911 VALIANT7 345 1 508298 LYDIA 7 345 510911 VALIANT7 345 1 510907 PITTSB-7 345 510911 VALIANT7 345 1 510911 VALIANT7 345 521157 HUGO 7 345 1 510911 VALIANT7 345 998397 VALIANT1 138 2 510911 VALIANT7 345 998396 VALIANT3 138 1 510911 VALIANT7 345 998394 VALIANT1 138 2 510911 VALIANT7 345 998393 VALIANT3 138 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | UNGER 4 | 0.8974 | 0.8699 | 0.0275 | 138 | 0.9 | 1.05 | 0.1706 | 81723: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
NRIS | 07NR | S2 | 24L0 | G07_G077&G085 | UNGER 4 | 0.8974 | 0.8699 | 0.0275 | 138 | 0.9 | 1.05 | 0.1706 | 817231: 510907 PITTSB-7 345 510911 VALIANT7 345 1 521157 HUGO 7 345 560088 G16-063-TAP 345 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | WAURIKA2 | >0.94 | 0.9186 | >0.0214 | 69 | 0.92 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | BASELIN2 | 0.9627 | 0.8953 | -0.0674 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | RYAN 2 | 0.9617 | 0.8994 | -0.0623 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | SUGDEN 2 | 0.9622 | 0.8999 | -0.0623 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | BRADYJT2 | 0.955 | 0.8913 | -0.0637 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | VELMA 2 | 0.9553 | 0.8881 | -0.0672 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | EOLA 2 | 0.9533 | 0.8883 | -0.065 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | BRADY 2 | 0.9472 | 0.8828 | -0.0644 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | WYNWOOD2 | 0.9454 | 0.8809 | -0.0645 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | HARISBG2 | 0.9598 | 0.895 | -0.0648 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1
ERIS | 07ALL | S1 | 24WP0 | G07_G077&G085 | LINDSAY2 | 0.9614 | 0.8971 | -0.0643 | 69 | 0.9 | 1.05 | 0.60954 | 81741: 97000 POI 345 515136 SUNNYSD7 345 1 514809 JOHNCO 7 345 515136 SUNNYSD7 345 1 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 515136 SUNNYSD7 345 998277 SUNNYSD3 138 1 515136 SUNNYSD7 345 998276 SUNNYSD2 138 1 515136 SUNNYSD7 345 998274 SUNNYSD3 138 1 515136 SUNNYSD7 345 998273 SUNNYSD2 138 1

## Stability Analysis
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2
7 | 19W | Base | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units under numerous contingencies across all cases. This issue was observed also in the original Study and was identified as a potential modeling issue. Since this issue is observed in many contingencies it's reported once.
7 | 19W | Sensitivity | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.56pu, MaxDur: 0.04s
7 | 19W | Transfer | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.56pu, MaxDur: 0.04s
7 | 21L | Base | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - EQT_BESS_LV[1] G15-045-GEN1[1] | 70106 [EQT_BESS_LV] (Study project) and 584862 [G15-045-GEN] tripped on over voltage protections. The protection were disabled for G15-045-GEN and the simulation was rerun. It was observed that, 70106 [EQT_BESS_LV] tripped on under voltage protection. No further action was taken in the sensitivity cases. Voltage Spike: 1.53pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.86pu | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.62pu, MaxDur: 0.04s NOTE: Some abnormal fluctuations are observed after clearing the fault in the Project's responses. This is not impacting stability results. However, it could be a modeling issue, which may need further investigations.
7 | 21S | Base | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] tripped on over voltage protections. The protection was disabled and the simulation was rerun. It was observed that, 70106 [EQT_BESS_LV] tripped on under frequency protection. No further action was taken in the sensitivity cases. Voltage Spike: 1.62pu, MaxDur: 0.06s
7 | 21S | Transfer | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] EQT_LV_GEN[1] | 70104 [EQT_LV_GEN] (Study project) and 584862 [G15-045-GEN] tripped on over voltage and frequency protections. The protection were disabled for G15-045-GEN and the simulation was rerun. No further issue was observed. Voltage Spike: 1.57pu, MaxDur: 0.06s
7 | 28S | Base | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.56pu, MaxDur: 0.06s
7 | 28S | Transfer | FLT_1_P1_POI | Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.65pu, MaxDur: 0.06s
7 | 19W | Base | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.48pu, MaxDur: 0.04s
7 | 19W | Transfer | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.48pu, MaxDur: 0.04s NOTE: There could be some power sharing modeling issues accocaited with the Project's BESS and PV units. Following the fault clearance the PV plant is settled at lower power and BESS is set at higher value. Since this is not impacting the stability results no further action was taken.
7 | 21L | Base | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - EQT_BESS_LV[1] | 70106 [EQT_BESS_LV] (Study project) tripped on under voltage protection. No further action was taken in the sensitivity cases. Voltage Spike: 1.46pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | No - MaxV: 1.45pu, MaxDur: 0.11s | Yes | Yes | Yes | No - EQT_LV_GEN[1] G1140G1204G2[1] G1140G1204G1[1] | 70104 [EQT_LV_GEN] (Study project) tripped under frequency protection and 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protection were disabled for G1140G units and the simulation was rerun. No further issues were oberved.
7 | 21S | Base | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.50pu, MaxDur: 0.06s
7 | 28S | Base | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.47pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_2_P1_POI | Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.50pu, MaxDur: 0.06s
7 | 19W | Base | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 19W | Transfer | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 21L | Transfer | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 21S | Transfer | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 28S | Transfer | FLT_3_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 19W | Transfer | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 21L | Transfer | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 21S | Transfer | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | No | No | No | No | No | No | System unstability was observed under this contingency (including 511946[KIOWA S1] & 511947[KIOWA S2] units). No further action was taken in the sensitivity scenario.
7 | 28S | Transfer | FLT_4_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_5_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_6_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_7_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_8_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_9_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
7 | 19W | Transfer | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.13pu | Yes | Yes
7 | 21L | Transfer | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.13pu | Yes | Yes
7 | 28S | Sensitivity | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.17pu | Yes | Yes
7 | 28S | Transfer | FLT_10_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.15pu | Yes | Yes
7 | 19W | Base | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
7 | 19W | Sensitivity | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.39pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.41pu, MaxDur: 0.03s
7 | 21L | Base | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed.
7 | 21L | Sensitivity | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.38pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.41pu, MaxDur: 0.04s
7 | 21S | Base | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed.
7 | 21S | Sensitivity | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.46pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 28S | Base | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed.
7 | 28S | Sensitivity | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.46pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_11_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 19W | Base | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.41pu, MaxDur: 0.04s
7 | 21S | Transfer | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.42pu, MaxDur: 0.04s
7 | 28S | Base | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.41pu, MaxDur: 0.04s
7 | 28S | Transfer | FLT_12_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.42pu, MaxDur: 0.05s
7 | 19W | Base | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_13_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_14_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_15_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.48pu, MaxDur: 0.03s
7 | 21L | Base | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.04s
7 | 21S | Base | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.49pu, MaxDur: 0.05s
7 | 28S | Base | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_16_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.49pu, MaxDur: 0.05s
7 | 19W | Base | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.44pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.46pu, MaxDur: 0.03s
7 | 21L | Base | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.43pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.04s
7 | 21S | Base | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.46pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 28S | Base | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.46pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_17_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 19W | Base | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.87pu | Yes | Yes | Yes
7 | 19W | Transfer | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.90pu | Yes | Yes | Yes
7 | 21L | Base | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.90pu | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.78pu | Yes | Yes | Yes
7 | 21L | Transfer | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.82pu | Yes | Yes | Yes
7 | 21S | Base | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | Yes
7 | 28S | Transfer | FLT_18_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_19_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G16-063-GEN1[1] G16-063-GEN2[1] | 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved.
7 | 21S | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - G16-063-GEN1[1] G16-063-GEN2[1] | 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved.
7 | 28S | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_21_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_22_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No - Min: 0.84pu | Yes | Yes | Yes
7 | 19W | Transfer | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No - Min: 0.84pu | Yes | Yes | Yes
7 | 21L | Transfer | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_23_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_24_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted Transmission Circuit. Simultaneously open DC line r"""SPP_44_OKLUN""" and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
7 | 19W | Transfer | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.13pu | Yes | Yes
7 | 21L | Transfer | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.13pu | Yes | Yes
7 | 28S | Sensitivity | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.17pu | Yes | Yes
7 | 28S | Transfer | FLT_25_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.15pu | Yes | Yes
7 | 19W | Base | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_26_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_27_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_28_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open LONEGRV4 to CHEEKTP4 138kV transmission line CKT 1.Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_29_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_30_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_31_P4_HUGO | Apply single-phase fault on HUGO PP4 138kV/345kV/13.8kV transformer CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Three Winding. Simultaneously open VALIANT7 to HUGO 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - EQT_LV_GEN[1] G1140G1204G2[1] G1140G1204G1[1] | 70104 [EQT_LV_GEN] (Study project) tripped under frequency protection and 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protection were disabled for G1140 units and the simulation was rerun. No further issues were oberved (no trip for the study project). Voltage Spike: 1.47pu, MaxDur: 0.04s
7 | 19W | Transfer | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.48pu, MaxDur: 0.04s
7 | 21L | Base | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G16-063-GEN1[1] G16-063-GEN2[1] G1140G1204G1[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.46pu, MaxDur: 0.04s
7 | 21L | Transfer | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | No - MaxV: 1.51pu, MaxDur: 0.11s | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved.
7 | 21S | Base | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.52pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.54pu, MaxDur: 0.06s
7 | 28S | Base | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.52pu, MaxDur: 0.06s
7 | 28S | Transfer | FLT_32_P6_POI | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.58pu, MaxDur: 0.06s
7 | 19W | Base | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 19W | Sensitivity | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 19W | Transfer | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 21L | Base | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 21L | Transfer | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 21L | Sensitivity | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. Since this issue is observed in the BC, TC, and SC of 19W no further action was taken.
7 | 21S | Base | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. No further action was taken in the sensitivity case.
7 | 21S | Transfer | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrements of 25%. At 25% dispatch no further issues were observed. Note, at 50% dispatch, EQT_LV_GEN (the study project) tripped. | 25% dispatch of Study Project
7 | 28S | Base | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.85pu | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A: Not Applicable. The N-1 case could not be solved due to high flow on the outaged line. No further action was taken in the sensitivity case.
7 | 28S | Transfer | FLT_33_P6_POI | Prior Outage of MINCO to GRACMNT7 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - LANOGSU10.60[W1] 032204201651[1 ] G15-045-GEN1[1] | 523812 [LANOGSU1], 511975 unit & 584862 [G15-045-GEN] tripped on voltage protections. The protection were disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrementally. At 10% dispatch no further issues were observed. | 10% dispatch of Study Project
7 | 19W | Base | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G16-063-GEN1[1] G1140G1204G1[1] G16-063-GEN2[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.57pu, MaxDur: 0.04s
7 | 19W | Transfer | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G16-063-GEN1[1] G16-063-GEN2[1] G1140G1204G1[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.64pu, MaxDur: 0.04s
7 | 21L | Base | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G16-063-GEN1[1] G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1] & 587433 [G16-063-GEN1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.54pu, MaxDur: 0.04s
7 | 21L | Transfer | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G16-063-GEN1[1] G1140G1204G2[1] G1140G1204G1[1] G16-063-GEN2[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.55pu, MaxDur: 0.04s
7 | 21S | Base | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.56pu, MaxDur: 0.04s
7 | 21S | Transfer | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G16-063-GEN1[1] G16-063-GEN2[1] G1140G1204G1[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.59pu, MaxDur: 0.04s
7 | 28S | Base | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G1140G1204G1[1] | 515919 [G1140G1204G2] & 515917 [G1140G1204G1] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.57pu, MaxDur: 0.04s
7 | 28S | Transfer | FLT_34_P6_POI | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to TERRYRD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G1140G1204G2[1] G16-063-GEN1[1] G16-063-GEN2[1] G1140G1204G1[1] | 515919 [G1140G1204G2], 515917 [G1140G1204G1], 587433 [G16-063-GEN1] & 587436 [G16-063-GEN2] tripped on over voltage protections. The protections were disabled and the simulation was rerun. No further issues were oberved. Voltage Spike: 1.57pu, MaxDur: 0.04s
7 | 19W | Base | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.87pu | Yes | Yes | Yes | 520519[BCI WTG], 520520[BCII WTG], 520521[BCV WTG] & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units. These units were gnetted and the simulation was rerun. The abnormal oscillations disappeared and no further issues were observed.
7 | 19W | Sensitivity | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability was observed before and after protection disable under this contingency (including the study project units). No further action was taken in the sensitivity case.
7 | 19W | Transfer | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrements of 25%. At 25% dispatch no further issues were observed. | 25% dispatch of Study Project
7 | 21L | Base | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.76pu | Yes | Yes | Yes | 520519[BCI WTG], 520520[BCII WTG], 520521[BCV WTG] & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units. These units were gnetted and the simulation was rerun. The abnormal oscillations disappeared and no further issues were observed.
7 | 21L | Sensitivity | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] G16-091-GEN1[1] | 584862 [G15-045-GEN] & 587743 [G16-091-GEN1] tripped on voltage protections. The protection was disabled and the simulation was rerun. System instability was observed before and after protection disable under this contingency (including the study project units). No further action was taken in the sensitivity case.
7 | 21L | Transfer | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] G16-091-GEN1[1] | 584862 [G15-045-GEN] & 587743 [G16-091-GEN1] tripped on voltage protections. The protection was disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrementally. At 10% dispatch no further issues were observed. | 10% dispatch of Study Project
7 | 21S | Base | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.80pu | Yes | Yes | Yes | 520519[BCI WTG], 520520[BCII WTG], 520521[BCV WTG] & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units. These units were gnetted and the simulation was rerun. The abnormal oscillations disappeared and no further issues were observed.
7 | 21S | Sensitivity | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability was observed before and after protection disable under this contingency (including the study project units). No further action was taken in the sensitivity case.
7 | 21S | Transfer | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrements of 25%. At 50% dispatch no further issues were observed. | 50% dispatch of Study Project
7 | 28S | Base | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | 520519[BCI WTG], 520520[BCII WTG], 520521[BCV WTG] & 520522[BCVI_WTG1]: Abnormal oscillations were observed for these units. These units were gnetted and the simulation was rerun. The abnormal oscillations disappeared and no further issues were observed.
7 | 28S | Sensitivity | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability was observed before and after protection disable under this contingency (including the study project units). No further action was taken in the sensitivity case.
7 | 28S | Transfer | FLT_35_P6_POI | Prior Outage of GRACMNT7 to G16-091-TAP 345kV transmission line CKT 1Apply 3-phase fault on POI to SUNNYSD7 345kV transmission line CKT 1, near POI 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Unstable | No | No | No | No | No | No - G15-045-GEN1[1] | 584862 [G15-045-GEN] : tripped on over voltage protection. The protection was disabled and the simulation was rerun. System instability and sustained undamped oscillations were observed following the protection disable. Mitigation: Study project dispatch was reduced in icnrements of 25%. At 50% dispatch no further issues were observed. | 50% dispatch of Study Project
7 | 19W | Base | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.85pu | Yes | Yes | Yes
7 | 19W | Transfer | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.85pu | Yes | Yes | Yes
7 | 21L | Transfer | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_36_P6_VALIANT7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_37_P6_SUNNYSD4 | Prior Outage of CARTER 4 to CHIKSAW4 138kV transmission line CKT 1Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.48pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.49pu, MaxDur: 0.03s
7 | 21L | Base | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.49pu, MaxDur: 0.04s
7 | 21S | Base | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.49pu, MaxDur: 0.05s
7 | 28S | Base | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_38_P6_SUNNYSD7 | Prior Outage of LYDIA to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.49pu, MaxDur: 0.05s
7 | 19W | Base | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 21L | Base | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.46pu, MaxDur: 0.04s
7 | 21L | Transfer | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.46pu, MaxDur: 0.04s
7 | 21S | Base | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.47pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.48pu, MaxDur: 0.05s
7 | 28S | Base | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 28S | Transfer | FLT_39_P6_SUNNYSD7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.47pu, MaxDur: 0.05s
7 | 19W | Base | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.53pu, MaxDur: 0.07s
7 | 19W | Transfer | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.04s
7 | 21L | Base | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.04s
7 | 21L | Transfer | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.53pu, MaxDur: 0.04s
7 | 21S | Base | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.53pu, MaxDur: 0.04s
7 | 21S | Transfer | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.04s
7 | 28S | Base | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.04s
7 | 28S | Transfer | FLT_40_P6_SUNNYSD7 | Prior Outage of HUGO to G16-063-TAP 345kV transmission line CKT 1Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.53pu, MaxDur: 0.04s
7 | 19W | Base | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.45pu, MaxDur: 0.03s
7 | 19W | Transfer | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 21L | Base | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.44pu, MaxDur: 0.03s
7 | 21L | Transfer | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.03s
7 | 21S | Base | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.05s
7 | 21S | Transfer | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.50pu, MaxDur: 0.05s
7 | 28S | Base | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.47pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_41_P6_SUNNYSD7 | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.50pu, MaxDur: 0.05s
7 | 19W | Base | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.07s
7 | 19W | Transfer | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.04s
7 | 21L | Base | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | No - MaxV: 1.51pu, MaxDur: 0.11s | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed.
7 | 21L | Transfer | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | No - MaxV: 1.52pu, MaxDur: 0.11s | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed.
7 | 21S | Base | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.03s
7 | 21S | Transfer | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.03s
7 | 28S | Base | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.05s
7 | 28S | Transfer | FLT_42_P6_SUNNYSD7 | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - G15-045-GEN1[1] | 584862 [G15-045-GEN]: tripped on over voltage protection. The protection was disabled and the simulation was rerun. No further issue was observed. Voltage Spike: 1.52pu, MaxDur: 0.05s
7 | 19W | Base | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Base | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Transfer | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Base | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_43_P6_HUGO | Prior Outage of SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Base | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Sensitivity | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 19W | Transfer | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.90pu | Yes | Yes | Yes
7 | 21L | Base | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21L | Sensitivity | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.90pu | Yes | Yes | Yes
7 | 21L | Transfer | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | No - Min: 0.89pu | Yes | Yes | Yes
7 | 21S | Base | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Sensitivity | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 21S | Transfer | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Base | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Sensitivity | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
7 | 28S | Transfer | FLT_44_P6_G16-063-TAP | Prior Outage of PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 584073 ID: 1 Name: G14-057-GEN1 | 07 - Southwestern Oklahoma | ALL | 249.9
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 584862 ID: 1 Name: G15-045-GEN1 | 07 - Southwestern Oklahoma | ALL | 20
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 563262 ID: 1 Name: G15-092-GEN1 | 07 - Southwestern Oklahoma | ALL | 140
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 563263 ID: 1 Name: G15-092-GEN2 | 07 - Southwestern Oklahoma | ALL | 110
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 587436 ID: 1 Name: G16-063-GEN2 | 07 - Southwestern Oklahoma | ALL | 100
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 587433 ID: 1 Name: G16-063-GEN1 | 07 - Southwestern Oklahoma | ALL | 100
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 584783 ID: 1 Name: G15-036-GEN1 | 07 - Southwestern Oklahoma | ALL | 143
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 584786 ID: 1 Name: G15-036-GEN2 | 07 - Southwestern Oklahoma | ALL | 137.5
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 584786 ID: 2 Name: G15-036-GEN2 | 07 - Southwestern Oklahoma | ALL | 23
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511852 ID: 1 Name: COM2-1 | 07 - Southwestern Oklahoma | 19W, 21L, 21S | 83.5
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511851 ID: 1 Name: COM1-1 | 07 - Southwestern Oklahoma | 19W, 21L, 21S | 88
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511853 ID: 1 Name: COM3-1 | 07 - Southwestern Oklahoma | 19W, 21L, 21S | 80
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511852 ID: 1 Name: COM2-1 | 07 - Southwestern Oklahoma | 28S | 76.5
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511851 ID: 1 Name: COM1-1 | 07 - Southwestern Oklahoma | 28S | 82
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511853 ID: 1 Name: COM3-1 | 07 - Southwestern Oklahoma | 28S | 72
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 587743 ID: 1 Name: G16-091-GEN1 | 07 - Southwestern Oklahoma | ALL | 303.6
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 587773 ID: 1 Name: G16-095-GEN1 | 07 - Southwestern Oklahoma | ALL | 200
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 520947 ID: 1 Name: HUGO1 | 07 - Southwestern Oklahoma | ALL | 465.07
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 587793 ID: 1 Name: G16-097-GEN1 | 07 - Southwestern Oklahoma | ALL | 100
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 563272 ID: 1 Name: G15-093-GEN1 | 07 - Southwestern Oklahoma | ALL | 140
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 563273 ID: 2 Name: G15-093-GEN2 | 07 - Southwestern Oklahoma | ALL | 110
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511944 ID: 1 Name: KIOWA G1 | 07 - Southwestern Oklahoma | ALL | 177
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511945 ID: 1 Name: KIOWA G2 | 07 - Southwestern Oklahoma | ALL | 177
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511946 ID: 1 Name: KIOWA S1 | 07 - Southwestern Oklahoma | ALL | 320
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511947 ID: 1 Name: KIOWA S2 | 07 - Southwestern Oklahoma | ALL | 320
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511948 ID: 1 Name: KIOWA G3 | 07 - Southwestern Oklahoma | ALL | 177
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 511949 ID: 1 Name: KIOWA G4 | 07 - Southwestern Oklahoma | ALL | 177
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 515913 ID: 1 Name: GEN-2013-007 | 07 - Southwestern Oklahoma | ALL | 100
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 515919 ID: 1 Name: GEN-2012-004 | 07 - Southwestern Oklahoma | ALL | 76
GEN-2020-074 & GEN-2020-085 | 70104 & 70106 | Bus: 515917 ID: 1 Name: GEN-2011-040 | 07 - Southwestern Oklahoma | ALL | 74

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 28SP Fault Current 3-Phase (kA) | Request In Service 28SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 70101 | EQT_SUB_HV | 345 | 9.4453 | 10.8327 | 0.27
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 97000 | POI | 345 | 12.4782 | 10.838 | -1.6402
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 508072 | NWTXARK7 | 345 | 11.9412 | 12.5917 | 0.65053
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 508298 | LYDIA 7 | 345 | 13.0919 | 12.0657 | -1.0261
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 510907 | PITTSB-7 | 345 | 12.5854 | 13.3845 | 0.79904
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 510911 | VALIANT7 | 345 | 14.1308 | 12.8182 | -1.3126
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 510918 | VALIANT4 | 138 | 12.866 | 14.3609 | 1.4949
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 510925 | KIOWA 7 | 345 | 12.3282 | 13.152 | 0.82378
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 510946 | C-RIVER4 | 138 | 7.6485 | 12.4791 | 4.8306
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511422 | FLETCHR4 | 138 | 8.389 | 7.7362 | -0.65275
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511423 | FLE TAP4 | 138 | 10.5857 | 8.4858 | -2.1
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511431 | LWS S4 | 138 | 9.2018 | 10.7595 | 1.5577
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511436 | COMANC-2 | 69 | 17.2556 | 9.2954 | -7.9601
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 11.043 | 17.5523 | 6.5094
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 4.9971 | 11.2254 | 6.2283
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511456 | O.K.U.-7 | 345 | 15.5394 | 5.0897 | -10.4497
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511466 | L.E.S.-2 | 69 | 23.6835 | 15.7612 | -7.9223
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 12.6712 | 24.1779 | 11.5068
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511468 | L.E.S.-7 | 345 | 7.5911 | 13.1046 | 5.5135
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511469 | LGORE-N2 | 69 | 6.6144 | 7.6917 | 1.0773
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511470 | LGORE-S2 | 69 | 11.7947 | 6.703 | -5.0918
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511474 | SHERID4 | 138 | 9.4536 | 11.9966 | 2.543
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511486 | ELGINJT4 | 138 | 8.0343 | 9.5752 | 1.5408
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511487 | ELGINJT2 | 69 | 12.1636 | 8.131 | -4.0326
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511488 | 112GORE4 | 138 | 20.646 | 12.3641 | -8.2819
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 11.4522 | 21.0494 | 9.5972
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511512 | RPPAPER4 | 138 | 11.2068 | 11.6407 | 0.43384
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511537 | ARTVLTP4 | 138 | 9.3797 | 11.3946 | 2.0149
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511563 | ELSWORTH 4 | 138 | 4.9833 | 9.499 | 4.5157
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511565 | OKLAUN HVDC7 | 345 | 9.7191 | 5.0757 | -4.6434
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511568 | TERRYRD7 | 345 | 6.3646 | 10.4153 | 4.0507
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 511571 | RUSHSPR7 | 345 | 17.559 | 6.7055 | -10.8535
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 514801 | MINCO 7 | 345 | 14.5838 | 17.7293 | 3.1455
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 514808 | JOHNCO 4 | 138 | 9.5105 | 15.1324 | 5.622
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 514809 | JOHNCO 7 | 345 | 28.9119 | 10.0498 | -18.862
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 514908 | ARCADIA7 | 345 | 20.4173 | 29.0442 | 8.6268
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 514934 | DRAPER 7 | 345 | 38.3176 | 20.5871 | -17.7305
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515044 | SEMINOL4 | 138 | 25.7062 | 38.7654 | 13.0592
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515045 | SEMINOL7 | 345 | 10.7847 | 25.9747 | 15.1899
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515120 | RUSSET-4 | 138 | 10.5186 | 11.1338 | 0.61518
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515121 | MILLCKT4 | 138 | 10.6587 | 10.8414 | 0.18278
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515122 | SXMLCKT4 | 138 | 4.916 | 10.9901 | 6.0741
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515128 | RATLIFF2 | 69 | 6.2632 | 5.0551 | -1.2081
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515129 | RATLIFF4 | 138 | 7.9907 | 6.4544 | -1.5363
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515130 | POOLVIL4 | 138 | 6.5617 | 8.2701 | 1.7084
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515131 | FOX 4 | 138 | 5.2154 | 6.7925 | 1.5771
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515134 | PRARPNT4 | 138 | 17.4979 | 5.3482 | -12.1497
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515135 | SUNNYSD4 | 138 | 10.5437 | 18.5938 | 8.0502
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515136 | SUNNYSD7 | 345 | 11.9203 | 11.6318 | -0.28844
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515137 | UNIROY 4 | 138 | 11.8138 | 12.4743 | 0.66048
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515138 | CARTER 4 | 138 | 9.2017 | 12.2985 | 3.0968
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515143 | WOLFCRK4 | 138 | 12.6635 | 9.6293 | -3.0342
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515144 | LONEGRV4 | 138 | 7.7366 | 13.3408 | 5.6042
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515147 | GLASSES4 | 138 | 7.7277 | 7.9556 | 0.22795
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515149 | MADINDT4 | 138 | 8.1318 | 7.9462 | -0.18558
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515150 | CANEYCK4 | 138 | 6.785 | 8.3547 | 1.5696
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515151 | LTLCITY4 | 138 | 11.0461 | 6.9544 | -4.0917
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515162 | FNDTION4 | 138 | 7.4589 | 11.4846 | 4.0257
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515163 | ROCKYPT2 | 69 | 9.9648 | 7.7142 | -2.2506
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515164 | ROCKYPT4 | 138 | 10.8964 | 10.3978 | -0.49862
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515172 | SPRNDAL4 | 138 | 26.7032 | 11.3339 | -15.3693
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515224 | MUSKOGE7 | 345 | 11.7591 | 26.856 | 15.0968
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515372 | ARDWEST4 | 138 | 11.4672 | 12.2952 | 0.82802
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515415 | CHEEKTP4 | 138 | 8.6171 | 12.0536 | 3.4365
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515420 | SCMMRCT2 | 69 | 9.3621 | 8.9063 | -0.45584
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515422 | C-RIVER7 | 345 | 4.3692 | 9.4967 | 5.1275
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515458 | BORDER 7 | 345 | 8.1706 | 4.384 | -3.7866
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515561 | CARTRCO4 | 138 | 5.2872 | 8.4567 | 3.1695
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515563 | ORIGINW4 | 138 | 2.1069 | 5.4222 | 3.3153
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515676 | MRIETAT2 | 69 | 16.6041 | 2.1729 | -14.4312
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515800 | GRACMNT7 | 345 | 27.6788 | 16.8449 | -10.8339
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515802 | GRACMNT4 | 138 | 10.1869 | 27.9414 | 17.7545
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515873 | DRPSPRG4 | 138 | 9.3522 | 10.5822 | 1.23
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 515932 | STIRLNG4 | 138 | 10.0245 | 9.6974 | -0.3271
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 520411 | SAWYER4 | 138 | 10.1397 | 10.2056 | 0.065909
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 520918 | FROGVIL4 | 138 | 21.4697 | 10.3341 | -11.1357
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 520948 | HUGO PP4 | 138 | 10.7182 | 21.8945 | 11.1763
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521044 | RUSSETT4 | 138 | 8.0346 | 11.0643 | 3.0297
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521067 | TEXOMAJ4 | 138 | 8.2098 | 8.254 | 0.044239
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521079 | VALLANT4 | 138 | 10.5586 | 8.347 | -2.2117
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521122 | HOWE 4 | 138 | 8.0914 | 10.8863 | 2.7949
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521125 | CHEEK_4 | 138 | 10.6309 | 8.4635 | -2.1674
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 521157 | HUGO 7 | 345 | 20.4948 | 10.8675 | -9.6273
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 525830 | TUCO_INT 6 | 230 | 11.6837 | 20.5682 | 8.8845
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 525832 | TUCO_INT 7 | 345 | 11.5973 | 11.7396 | 0.14228
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 525850 | ELK_CT1 | 345 | 8.4307 | 11.6528 | 3.2221
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 526936 | YOAKUM_345 | 345 | 6.3304 | 8.4476 | 2.1173
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 529304 | OMDUNCN4 | 138 | 7.4174 | 6.41 | -1.0074
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 560078 | G16-037-TAP | 345 | 7.3408 | 7.4846 | 0.14375
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 560088 | G16-063-TAP | 345 | 6.1782 | 7.6856 | 1.5074
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 563259 | GEN-2015-092 | 345 | 9.5941 | 6.504 | -3.0901
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 563269 | GEN-2015-093 | 345 | 6.8592 | 9.7168 | 2.8577
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 584780 | GEN-2015-036 | 345 | 7.2554 | 7.189 | -0.066466
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 587430 | GEN-2016-063 | 345 | 12.7848 | 7.5937 | -5.1911
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 587740 | GEN-2016-091 | 345 | 14.3565 | 13.0105 | -1.346
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 587744 | G16-091-TAP | 345 | 10.6216 | 14.6201 | 3.9985
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 587770 | GEN-2016-095 | 345 | 11.0052 | 10.7956 | -0.20958
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 587794 | G16-097-TAP | 138 | 10.1033 | 11.1058 | 1.0025
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 588839 | FIREWHL-TAP | 345 | 5.0996 | 10.1975 | 5.0979
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 590001 | OKLEHV24 | 138 | 5.2228 | 5.0978 | -0.125
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 590003 | OKLEHV14 | 138 | 4.3113 | 5.221 | 0.90963
GEN-2020-074 & GEN-2020-085 | 07 - Southwestern Oklahoma | 599891 | OKLAUN 7 | 345 | 4309.7896 | 4.3098 | -4305.4798
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X