## Executive Summary
Executive Summary: Group 9 Limited Operation & Interim Availability Interconnection System Impact Study
Interconnection Customer (GEN-2020-025, GEN-2020-028, GEN-2020-043, GEN-2020-044 & GEN-2020-045) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by or within a three (3) year extension of the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades. This amount is a preliminary calculation which includes all pending higher queued Interconnection Requests and previously assigned upgrades that requires further study to substantiate. Interconnection Customers are notified of these preliminary Limited Operation amounts with the posting of the DISIS report.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Sensitivity Dispatch Tab; added to identify diapatch variations from DISIS manual
- Stability Analysis Tab; added to include Stability analysis events and results
- Short Circuit Analysis Tab; added to include Short Circuit analysis results for year 10 summer peak case only
Models Used in Study
Power Flow Analysis: 2019 ITP Series
Light: 2024 (24L)
Summer: 2020 (20SP), 2024 (24SP), 2029 (29SP)
Spring: 2020 (20G)
Winter: 2019 (19WP), 2024 (24WP)
Stability analysis: 2018 Series MDWG Dynamics
Light: 2021 (21L)
Summer: 2021 (21SP), 2028 (28SP)
Winter: 2019 (19WP)
Short Circuit Analysis: 2018 Series MDWG Dynamics
Summer: 2028 (28SP)
Author: SPP Generator Interconnection Department
Published: 07/21/2022

## Revision History
Revision History
Date | Author | Change Description
2022-07-21 | SPP | Posted to SPP website

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Service | Area | POI | Status | Reactive Compensation Requirements
GEN-2020-025 | 09 - Nebraska | NA | NA | Thermal (CT) | 255 | 222.4435 | ER/NR | OPPD | Substation 1363; 161kV Substation | IASIS Stage | 1
GEN-2020-028 | 09 - Nebraska | NA | NA | Thermal (CT) | 255 | 222.4435 | ER/NR | OPPD | Substation 1363; 161kV Substation | IASIS Stage | 1
GEN-2020-043 | 09 - Nebraska | NA | NA | Thermal Reciprocating Engine | 56.52 | 56.52 | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | IASIS Stage | 0.374
GEN-2020-044 | 09 - Nebraska | NA | NA | Thermal Reciprocating Engine | 56.52 | 56.52 | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | IASIS Stage | 0.374
GEN-2020-045 | 09 - Nebraska | NA | NA | Thermal Reciprocating Engine | 56.52 | 56.52 | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | IASIS Stage | 0.374
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 2.5 | 0 | ER | SPS | Wolfforth 115kV | Exclude
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 4.2 | 0 | ER/NR | SPS | SPS Erskine 115kV | Exclude
GEN-2016-005 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | SUNC | Clark-Thistle 345kV | Exclude
GEN-2016-034 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 90 | 0 | ER | WAPA | Laramie River Station (GEN-2016-023 Tap)-Sidney 345kV | Exclude
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | AEPW | Chisholm-Gracemont 345kV | Exclude
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | 0 | ER | SPS | Swisher 115kV | WITHDRAWN
GEN-2016-049 | 03 - Spearville | 18 | DIS-17-1 | Wind | 310.2 | 55.8 | ER | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 300 | 0 | ER | OKGE | Renfrow 345kV | Exclude
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 54 | 0 | ER/NR | SPS | Lakeview-Brownfield 69kV line | Exclude
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 108 | 0 | ER/NR | SPS | Bailey County 115kV | Exclude
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | SPS | Yoakum-Seagraves 115kV circuit | Exclude
GEN-2016-093 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 70 | 0 | ER | NPPD | Bobcat 115kV | Exclude
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 250.7 | 0 | ER/NR | WAPA | Fort Thompson-Leland Olds 345kV | WITHDRAWN
GEN-2016-107 | 01 - Woodward | 18 | DIS-17-1 | Wind | 141.75 | 0 | ER/NR | WFEC | Okeene-Cederdale 138kV Line | Exclude
GEN-2016-109 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | NPPD | Fairbury 115kV | Exclude
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER/NR | AEPW | Shidler 138kV | Exclude
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | 0 | ER/NR | NPPD | Turtle Creek 345kV | Exclude
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 64 | 0 | ER | SPS | Hobbs-Yoakum 230kV | Exclude
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | 0 | ER | SPS | Newhart 115kV | Exclude
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 42 | 0 | ER/NR | WERE | Creswell 69kV Sub | Exclude
GEN-2017-001 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 250 | 0 | ER/NR | NPPD | Sweetwater 345kV | Exclude
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SUNC | Elm Creek - Summit 345kV | Exclude
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 195 | 0 | ER | WERE | Marmaton - Litchfield 161kV | Exclude
GEN-2017-006 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 73.6 | 0 | ER | NPPD | Moore (GEN-2015-088 Tap)-Pauline 345kV | Exclude
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | 0 | ER | SPS | Pleasant Hill 230kV sub | Exclude
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | 23 | ER | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | Exclude
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302.5 | 0 | ER | WERE | Neosho - Caney River 345kV | Exclude
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | WAPA | Rhame 230kV Sub | Exclude
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 0 | ER/NR | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | Exclude
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SPS | Newhart-Potter County 230kV | Exclude
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Mingo 345kV | Exclude
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Underwood - Philip Tap 230kV | Exclude
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 190 | 21.5 | ER/NR | SUNC | Thistle 345kV sub | Exclude
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 0 | ER/NR | WERE | Altoona- NE Parson 138kV | Exclude
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 0 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | Exclude
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | WFEC | Frogville 138kV sub | Exclude
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | 8 | ER/NR | SPS | Tolk 230kV | Exclude
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 0 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | Exclude
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | OKGE | El Reno SW 138kV switch station | Exclude
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | 0 | ER | NPPD | Wildhorse - Covalt 115kV | Exclude
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SPS | Finney - Lamar 345kV | Exclude
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | WFEC | Snyder 138kV | Exclude
GEN-2017-037 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 20 | 0 | ER | NPPD | Bobcat 115kV | Exclude
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | SPS | Needmore 230kV sub | Exclude
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | SPS | Cole 115kV | Exclude
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Neset 230kV | Exclude
GEN-2017-049 | 03 - Spearville | 18 | DIS-17-1 | Solar | 50 | 0 | ER | MIDW | Tap Pawnee Valley - Hanston 69kV | Exclude
GEN-2017-050 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 25 | 0.6 | ER | WERE | Tap Neosho â€“ Crawford 69kV | Exclude
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | 2.6 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | Exclude
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | 0 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | Exclude
GEN-2017-053 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 50 | 8.9 | ER | WFEC | Tap Hollister SW - PSO Walters 69kV | Exclude
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | 0 | ER/NR | LES | Wagener 115kV Sub | Exclude
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Hosston 69kV | Exclude
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | 27 | ER | SPS | Hereford Northeast 115kV | Exclude
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | 0 | ER/NR | SPS | TUCO 230kV | Exclude
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 29.9 | ER | EMDE | LaRussell Energy Center 161kV | Exclude
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 0 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | Exclude
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 0 | ER/NR | WAPA | Underwood - Wayside 230kV | Exclude
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | Exclude
GEN-2017-066 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 150.75 | 0 | ER/NR | WFEC | Oney 138kV Sub | Exclude
GEN-2017-067 | 01 - Woodward | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | OKGE | Minco 345kV | Exclude
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | ER/NR | WERE | Wichita 345kV | Exclude
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 3.6 | 0 | ER/NR | SPS | Norton 115kV Switching Station | Exclude (-3.6)
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | OKGE | Greenwood 138kV sub | Exclude
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | GRDA | Dry Gulch 161kV sub | Exclude
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Pryor Junction 138kV sub | Exclude
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 0 | ER/NR | OKGE | Hugo-Sunnyside 345kV | Exclude
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | AEPW | Chamber Springs 161kV sub | Exclude
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | AEPW | Explorer Claremore Tap EXCLART4 | Exclude
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | Exclude
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 49.88 | 0 | ER | SPS | Hart Industrial 115kV sub | Exclude
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | 0 | ER | SPS | Tolk 230kV | Exclude
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 300 | 0 | ER | SPS | Amarillo South-Swisher 230kV | Exclude
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 28.8 | ER | EMDE | Asbury Plant 161kV | Exclude
GEN-2017-083 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 100 | 0 | ER/NR | SUNC | Mingo 115kV | WITHDRAWN
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 89.25 | 0 | ER | SPS | Newhart-Swisher 230kV | Exclude
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0 | ER/NR | NPPD | Friend 115kV | Exclude
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | WERE | Viola 345kV | Exclude
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | SPS | Clovis Interchange 115kV | Exclude
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 150 | ER | KCPL | Adrian 161kV sub | Exclude
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 26.25 | 0 | ER | SPS | Lamton 115kV | Exclude
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | Exclude
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | WAPA | Fort Thompson-Huron 230kV | Exclude
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | Exclude
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | WAPA | Underwood 115kV Sub | Exclude
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | Exclude
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 0 | ER/NR | SPS | Texas County 115kV | Exclude
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | 0 | ER/NR | SPS | Hobbs 230kV | Exclude
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
AshburyRetired | 08 - North Oklahoma/South Central Kansas | 17.5 | DIS-17-1-PQ | Retired Coal | 198 |  | ER | EMDE | Asbury Plant 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  | ER | WAPA
ASGI-2016-009 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 3 |  | ER | SPS | Wolfforth 12.47kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | WITHDRAWN
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | WITHDRAWN
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | WITHDRAWN
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-135 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-136 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-140 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-143 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-144 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-002 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.35 |  | ER | SPS | SP-Yuma 115kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 0 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
ASGI-2015-006 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Solar | 9 |  | ER | SWPA | Tupelo 138kV
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Nelson 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  | ER/NR | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  | ER | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-029 | 01 - Woodward | 14 | DIS-15-1 | Wind | 161 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/ON SCHEDULE
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  | ER | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  | ER | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  | ER | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-030 | 02 - Hitchland | 11 | DIS-13-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  | ER | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 30 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  | ER | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  | ER | SPS | Pleasant Hill 69kV | Commerical Operation
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  | ER | SPS | Herring 115kV | Commerical Operation
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  | ER | SPS | Hendricks 69kV | Commerical Operation
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commerical Operation
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commerical Operation
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  | ER | WERE | Westar 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  | ER | AECI | Remington 138kV | GIA Executed
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  | ER | SPS | Martin 115kV | Commerical Operation
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  | ER | OTP
Note on G2: Based on Min MW Availablity in the NR and ER scenarios (See sheet "Scenarios")

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Priority | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Capacity or Upgrade Details | Scenario 1: Status or Available MW | Scenario 2: Status or Available MW
GEN-2020-025 | DISIS-2020 | NA | NA | ERIS/NRIS | Substation 1363; 161kV Substation | Interim Study | 255 | 222.4435 | 0
GEN-2020-028 | DISIS-2020 | NA | NA | ERIS/NRIS | Substation 1363; 161kV Substation | Interim Study | 255 | 222.4435 | 0
GEN-2020-043 | DISIS-2020 | NA | NA | ERIS/NRIS | Between Substation 1209 and 1252; 161kV | Interim Study | 56.52 | 56.52 | 0
GEN-2020-044 | DISIS-2020 | NA | NA | ERIS/NRIS | Between Substation 1209 and 1252; 161kV | Interim Study | 56.52 | 56.52 | 0
GEN-2020-045 | DISIS-2020 | NA | NA | ERIS/NRIS | Between Substation 1209 and 1252; 161kV | Interim Study | 56.52 | 56.52 | 0
50442 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. - Gentleman 345 kV Ckt 1 | NA | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50444 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. Substation 345 kV | NA | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50445 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. - Holt Co. 345 kV Ckt 1 | NA | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50446 (NTC 200220) | ITP10 | NA | NA | NA | Holt Co. Substation 345 kV | NA | Build new Holt County 345 kV substation tap on the Grand Island - Fort Thompson 345 kV line owned by WAPA. Install necessary terminal equipment at new substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | In-Service | In-Service
112381 (NTC 210542) | 2019 ITP | NA | NA | NA | Bailey - Seneca 115kV Ckt 1 | NA | Rebuild 6.03 miles of 115 kV line from Baileyville to S Seneca and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
112382 (NTC 210542) | 2019 ITP | NA | NA | NA | Bailey - Smittyville 115kV Ckt 1 | NA | Rebuild 7.99 miles of 115 kV line from Baileyville to Smittyville and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
112383 (NTC 210542) | 2019 ITP | NA | NA | NA | Marshallville - Smittyville 115kV Ckt 1 | NA | Rebuild 2.17 miles of 115 kV line from Marshall County to Smittyville and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
122699 | DISIS-2016-002 | NA | NA | NA | Antelope - Holt 345kV CKT1 (DISIS-2016-002-2) | NA | Build approximately 30 miles of 345kV from Antelope - Holt with a minimum emergency of 1793MVA | Not In-Service | Not In-Service
122700 | DISIS-2016-002 | NA | NA | NA | Keystone - Red Willow 345kV CKT1 (DISIS-2016-002-2) | NA | Build 110 miles of 345kV from Keystone - Red Willow 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
122701 | DISIS-2016-002 | NA | NA | NA | Post Rock - Red Willow 345kV (DISIS-2016-002-2) | NA | Build 150 miles of 345kV line from Red Willow - Postrock 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
122704 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT1 (DISIS-2016-002-2) | NA | Replace Ft. Thompson 345/230kV Transformer CKT 1 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
122711 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT2 (DISIS-2016-002-2) | NA | Replace Ft. Thompson 345/230kV Transformer CKT 2 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
143215 | DISIS-2017-001-P2 | NA | NA | NA | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | NA | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | Not In-Service | Not In-Service
143227 | DISIS-2017-001-P2 | NA | NA | NA | Cooper Joe 345kV New Substation (DISIS-2017-001) | NA | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | Not In-Service | Not In-Service
143212 | DISIS-2017-001-P2 | NA | NA | NA | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | NA | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | Not In-Service | Not In-Service
143214 | DISIS-2017-001-P2 | NA | NA | NA | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | NA | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | Not In-Service | Not In-Service
143217 | DISIS-2017-001-P2 | NA | NA | NA | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | NA | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | Not In-Service | Not In-Service
143218 | DISIS-2017-001-P2 | NA | NA | NA | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | NA | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | Not In-Service | Not In-Service
143258 | DISIS-2017-001-P2 | NA | NA | NA | Dixon County to Twin Church 230kV Rebuild (DISIS-2017-001) | NA | Rebuild the existing Dixon County to Twin Church 230kV 27.7 mile line to achieve a minimum light/emergency rating of 325 MVA | Not In-Service | Not In-Service
133063 | DISIS-2017-001-P2 | NA | NA | NA | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | Not In-Service | Not In-Service
133062 | DISIS-2017-001-P2 | NA | NA | NA | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | Not In-Service | Not In-Service
143200 | DISIS-2017-001-P2 | NA | NA | NA | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | NA | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA | Not In-Service | Not In-Service
143205 | DISIS-2017-001-P2 | NA | NA | NA | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | NA | Build approximately 80 miles of new 345kV line from Keystone to Sidney | Not In-Service | Not In-Service
143234 | DISIS-2017-001-P2 | NA | NA | NA | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | NA | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2 | Not In-Service | Not In-Service
132945 | DISIS-2017-001-P2 | NA | NA | NA | Moore - Pauline 345 kV GEN-2017-008 Interconnection (Non-Shared NU) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | Not In-Service | Not In-Service
132944 | DISIS-2017-001-P2 | NA | NA | NA | Moore - Pauline 345 kV GEN-2017-008 Interconnection (TOIF) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | Not In-Service | Not In-Service
143252 | DISIS-2017-001-P2 | NA | NA | NA | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | NA | Install a new 345/230kV Transformer at Potter County | Not In-Service | Not In-Service
143231 | DISIS-2017-001-P2 | NA | NA | NA | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | NA | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2 | Not In-Service | Not In-Service
132927 | DISIS-2017-001-P2 | NA | NA | NA | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (Non-Shared NU) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | Not In-Service | Not In-Service
132926 | DISIS-2017-001-P2 | NA | NA | NA | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (TOIF) (NPPD) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | Not In-Service | Not In-Service
133011 | DISIS-2017-001-P2 | NA | NA | NA | Wagener 115 kV Substation GEN-2017-055 Interconnection (Non-Shared NU) (LES) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | Not In-Service | Not In-Service
133010 | DISIS-2017-001-P2 | NA | NA | NA | Wagener 115 kV Substation GEN-2017-055 Interconnection (TOIF) (LES) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | Not In-Service | Not In-Service
132979 | DISIS-2017-001-P2 | NA | NA | NA | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (Non-Shared NU) (TSGT) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | Not In-Service | Not In-Service
132978 | DISIS-2017-001-P2 | NA | NA | NA | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (TOIF) (TSGT) | NA | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | Not In-Service | Not In-Service
TBD | DISIS-2017-001-P1 | NA | NA | NA | Seneca to Bailyville to Smittyville to Marshall County 115kV CKT 1 Rebuild | NA | NTC 210542 | Not In-Service | Not In-Service
122699 | DISIS-2016-002-2 | NA | NA | NA | Antelope - Holt 345kV CKT1 (DISIS-2016-002-2) | NA | Build approximately 30 miles of 345kV from Antelope - Holt with a minimum emergency of 1793MVA | Not In-Service | Not In-Service
122700 | DISIS-2016-002-2 | NA | NA | NA | Keystone - Red Willow 345kV CKT1 (DISIS-2016-002-2) | NA | Build 110 miles of 345kV from Keystone - Red Willow 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
122701 | DISIS-2016-002-2 | NA | NA | NA | Post Rock - Red Willow 345kV (DISIS-2016-002-2) | NA | Build 150 miles of 345kV line from Red Willow - Postrock 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
Note on J2: Note1: extremly low voltage issues were observed in the NR00 cases, prior to inclusion of the study project and higher queued projects. Due to this issue, the NR00 BC and TC cases could not be developed. In discussion with SPP, in order to overcome this, dummy switched shunts were placed in the model in areas KCPL, ALTW and MEC to raise the voltages at 345kV to 0.95pu. The study results for these cases are subject to installment of these switched shunts or other mitigation low voltage plans in the aformentioned areas. Note 2: Irrespective to Note1 issue, the results indicates 0 MW availablity at the POIs of the study projects in the Scenario 2 (NR).

## Constraints Summary
SCENARIO | Generation Interconnection Number | Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading % | TC Voltage | VMIN | VMAX | Impact Study Mitigation | Seasons in BC | Footprint | count in ER | count in NR
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 24L | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | 641 | 641 | 122.13 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 1 to minimum 783MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997475 DGG9T1 161 1 | 29SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 108.41 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 759MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603110 TERMINL7 115 997649 90198-B 115 10 | 29SP | P23:345:XEL:8P33 KOL | 672 | 734 | 113.3 |  |  |  | Upgrade TERMINL7 - 90198-B 115kV ckt 10 to minimum 832MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 29SP 24WP 24SP 19WP | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | 233 | 233 | 121.22 |  |  |  | Upgrade ADAMS 5 - HAYWARD L1 5 161kV ckt 1 to minimum 283MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 19WP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 109.38 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 77MVA RateB rating. | 19WP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601024 TERMINL3 345 997649 90198-B 115 10 | 29SP | P23:345:XEL:8P33 KOL | 672 | 734 | 111.11 |  |  |  | Upgrade TERMINL3 345/115kV ckt 10 to minimum 816MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 20G | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 400 | 440 | 104.54 |  |  |  | Upgrade SIBLEY 7 345/161kV ckt 11 to minimum 460MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 29SP | P23:345:MEC:OAK GROVE 901 | 180 | 180 | 111.58 |  |  |  | Upgrade KPECKTP5 - SB 112 5 161kV ckt 1 to minimum 201MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 29SP 24SP | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | 280 | 308 | 120.06 |  |  |  | Upgrade 5PALMYR_AI - 5MARBLE N 161kV ckt 1 to minimum 370MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 20SP 29SP 24SP | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | 201 | 221 | 118.11 |  |  |  | Upgrade SENECA 5 - GRANGRAE 161kV ckt 1 to minimum 262MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 7
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 24L | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | 641 | 641 | 122.13 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 2 to minimum 783MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 29SP | P23:345:MEC:LOUISA 924 | 956 | 1152 | 106.06 |  |  |  | Upgrade SB 56 3 - WALCOTT3 345kV ckt 1 to minimum 1222MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1: 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | 162 | 162 | 108.92 |  |  |  | Upgrade 5MT HOME - 5SOUTHLAND# 161kV ckt 1 to minimum 177MVA RateB rating. | 29SP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 24WP 19WP 20G | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 120 | 131 | 237.09 |  |  |  | Upgrade BEULAH 7 - COYOTE 7 115kV ckt 1 to minimum 311MVA RateB rating. | 24WP 19WP 20G | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631048 EMERY 5 161 631202 COLBY5 161 1 | 29SP 24SP | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | 327 | 327 | 116.88 |  |  |  | Upgrade EMERY 5 - COLBY5 161kV ckt 1 to minimum 383MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 29SP 24WP 24SP 19WP | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | 1016 | 1016 | 112.46 |  |  |  | Upgrade NEOSHO 7 - LACYGNE7 345kV ckt 1 to minimum 1143MVA RateB rating. | 29SP 24WP 19WP | Internal | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 118.5 |  |  |  | Upgrade 4E_OPELUSAS! - 4CHAMPAGNE! 138kV ckt 1 to minimum 267MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 24WP 19WP | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | 641 | 641 | 105.64 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 1 to minimum 678MVA RateB rating. | 24WP 19WP | External | 6 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 20SP 29SP 24SP | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 109.52 |  |  |  | Upgrade 2STURGN 69/161kV ckt 2 to minimum 28MVA RateB rating. | 20SP 29SP 24SP | External | 5 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 24L 20G | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | 864 | 864 | 108.22 |  |  |  | Upgrade LAKEFLD3 - OBRIEN 3 345kV ckt 1 to minimum 936MVA RateB rating. | 24L 20G | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 24SP 24L 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 325 | 325 | 106.86 |  |  |  | Upgrade DMOINES5 - RISING SUN 5 161kV ckt 1 to minimum 348MVA RateB rating. | 24L | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 20SP | Base Case | 800 | 1084 | 107.16 |  |  |  | Upgrade ARROWHD4 - AWHD PST 230kV ckt 1 to minimum 858MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 20SP | P13:69-115-13:GRE-XEL-XEL:AUTO-SINGLE:GRE-STBONI8:GRE-STBONI7:GRE-STBONI2T:2 | 70 | 70 | 103.94 |  |  |  | Upgrade GRE-ST BONI7 115/69kV ckt 1 to minimum 73MVA RateB rating. | 20SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 29SP 24SP | P23:345:XEL:8M53 SCO | 321.9 | 321.9 | 108.99 |  |  |  | Upgrade GRE-PANTHER4 - HUC-MCLEOD 4 230kV ckt 1 to minimum 351MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 235 | 235 | 100.59 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 1 to minimum 237MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 29SP | P12:138:GRDA:CLEVLND-COLLINS | 56 | 56 | 100.17 |  |  |  | Upgrade 2FAIRFAX 69/138kV ckt 1 to minimum 57MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 346156 1HITT 34.5 344270 5HITT 161 1 | 20SP 29SP 24SP | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | 56 | 56 | 112.36 |  |  |  | Upgrade 1HITT 35/161kV ckt 1 to minimum 63MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 20G | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 400 | 440 | 104.54 |  |  |  | Upgrade SIBLEY 7 345/161kV ckt 11 to minimum 460MVA RateB rating. | 20G | Internal | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 20SP 29SP 24WP 24SP 19WP | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 117.68 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 2 to minimum 30MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 606 | 606 | 106.51 |  |  |  | Upgrade 5FAIRPT 161/345kV ckt 3 to minimum 646MVA RateB rating. |  | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 29SP 24SP 24L 20G | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | 171 | 171 | 120.88 |  |  |  | Upgrade WAPELLO5 - APANOSE5 161kV ckt 1 to minimum 207MVA RateB rating. | 29SP 24L 20G | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 681519 STONEMAN 161 699010 NED 161 161 1 | 20SP 24SP | Base Case | 201 | 221 | 104.44 |  |  |  | Upgrade STONEMAN - NED 161 161kV ckt 1 to minimum 210MVA/263MVA RateA/RateB rating. | 20SP 24SP | External | 14 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 618600 GRE-MCGREGR7 115 618601 GRE-KIMBRLY7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 102.01 |  |  |  | Upgrade GRE-MCGREGR7 - GRE-KIMBRLY7 115kV ckt 1 to minimum 87MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 29SP 24SP 24L | P23:345:XEL:8S23 WLM | 168 | 168 | 130.46 |  |  |  | Upgrade RUTLAND5 - FOX LK 5 161kV ckt 1 to minimum 220MVA RateB rating. | 29SP 24SP 24L | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 24WP 24SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 117.17 |  |  |  | Upgrade GRE-CHUBLAK7 - CHL345-115-1 115kV ckt 1 to minimum 525MVA RateB rating. | 24WP 24SP | External | 0 | 4
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 602021 EAU CLA5 161 997642 EAU CL 3 161 9 | 24WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 106.05 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 355MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 29SP 24WP 20G | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 162 | 162 | 151.87 |  |  |  | Upgrade VIELE 5 - DENMARK5 161kV ckt 1 to minimum 247MVA RateB rating. | 29SP 24WP | External | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 29SP | P23:500:EMI:ABF_MCKNT-C | 1200 | 1200 | 100.1 |  |  |  | Upgrade 8BOGALUS - 8FRANKLIN% 500kV ckt 1 to minimum 1202MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 24WP 19WP | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1055 | 1319 | 104.02 |  |  |  | Upgrade GRIMES 3 - SYCAMOR3 345kV ckt 1 to minimum 1373MVA RateB rating. | 24WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 20SP 29SP 24WP 24SP 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 120.8 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 1 to minimum 701MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 281.6 | 281.6 | 120.4 |  |  |  | Upgrade COON CK7 - TWIN LK7 115kV ckt 1 to minimum 340MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 29SP 24WP 24SP 24L 20G | P23:345:ITCM:HCKRYCK:FUT2 | 325 | 325 | 172.33 |  |  |  | Upgrade LORE 5 - HCKRYCK5 161kV ckt 1 to minimum 561MVA RateB rating. | 29SP 24WP 24L 20G | External | 0 | 13
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 29SP 24WP 24SP 19WP | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | 1195 | 1195 | 110.25 |  |  |  | Upgrade STRANGR7 - IATAN 7 345kV ckt 1 to minimum 1318MVA RateB rating. | 24WP | Internal | 0 | 9
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | 446 | 446 | 104.64 |  |  |  | Upgrade SIBLEY 5 - SIBLEYPL 161kV ckt 1 to minimum 467MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 104.05 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 2 to minimum 274MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 138.53 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 1 to minimum 582MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 29SP | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | 339 | 339 | 103.83 |  |  |  | Upgrade 6ESSO% - 6DELMONT 230kV ckt 1 to minimum 352MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997049 GLENHAM TR1 115 1 | 29SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 113.07 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 345221 5MOBERLY 161 345409 5OVERTON 161 1 | 29SP | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | 204 | 242 | 100.95 |  |  |  | Upgrade 5MOBERLY - 5OVERTON 161kV ckt 1 to minimum 245MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | 20G | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | 864 | 864 | 105.2 |  |  |  | Upgrade OBRIEN 3 - HIGHLND 3 345kV ckt 1 to minimum 909MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.7 |  |  |  | Upgrade ST JOE 3 345/161kV ckt 33 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 29SP 24WP 19WP | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | 41.7 | 60 | 107.19 |  |  |  | Upgrade MONONA 5 161/69kV ckt 1 to minimum 65MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 29SP 24SP | Base Case | 78 | 85.8 | 105.95 |  |  |  | Upgrade CLOQUET7 - GRE-KNFFLTP7 115kV ckt 1 to minimum 83MVA/120MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 10
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 29SP 24SP 24L 20G | P23:345:MEC:SYCAMORE 905 | 373 | 395 | 123.44 |  |  |  | Upgrade GRIMES 5 - GRNGRTP5 161kV ckt 1 to minimum 488MVA RateB rating. | 29SP 24SP 24L 20G | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608639 MNP-STP7 115 619701 GRE-ALDRICH7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 77 | 84.7 | 100.35 |  |  |  | Upgrade MNP-STP7 - GRE-ALDRICH7 115kV ckt 1 to minimum 85MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 29SP | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 6: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 102.39 |  |  |  | Upgrade GRAVL ISLE 8 69/161kV ckt 5 to minimum 83MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 115.82 |  |  |  | Upgrade 3HENSLEY - 3ARCH ST 115kV ckt 1 to minimum 294MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 523959 POTTER_CO 6 230 998118 WAUK 90343-A 230 1 | 24L | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | 516 | 559 | 105.28 |  |  |  | Upgrade POTTER_CO 6 - WAUK 90343-A 230kV ckt 1 to minimum 589MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 123.32 |  |  |  | Upgrade 6TEZCUCO% - 6IRONMAN% 230kV ckt 1 to minimum 641MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 24SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | 550 | 605 | 111.84 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 677MVA RateB rating. | 24SP | Internal | 0 | 5
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 29SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 111.54 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 79MVA RateB rating. | 29SP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 24WP | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | 239 | 239 | 100.14 |  |  |  | Upgrade CHEMOLT7 - COTTAGE7 115kV ckt 1 to minimum 240MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 24L | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 405 | 405 | 101.43 |  |  |  | Upgrade 6ROMEVL! - 6CONVNT! 230kV ckt 1 to minimum 411MVA RateB rating. | 24L | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 24WP | P23:345:OTP:JAMESTN3:3145:V2020 | 319 | 351 | 102.75 |  |  |  | Upgrade HANKSON4 - WAHPETN4 230kV ckt 1 to minimum 361MVA RateB rating. | 24WP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 29SP 24WP 24SP 19WP | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 251 | 251 | 114.9 |  |  |  | Upgrade 4DELCAMBRE - 4MORIL! 138kV ckt 1 to minimum 289MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 29SP 24WP 24SP 19WP 20G | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | 83.3 | 83.3 | 117.04 |  |  |  | Upgrade WRIGHT 5 161/69kV ckt 1 to minimum 98MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 29SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 121.59 |  |  |  | Upgrade GRE-CHUBLAK7 - CHL345-115-1 115kV ckt 1 to minimum 545MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 24WP 24SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 117.79 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 37MVA RateB rating. | 24WP 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 29SP 24SP | Base Case | 78 | 78 | 109.21 |  |  |  | Upgrade FLDWDTP7 - MDWLNDS7 115kV ckt 1 to minimum 86MVA/122MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 29SP | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | 143.4 | 143.4 | 104.18 |  |  |  | Upgrade YORKTON 4 230/138kV ckt 1 to minimum 150MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 29SP 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 114.36 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 1 to minimum 301MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 24SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 115.56 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 387MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 24L | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 434 | 434 | 107.78 |  |  |  | Upgrade 6CONVNT! - 6FRISCO! 230kV ckt 1 to minimum 468MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 110.55 |  |  |  | Upgrade AITKNMN7 - RVT2BUS7 115kV ckt 1 to minimum 94MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603103 SCOTTCO7 115 997636 SCOTTCO3 115 9 | 24SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 111.95 |  |  |  | Upgrade SCOTTCO7 - SCOTTCO3 115kV ckt 9 to minimum 727MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 29SP 24SP 19WP 20G | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 223 | 223 | 118.12 |  |  |  | Upgrade WAPELLO5 - JEFF 5 161kV ckt 1 to minimum 264MVA RateB rating. | 29SP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 24WP 19WP | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | 61 | 77.8 | 103.5 |  |  |  | Upgrade 2ADAIR 2 69/161kV ckt 1 to minimum 81MVA RateB rating. | 24WP 19WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 24WP 24SP 19WP | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | 74.7 | 74.7 | 108.76 |  |  |  | Upgrade LIME CK L1 5 161/69kV ckt 1 to minimum 82MVA RateB rating. | 24WP 24SP 19WP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | ALL | Base Case | 90 | 90 | 126.79 |  |  |  | Upgrade M-TOWN 7 - BLRSTWN7 115kV ckt 1 to minimum 115MVA/146MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 32
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 20SP 29SP 24WP 24SP 19WP | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | 56 | 56 | 142.36 |  |  |  | Upgrade 2BUTLER 69/161kV ckt 1 to minimum 80MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 15
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.89 |  |  |  | Upgrade ST JOE 3 345/161kV ckt 22 to minimum 357MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EMI-EES:ABF_FRKLN-A | 112 | 112 | 130.93 |  |  |  | Upgrade 3AMITE! - 3GILLSBURG+ 115kV ckt 1 to minimum 147MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 24SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 109.41 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 367MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 29SP 24WP 24SP | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 223 | 223 | 119.8 |  |  |  | Upgrade 5HUNTSDL - 5OVERTON 161kV ckt 1 to minimum 268MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 602021 EAU CLA5 161 997656 EAU CL 3 161 9 | 20G | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 117.74 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 394MVA RateB rating. | 20G | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 24SP | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 56 | 56 | 102.26 |  |  |  | Upgrade 2NOVLTY_SW 69/161kV ckt 1 to minimum 58MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 29SP 24WP 19WP | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | 84 | 84 | 128.05 |  |  |  | Upgrade VIELE 5 161/69kV ckt 1 to minimum 108MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 24SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | 550 | 605 | 116.66 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 706MVA RateB rating. | 24SP | Internal | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 29SP 24SP 24L 19WP 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 311 | 311 | 122.77 |  |  |  | Upgrade POWESHK5 - REASNOR5 161kV ckt 1 to minimum 382MVA RateB rating. | 29SP 24SP 24L 19WP 20G | External | 0 | 20
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 293 | 334 | 105.32 |  |  |  | Upgrade NAVY 5 - TERRACE5 161kV ckt 1 to minimum 352MVA RateB rating. | 24SP | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 24SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 105.33 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 527MVA RateB rating. | 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 20SP 29SP 24WP 24SP 19WP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 478 | 478 | 144.55 |  |  |  | Upgrade GRE-STANTON4 - SQBUTTE4 230kV ckt 1 to minimum 691MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 10 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | ALL | Base Case | 223 | 223 | 142.67 |  |  |  | Upgrade ADAMS 5 - BVR CRK5 161kV ckt 1 to minimum 319MVA/378MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997476 DGG9T1 161 1 | 24SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 101.88 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 714MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 29SP 24WP 24SP | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 104.29 |  |  |  | Upgrade EASTOWN7 - G17-030-TAP 345kV ckt 1 to minimum 1185MVA RateB rating. |  | Internal | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 20SP 29SP 24SP 20G | Base Case | 84 | 84 | 111.05 |  |  |  | Upgrade THOMSON7 - POTLTCH7 115kV ckt 1 to minimum 94MVA/97MVA RateA/RateB rating. | 20SP 29SP 24SP 20G | External | 0 | 12
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 29SP | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 106.19 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 643MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 29SP | P23:500:EMI:ABF_MCKNT-C | 1200 | 1200 | 100.1 |  |  |  | Upgrade 8BOGALUS - 8FRANKLIN% 500kV ckt 1 to minimum 1202MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 24WP 24SP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 137.21 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 769MVA RateB rating. | 24WP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 29SP 24SP | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | 386 | 416 | 109.82 |  |  |  | Upgrade ELEESV 6 - RODEMR 6 230kV ckt 1 to minimum 457MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 29SP 20G | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 258 | 258 | 107.08 |  |  |  | Upgrade TRAER 5 - DYSART 5 161kV ckt 1 to minimum 277MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 24L 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 357 | 390 | 133.2 |  |  |  | Upgrade ST JOE 5 - WOODBIN5 161kV ckt 1 to minimum 520MVA RateB rating. | 24L 20G | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 29SP 24WP 24SP 19WP 20G | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | 307 | 307 | 118.46 |  |  |  | Upgrade WAPELLO5 - OTTUMWA5 161kV ckt 1 to minimum 364MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 29SP 24SP | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470 | 517 | 122.35 |  |  |  | Upgrade ARROWHD4 - FORBES 4 230kV ckt 1 to minimum 633MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 24L | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 434 | 434 | 107.78 |  |  |  | Upgrade 6CONVNT! - 6FRISCO! 230kV ckt 1 to minimum 468MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 20SP 19WP | P13:161-69:EES-EAI:HERGET:AT2 | 100 | 112 | 118.09 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 133MVA RateB rating. | 20SP 19WP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 107.99 |  |  |  | Upgrade 3MABLVALE-E! - 3SARDIS# 115kV ckt 1 to minimum 274MVA RateB rating. | 20G | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 24L 20G | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | 199 | 199 | 111.67 |  |  |  | Upgrade BUNGE 5 - HASTING5 161kV ckt 1 to minimum 223MVA RateB rating. |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 29SP 24WP 24SP 24L 19WP | P23:345:MEC:GRIMES 901 | 1247 | 1319 | 119.24 |  |  |  | Upgrade GRIMES 3 - SYCAMOR3 345kV ckt 2 to minimum 1573MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601055 SCOTTCO3 345 997635 SCOTTCO3 115 9 | 29SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 111.96 |  |  |  | Upgrade SCOTTCO3 345/115kV ckt 9 to minimum 727MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 20SP 29SP 24SP | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | 84 | 84 | 108.07 |  |  |  | Upgrade 2LAMR 69/161kV ckt 1 to minimum 91MVA RateB rating. | 20SP 29SP 24SP | External | 4 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 24L 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 334 | 334 | 148.55 |  |  |  | Upgrade EAST 5 - WOODBIN5 161kV ckt 1 to minimum 497MVA RateB rating. | 24L 20G | Internal | 0 | 4
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 72 | 72 | 104.09 |  |  |  | Upgrade ADAMS 8 69/161kV ckt 1 to minimum 75MVA/100MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 31 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 29SP | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | 227 | 227 | 104.61 |  |  |  | Upgrade 5BIG CK - 5WARENTN 161kV ckt 1 to minimum 238MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | ALL | Base Case | 926 | 1010 | 129.65 |  |  |  | Upgrade BONDRNT3 - MNTZUMA3 345kV ckt 1 to minimum 1201MVA/1337MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 25
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 29SP | P23:345:MEC:OAK GROVE 901 | 180 | 180 | 111.58 |  |  |  | Upgrade KPECKTP5 - SB 112 5 161kV ckt 1 to minimum 201MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 29SP 24SP | P23:345:XEL:8P4 ASK | 229.9 | 252.8 | 103.19 |  |  |  | Upgrade BAYTOWN7 - LONG LK7 115kV ckt 1 to minimum 261MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 29SP 24WP 24SP 19WP 20G | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | 25 | 25 | 127.76 |  |  |  | Upgrade 2STURGN 69/161kV ckt 2 to minimum 32MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 14
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | 100 | 112 | 129.2 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 145MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 29SP 24WP 24SP | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | 84 | 84 | 103.57 |  |  |  | Upgrade 2LAMR 69/161kV ckt 1 to minimum 87MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 20SP 29SP 24WP 24SP 19WP | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 117.6 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 3 to minimum 30MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 29SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 120.94 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 865MVA RateB rating. | 29SP | Internal | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 24SP 24L 19WP 20G | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 325 | 325 | 130.81 |  |  |  | Upgrade REASNOR5 - RISING SUN 5 161kV ckt 1 to minimum 426MVA RateB rating. | 24L 20G | External | 0 | 15
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 29SP | P13:500-161:EES-EAI:ARK_NU:AT3 | 600 | 600 | 100.46 |  |  |  | Upgrade 8P.HILL% 500/161kV ckt 1 to minimum 603MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 345408 7OVERTON 345 345409 5OVERTON 161 1 | 24WP | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | 560 | 560 | 103.89 |  |  |  | Upgrade 7OVERTON 345/161kV ckt 1 to minimum 582MVA RateB rating. | 24WP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 24WP 19WP | P24:345:AMMO::MCCREDIE:1 | 335 | 335 | 111.22 |  |  |  | Upgrade 5OVERTON - 5OVERTON 2 161kV ckt Z to minimum 373MVA RateB rating. | 19WP | External | 6 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 20SP 29SP 24WP 24SP 19WP | Base Case | 50 | 50 | 136.54 |  |  |  | Upgrade 2MARYVL 69/161kV ckt 2 to minimum 69MVA/86MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 21
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 29SP 24SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 102 | 102 | 104.76 |  |  |  | Upgrade COYOTE 7 - WSTMD1 7 115kV ckt 1 to minimum 107MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 20SP 29SP 24WP 24SP 19WP | Base Case | 50 | 50 | 136.54 |  |  |  | Upgrade 2MARYVL 69/161kV ckt 2 to minimum 69MVA/86MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 21
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 29SP 24WP 24SP 19WP 20G | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | 83.3 | 83.3 | 117.04 |  |  |  | Upgrade WRIGHT 5 161/69kV ckt 1 to minimum 98MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 10
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 601028 EAU CL 3 345 997643 EAU CL 3 161 9 | 19WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 114.94 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 385MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 115.08 |  |  |  | Upgrade 5MPLTAP - 5LATHRP 161kV ckt 1 to minimum 262MVA RateB rating. | 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 29SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 121.28 |  |  |  | Upgrade GRE-CHUBLAK3 345/115kV ckt 1 to minimum 544MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 29SP 24SP | P23:345:XEL:8M36 CNC | 1195.1 | 1195.1 | 111.73 |  |  |  | Upgrade COON CK3 - KOLMNLK3 345kV ckt 1 to minimum 1336MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 141.08 |  |  |  | Upgrade 6IRONMAN% - 6GYPSY% 230kV ckt 1 to minimum 733MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 29SP 24SP | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | 56 | 56 | 108.05 |  |  |  | Upgrade 2LOCUST 69/161kV ckt 1 to minimum 61MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 603020 MAPLE R7 115 997612 MAPLE RIVER 69.0 1 | 19WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 121.89 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 171MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 29SP | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 276 | 276 | 122.18 |  |  |  | Upgrade ABBOTT 5 - TRAER 5 161kV ckt 1 to minimum 338MVA RateB rating. | 29SP | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 112.95 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 24WP 24SP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 24SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 101.24 |  |  |  | Upgrade HUC-MCLEOD 4 230/115kV ckt 1 to minimum 190MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 138.53 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 1 to minimum 582MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 24SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | 500 | 500 | 104.35 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 1 to minimum 522MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 20SP 29SP 24WP 24SP 19WP | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 67.2 | 71 | 122.47 |  |  |  | Upgrade BELLCTR5 161/69kV ckt 1 to minimum 87MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603103 SCOTTCO7 115 997635 SCOTTCO3 115 9 | 29SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 114.95 |  |  |  | Upgrade SCOTTCO7 - SCOTTCO3 115kV ckt 9 to minimum 746MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 29SP 24SP 24L 20G | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | 171 | 171 | 120.88 |  |  |  | Upgrade WAPELLO5 - APANOSE5 161kV ckt 1 to minimum 207MVA RateB rating. | 29SP 24L 20G | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 29SP 24WP 24SP | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 109.07 |  |  |  | Upgrade 5CLINTN - 5HOLDEN 161kV ckt 1 to minimum 248MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 106.99 |  |  |  | Upgrade AITKNMN7 - GRE-AITKIN 7 115kV ckt 1 to minimum 91MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 19WP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 123.06 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 690MVA RateB rating. | 19WP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 603020 MAPLE R7 115 997612 MAPLE RIVER 69.0 1 | 19WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 121.89 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 171MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | ALL | Base Case | 252 | 252 | 113.9 |  |  |  | Upgrade 5GENTRY - 5FAIRPT 161kV ckt 1 to minimum 288MVA/272MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 21
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 24L | Base Case | 478 | 478 | 114.12 |  |  |  | Upgrade OTTUMWA3 - MNTZUMA3 345kV ckt 1 to minimum 546MVA/1128MVA RateA/RateB rating. | 24L | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 29SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 109.73 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 549MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 112.95 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 24WP 24SP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 104.05 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 2 to minimum 274MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 29SP 24SP | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1195 | 1209 | 116.2 |  |  |  | Upgrade OAKGROV3 - SUB 93 3 345kV ckt 1 to minimum 1405MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 24L 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 212 | 212 | 120.36 |  |  |  | Upgrade JASPER 5 - NEANKNY5 161kV ckt 1 to minimum 256MVA RateB rating. | 24L 20G | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 20SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 145.48 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 102MVA RateB rating. | 20SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 29SP 24WP | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | 1000 | 1136 | 102.49 |  |  |  | Upgrade IATAN 7 - G17-030-TAP 345kV ckt 1 to minimum 1165MVA RateB rating. |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 223 | 248 | 120.75 |  |  |  | Upgrade TRK RIV5 - STONEMAN 161kV ckt 1 to minimum 270MVA/327MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 16
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 24SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 108.24 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 542MVA RateB rating. | 24SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 24WP 24SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 117.79 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 37MVA RateB rating. | 24WP 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631036 NIW 5 161 631202 COLBY5 161 1 | 20G | P23:345:MEC:BLACK HAWK 901 | 200 | 200 | 108.74 |  |  |  | Upgrade NIW 5 - COLBY5 161kV ckt 1 to minimum 218MVA RateB rating. | 20G | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608639 MNP-STP7 115 619701 GRE-ALDRICH7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 77 | 84.7 | 100.35 |  |  |  | Upgrade MNP-STP7 - GRE-ALDRICH7 115kV ckt 1 to minimum 85MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 29SP 24SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 107.9 |  |  |  | Upgrade 3ELD DONAN - 3ELD MONSNTO 115kV ckt 1 to minimum 172MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 19WP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | 330 | 334.6 | 113.15 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 379MVA RateB rating. | 19WP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 115.82 |  |  |  | Upgrade 3HENSLEY - 3ARCH ST 115kV ckt 1 to minimum 294MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 20SP 29SP 24WP 24SP 19WP | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | 56 | 56 | 142.36 |  |  |  | Upgrade 2BUTLER 69/161kV ckt 1 to minimum 80MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 15
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337753 8HS EHV% 500 337685 3HS EHV-W! 115 1 | 20SP | P23:HV-EHV:EES::8HS EHV%:5 | 550 | 550 | 104.9 |  |  |  | Upgrade 8HS EHV% 500/115kV ckt 1 to minimum 577MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 268.1 | 268.1 | 105.26 |  |  |  | Upgrade RIVRSID7 - BRKLNPK7 115kV ckt 1 to minimum 283MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | 29SP | 92681: 515300 FTSMTHE5 161 515301 FTSMTHW5 161 1 515300 FTSMTHE5 161 515301 FTSMTHW5 161 2 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 515301 FTSMTHW5 161 998255 FTSMITH4 161 4 515301 FTSMTHW5 161 998254 FTSMITH5 161 5 515299 BEVYTAP5 161 515300 FTSMTHE5 161 1 515300 FTSMTHE5 161 515310 QUANXTP5 161 1 515300 FTSMTHE5 161 515345 COLONY 5 161 1 515300 FTSMTHE5 161 998257 FTSMITH3 161 3 515300 FTSMTHE5 161 998256 FTSMTH6 161 6 | 106 | 106 | 103.09 |  |  |  | Upgrade 3CHEETAH% - 3HS VILLAGE 115kV ckt 1 to minimum 110MVA RateB rating. | 29SP | External | 1 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300036 5MPLTAP 161 301310 5REX 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 118 |  |  |  | Upgrade 5MPLTAP - 5REX 161kV ckt 1 to minimum 268MVA RateB rating. | 24L 20G | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 29SP 24SP | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | 336 | 336 | 125.16 |  |  |  | Upgrade 5PALMYR_AI 161/345kV ckt 1 to minimum 421MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 24L | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 203 | 203 | 102.26 |  |  |  | Upgrade 5CHILLI - 5HICKCK 161kV ckt 1 to minimum 208MVA RateB rating. |  | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 24L 20G | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | 864 | 864 | 108.22 |  |  |  | Upgrade LAKEFLD3 - OBRIEN 3 345kV ckt 1 to minimum 936MVA RateB rating. | 24L 20G | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631198 COLBY3 345 631202 COLBY5 161 1 | 29SP 24WP 24SP 19WP 20G | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | 450 | 450 | 110.96 |  |  |  | Upgrade COLBY3 345/161kV ckt 1 to minimum 500MVA RateB rating. | 29SP 24SP 19WP | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | ALL | Base Case | 72 | 72 | 112.77 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 2 to minimum 82MVA/108MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 33
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | ALL | Base Case | 956 | 1010 | 105.66 |  |  |  | Upgrade MNTZUMA3 - DIAMOND TRL3 345kV ckt 1 to minimum 1011MVA/1306MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 29SP 24SP 24L | P23:345:XEL:8S23 WLM | 168 | 168 | 130.46 |  |  |  | Upgrade RUTLAND5 - FOX LK 5 161kV ckt 1 to minimum 220MVA RateB rating. | 29SP 24SP 24L | External | 0 | 10
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | 20SP | Base Case | 325 | 325 | 144.6 |  |  |  | Upgrade 1THLG2 22.0/161kV ckt 1 to minimum 470MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 24WP 19WP 20G | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 92 | 92 | 109.26 |  |  |  | Upgrade 16L TAP7 - COTTNTP7 115kV ckt 1 to minimum 101MVA RateB rating. | 24WP 19WP 20G | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 29SP 24SP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 107.69 |  |  |  | Upgrade 98L TAP4 - ARROWHD4 230kV ckt 1 to minimum 557MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 24SP | Base Case | 144 | 144 | 101.59 |  |  |  | Upgrade HOYT LK7 - 43L TAP7 115kV ckt 1 to minimum 147MVA/150MVA RateA/RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 20SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 108.58 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 543MVA RateB rating. | 20SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 29SP 24WP 24SP 19WP 20G | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | 56 | 56 | 134.34 |  |  |  | Upgrade 2OSBORN 69/161kV ckt 1 to minimum 76MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 24SP | P12:161:DPC:AUTO-SINGLE:GENOA5:HARMONY5:1 | 240 | 264 | 105.05 |  |  |  | Upgrade LANSING L1 5 - GENOA 5 161kV ckt 1 to minimum 278MVA RateB rating. | 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 24SP | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | 70 | 80.5 | 102.98 |  |  |  | Upgrade RIV FLS7 115/69kV ckt 5 to minimum 83MVA RateB rating. | 24SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 29SP 24SP | P23:345:XEL:8M53 SCO | 321.9 | 321.9 | 108.99 |  |  |  | Upgrade GRE-PANTHER4 - HUC-MCLEOD 4 230kV ckt 1 to minimum 351MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 19WP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 122.63 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 687MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 29SP 24WP 24SP 19WP | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | 1016 | 1016 | 112.46 |  |  |  | Upgrade NEOSHO 7 - LACYGNE7 345kV ckt 1 to minimum 1143MVA RateB rating. | 29SP 24WP 19WP | Internal | 0 | 11
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 20G | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 400 | 440 | 105.97 |  |  |  | Upgrade SIBLEY 5 - SIBLEY11 161kV ckt 11 to minimum 467MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 142.02 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 100MVA RateB rating. | 24WP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603150 HOLCOMB7 115 680245 HOLCOMBE 69.0 1 | 24SP | 71613: 605353 CADOTT 8 69.0 605354 BOYD 8 69.0 1 605354 BOYD 8 69.0 605420 DELMAR 8 69.0 1 605351 WISOTBC8 69.0 680482 DPC TAP8 69.0 1 605353 CADOTT 8 69.0 680482 DPC TAP8 69.0 1 605349 WISSOTAG 69.0 605523 LFY TAP8 69.0 1 605351 WISOTBC8 69.0 605523 LFY TAP8 69.0 1 605523 LFY TAP8 69.0 680511 LAFAYETE 69.0 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 605355 STANLEY8 69.0 605420 DELMAR 8 69.0 1 | 46.7 | 54 | 103.71 |  |  |  | Upgrade HOLCOMB7 115/69kV ckt 1 to minimum 57MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 29SP | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 327 | 327 | 109.63 |  |  |  | Upgrade TOLEDO 5 - BL.PLN.5 161kV ckt 1 to minimum 359MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608700 43L TAP7 115 608702 LASKIN 7 115 1 | 24SP | Base Case | 144 | 158.4 | 101.68 |  |  |  | Upgrade 43L TAP7 - LASKIN 7 115kV ckt 1 to minimum 147MVA RateA rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.7 |  |  |  | Upgrade ST JOE 3 345/161kV ckt 33 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631036 NIW 5 161 631202 COLBY5 161 1 | 20G | P23:345:MEC:BLACK HAWK 901 | 200 | 200 | 108.74 |  |  |  | Upgrade NIW 5 - COLBY5 161kV ckt 1 to minimum 218MVA RateB rating. | 20G | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 29SP | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 197 | 197 | 106.84 |  |  |  | Upgrade HENRYCO5 - JEFF 5 161kV ckt 1 to minimum 211MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 29SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 111.53 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 558MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 29SP 24SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 102 | 102 | 104.76 |  |  |  | Upgrade COYOTE 7 - WSTMD1 7 115kV ckt 1 to minimum 107MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 104.22 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 574MVA RateB rating. |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | ALL | Base Case | 72 | 72 | 112.77 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 2 to minimum 82MVA/108MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 33
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 24L | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1210.7 | 1210.7 | 141.53 |  |  |  | Upgrade 8WILLOW_GL% - 8WATERFO 500kV ckt 1 to minimum 1714MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 29SP 24WP 24SP | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | 1195 | 1195 | 108.71 |  |  |  | Upgrade ST JOE 3 - EASTOWN7 345kV ckt 1 to minimum 1300MVA RateB rating. |  | Internal | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681519 STONEMAN 161 699010 NED 161 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 201 | 221 | 126.32 |  |  |  | Upgrade STONEMAN - NED 161 161kV ckt 1 to minimum 254MVA/321MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 16
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 20G | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 400 | 400 | 110.85 |  |  |  | Upgrade OTTUMWA3 345/161kV ckt 1 to minimum 444MVA RateB rating. | 20G | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 24SP | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | 56 | 56 | 102.26 |  |  |  | Upgrade 2NOVLTY_SW 69/161kV ckt 1 to minimum 58MVA RateB rating. | 24SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997055 GLENHAM TR1 115 1 | 20SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 102.54 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 32MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 29SP 24SP | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | 326 | 326 | 115.62 |  |  |  | Upgrade ARNOLD 5 - DWNTWN IND5 161kV ckt 1 to minimum 377MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 29SP 24SP 19WP 20G | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 137.9 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 2 to minimum 35MVA RateB rating. | 29SP 24SP 19WP 20G | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 29SP 24WP 24SP | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 276 | 276 | 122 |  |  |  | Upgrade MURPHY CR 5 - HAYWARD L2 5 161kV ckt 1 to minimum 337MVA RateB rating. | 29SP 24SP | External | 0 | 10
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 129.57 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 146MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 29SP 24WP 24SP 19WP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 188.8 | 220.5 | 113.73 |  |  |  | Upgrade ALDRICH7 - FIFTHST7 115kV ckt 1 to minimum 251MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 29SP | P23:345:GRE:PVS 19JB1 | 500 | 500 | 110.69 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 1 to minimum 554MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 24WP 24SP 20G | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | 1099 | 1202 | 110.56 |  |  |  | Upgrade 87TH 7 - CRAIG 7 345kV ckt 1 to minimum 1329MVA RateB rating. | 20G | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 19WP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 107.61 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 592MVA RateB rating. | 19WP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 345408 7OVERTON 345 345409 5OVERTON 161 1 | 24WP | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | 560 | 560 | 103.89 |  |  |  | Upgrade 7OVERTON 345/161kV ckt 1 to minimum 582MVA RateB rating. | 24WP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608700 43L TAP7 115 608702 LASKIN 7 115 1 | 24SP | Base Case | 144 | 158.4 | 101.68 |  |  |  | Upgrade 43L TAP7 - LASKIN 7 115kV ckt 1 to minimum 147MVA RateA rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 104.22 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 574MVA RateB rating. |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997476 DGG9T1 161 1 | 24SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 101.88 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 714MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 588307 ASGI1706-XFM 34.5 588306 ASGI1706 161 1 | 20SP | Base Case | 104 | 130 | 118.65 |  |  |  | Upgrade ASGI1706-XFM 35/161kV ckt 1 to minimum 124MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 29SP 24WP 24SP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 113.14 |  |  |  | Upgrade 3HENSLEY - 3ARCH ST 115kV ckt 1 to minimum 287MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | ALL | Base Case | 81 | 81 | 103.04 |  |  |  | Upgrade BLRSTWN7 - PRAR CK7 115kV ckt 1 to minimum 84MVA/103MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 34
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 29SP 24WP 24SP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 266 | 266 | 110.3 |  |  |  | Upgrade 3WHT BLUFF! - 3HENSLEY 115kV ckt 1 to minimum 294MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 29SP 20G | P23:345:MEC:LOUISA 964 | 1195 | 1304 | 102.78 |  |  |  | Upgrade HILLS 3 - SUB 92 3 345kV ckt 1 to minimum 1341MVA RateB rating. | 29SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 29SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 120.94 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 865MVA RateB rating. | 29SP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 227 | 227 | 105.4 |  |  |  | Upgrade 5CLINTN - 5HOLDEN 161kV ckt 1 to minimum 240MVA/271MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 26
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 29SP 24WP 24SP 20G | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | 1099 | 1195 | 123.7 |  |  |  | Upgrade STRANGR7 - 87TH 7 345kV ckt 1 to minimum 1479MVA RateB rating. | 29SP 24WP 24SP 20G | Internal | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601055 SCOTTCO3 345 997635 SCOTTCO3 115 9 | 29SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 111.96 |  |  |  | Upgrade SCOTTCO3 345/115kV ckt 9 to minimum 727MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601024 TERMINL3 345 997650 90198-B 115 10 | 24SP | P23:345:XEL:8P33 KOL | 672 | 734 | 109.3 |  |  |  | Upgrade TERMINL3 345/115kV ckt 10 to minimum 803MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 19WP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 122.63 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 687MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 110.55 |  |  |  | Upgrade AITKNMN7 - RVT2BUS7 115kV ckt 1 to minimum 94MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 20G | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 56 | 56 | 101.88 |  |  |  | Upgrade 2HENRY 69/161kV ckt 1 to minimum 58MVA RateB rating. | 20G | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 29SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 104.69 |  |  |  | Upgrade 3ELD DONAN - 3ELD MONSNTO 115kV ckt 1 to minimum 167MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 29SP 24L 20G | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 240 | 240 | 123.88 |  |  |  | Upgrade PARNEL 5 - POWESHK5 161kV ckt 1 to minimum 298MVA RateB rating. | 29SP 24L 20G | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681519 STONEMAN 161 699010 NED 161 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 201 | 221 | 126.32 |  |  |  | Upgrade STONEMAN - NED 161 161kV ckt 1 to minimum 254MVA/321MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 16
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 29SP 24WP 24SP | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 276 | 276 | 122 |  |  |  | Upgrade MURPHY CR 5 - HAYWARD L2 5 161kV ckt 1 to minimum 337MVA RateB rating. | 29SP 24SP | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 24WP 24SP 20G | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | 1099 | 1202 | 110.56 |  |  |  | Upgrade 87TH 7 - CRAIG 7 345kV ckt 1 to minimum 1329MVA RateB rating. | 20G | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 24SP | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | 330 | 330 | 106.37 |  |  |  | Upgrade LORE 5 - TRK RIV5 161kV ckt 1 to minimum 352MVA RateB rating. |  | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 29SP | Base Case | 36 | 36 | 142.71 |  |  |  | Upgrade BL.PLN.5 161/69kV ckt 1 to minimum 52MVA/55MVA RateA/RateB rating. | 29SP | External | 0 | 7
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 143.52 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 2 to minimum 603MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 29SP 24SP | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | 172 | 172 | 115.85 |  |  |  | Upgrade 5SRIVER - 5PALMYR_AI 161kV ckt 1 to minimum 200MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 24WP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 108.77 |  |  |  | Upgrade 3ARCH ST - 3SARDIS# 115kV ckt 1 to minimum 276MVA RateB rating. | 24WP 19WP 20G | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 29SP 24SP 19WP 20G | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 223 | 223 | 118.12 |  |  |  | Upgrade WAPELLO5 - JEFF 5 161kV ckt 1 to minimum 264MVA RateB rating. | 29SP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 24WP | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | 241 | 241 | 101.35 |  |  |  | Upgrade 4STONGAT! - 4MID CO% 138kV ckt 1 to minimum 245MVA RateB rating. | 24WP | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 441 | 441 | 128.58 |  |  |  | Upgrade 6BLPNT! - 6GYPSY% 230kV ckt 1 to minimum 568MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 20SP 29SP 24SP 20G | Base Case | 1000 | 1136 | 101.27 |  |  |  | Upgrade HAWTH 7 - NASHUA 7 345kV ckt 1 to minimum 1013MVA/1354MVA RateA/RateB rating. | 29SP 24SP | Internal | 0 | 11
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 29SP 24WP 24SP 24L 19WP 20G | Base Case | 269 | 269 | 102.8 |  |  |  | Upgrade 5MARYVL - 5NODWAY 161kV ckt 1 to minimum 277MVA/365MVA RateA/RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 17
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 29SP 24WP | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | 96 | 106 | 102.22 |  |  |  | Upgrade RICE 8 69/161kV ckt 1 to minimum 109MVA RateB rating. | 24WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 29SP 24WP 24SP 19WP | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | 117.1 | 118.3 | 132.83 |  |  |  | Upgrade FLOYD 5 161/69kV ckt 1 to minimum 158MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 20SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 108.58 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 543MVA RateB rating. | 20SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 20SP 29SP 24WP 24SP 19WP | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 122.88 |  |  |  | Upgrade 2KOLBS_1! 69/230kV ckt 1 to minimum 196MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 29SP | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | 112 | 140 | 107.56 |  |  |  | Upgrade POPLK_5 161/69kV ckt 1 to minimum 151MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 19WP | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 113.4 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 687MVA RateB rating. | 19WP | Internal | 0 | 4
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 20SP 24WP 24SP 19WP | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 117.51 |  |  |  | Upgrade 6IRONMAN% - 6GYPSY% 230kV ckt 1 to minimum 610MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 20SP 29SP 24WP 24SP 19WP | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 128.03 |  |  |  | Upgrade 2KOLBS_1! 69/230kV ckt 1 to minimum 204MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 20SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 110.8 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 554MVA RateB rating. | 20SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 29SP | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 206 | 206 | 107.67 |  |  |  | Upgrade 4SPLENDR! - 4JACINTO% 138kV ckt 1 to minimum 222MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 19WP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 137.91 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 97MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 20SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 108.36 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 596MVA RateB rating. | 20SP | Internal | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 346156 1HITT 34.5 344270 5HITT 161 1 | 20SP 29SP 24SP | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | 56 | 56 | 112.36 |  |  |  | Upgrade 1HITT 35/161kV ckt 1 to minimum 63MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 29SP 24SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 102 | 102 | 101.93 |  |  |  | Upgrade DIXGREENRVR7 - WSTMD1 7 115kV ckt 1 to minimum 104MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 24SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | 500 | 500 | 104.35 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 1 to minimum 522MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EMI-EES:ABF_FRKLN-A | 112 | 112 | 130.93 |  |  |  | Upgrade 3AMITE! - 3GILLSBURG+ 115kV ckt 1 to minimum 147MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 227 | 227 | 105.4 |  |  |  | Upgrade 5CLINTN - 5HOLDEN 161kV ckt 1 to minimum 240MVA/271MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 26
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 29SP | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | 120 | 120 | 102.22 |  |  |  | Upgrade 3BERNICE - 3JNCTN CITY! 115kV ckt 1 to minimum 123MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 29SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 143.05 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 101MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631048 EMERY 5 161 631202 COLBY5 161 1 | 29SP 24SP | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | 327 | 327 | 116.88 |  |  |  | Upgrade EMERY 5 - COLBY5 161kV ckt 1 to minimum 383MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 24L | Base Case | 478 | 478 | 114.12 |  |  |  | Upgrade OTTUMWA3 - MNTZUMA3 345kV ckt 1 to minimum 546MVA/1128MVA RateA/RateB rating. | 24L | External | 0 | 7
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 128.84 |  |  |  | Upgrade 3WOODWARD% - 3DIERKS! 115kV ckt 1 to minimum 127MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 20SP 29SP 24SP 24L 20G | Base Case | 206 | 206 | 110.64 |  |  |  | Upgrade WRIGHT 5 - WALL LK5 161kV ckt 1 to minimum 228MVA/270MVA RateA/RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 27
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 24SP | Base Case | 78 | 114 | 102.34 |  |  |  | Upgrade THOMSON7 - FONDULAC 115kV ckt 1 to minimum 80MVA/118MVA RateA/RateB rating. |  | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 602021 EAU CLA5 161 997643 EAU CL 3 161 9 | 19WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 118.07 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 396MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1049 | 1049 | 166.19 |  |  |  | Upgrade 8WATERFO 500/230kV ckt 1 to minimum 1744MVA RateB rating. | 24L 19WP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 106.99 |  |  |  | Upgrade AITKNMN7 - GRE-AITKIN 7 115kV ckt 1 to minimum 91MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608642 VERNDLE7 115 615567 GRE-WINGRIV7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 98 | 107.8 | 107.64 |  |  |  | Upgrade VERNDLE7 - GRE-WINGRIV7 115kV ckt 1 to minimum 117MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 29SP 24WP 24SP | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 104.29 |  |  |  | Upgrade EASTOWN7 - G17-030-TAP 345kV ckt 1 to minimum 1185MVA RateB rating. |  | Internal | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 20SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 110.87 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 610MVA RateB rating. | 20SP | Internal | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 20SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 113.77 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 20SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 20SP 29SP 24SP | P12:345:MEC:WALCOTT-HILLS-LOUISA | 80 | 80 | 112.35 |  |  |  | Upgrade PRAR CK7 - SUTLIFF7 115kV ckt 1 to minimum 90MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 9
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 29SP | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | 112 | 140 | 107.56 |  |  |  | Upgrade POPLK_5 161/69kV ckt 1 to minimum 151MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300036 5MPLTAP 161 301310 5REX 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 118 |  |  |  | Upgrade 5MPLTAP - 5REX 161kV ckt 1 to minimum 268MVA RateB rating. | 24L 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 20SP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 148.4 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 104MVA RateB rating. | 20SP | External | 0 | 5
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 127.22 |  |  |  | Upgrade ST JOE 5 - AVENUECTY 5 161kV ckt 1 to minimum 254MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 29SP 24SP | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | 56 | 56 | 103.99 |  |  |  | Upgrade 2HICKRY 69/161kV ckt 1 to minimum 59MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 24L | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | 641 | 641 | 122.13 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 2 to minimum 783MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 20SP | P23:345:XEL:8N22 SHC | 1332.6 | 1332.6 | 101.45 |  |  |  | Upgrade FIELD_S3 - CRANDAL 3 345kV ckt 1 to minimum 1352MVA RateB rating. |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 20SP | 637035 J524 161 3WXFMR J524 1: 637035 J524 161 997470 J524 34.5 1 637032 J524 COL2 34.5 997470 J524 34.5 1 637034 J524 TERT 13.2 997470 J524 34.5 1 | 560 | 560 | 103.38 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 579MVA RateB rating. | 20SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 20SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1210.7 | 1210.7 | 125.55 |  |  |  | Upgrade 8WILLOW_GL% - 8WATERFO 500kV ckt 1 to minimum 1521MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 20SP 29SP 24WP 24SP | Base Case | 92 | 92 | 104.26 |  |  |  | Upgrade GRE-JOHNJCT7 - MORRIS 7 115kV ckt 1 to minimum 96MVA/133MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 18
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 20SP 29SP 24WP 24SP | Base Case | 108 | 108 | 110.38 |  |  |  | Upgrade GRE-JOHNJCT7 - ORTONVL7 115kV ckt 1 to minimum 120MVA/162MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 21
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 20SP 29SP 24SP 24L 20G | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | 200 | 200 | 122.87 |  |  |  | Upgrade HUNTLEY5 - FREEBORN5 161kV ckt 1 to minimum 246MVA RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 11
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 266 | 266 | 113.9 |  |  |  | Upgrade 3WHT BLUFF! - 3HENSLEY 115kV ckt 1 to minimum 303MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603150 HOLCOMB7 115 680245 HOLCOMBE 69.0 1 | 24SP | 71613: 605353 CADOTT 8 69.0 605354 BOYD 8 69.0 1 605354 BOYD 8 69.0 605420 DELMAR 8 69.0 1 605351 WISOTBC8 69.0 680482 DPC TAP8 69.0 1 605353 CADOTT 8 69.0 680482 DPC TAP8 69.0 1 605349 WISSOTAG 69.0 605523 LFY TAP8 69.0 1 605351 WISOTBC8 69.0 605523 LFY TAP8 69.0 1 605523 LFY TAP8 69.0 680511 LAFAYETE 69.0 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 605355 STANLEY8 69.0 605420 DELMAR 8 69.0 1 | 46.7 | 54 | 103.71 |  |  |  | Upgrade HOLCOMB7 115/69kV ckt 1 to minimum 57MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 29SP 24SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 102 | 102 | 101.93 |  |  |  | Upgrade DIXGREENRVR7 - WSTMD1 7 115kV ckt 1 to minimum 104MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 29SP | P12:138:GRDA:CLEVLND-COLLINS | 56 | 56 | 100.17 |  |  |  | Upgrade 2FAIRFAX 69/138kV ckt 1 to minimum 57MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 293 | 318 | 100.3 |  |  |  | Upgrade TERRACE5 - BARBER 5 161kV ckt 1 to minimum 319MVA RateB rating. |  | Internal | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 108.63 |  |  |  | Upgrade 3ARCH ST - 3SARDIS# 115kV ckt 1 to minimum 275MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 29SP 24SP | Base Case | 78 | 85.8 | 105.95 |  |  |  | Upgrade CLOQUET7 - GRE-KNFFLTP7 115kV ckt 1 to minimum 83MVA/120MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 10
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | 100 | 112 | 121.55 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 9
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 19WP | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | 500 | 550 | 110.91 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 611MVA RateB rating. | 19WP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300194 2CHILLI 69.0 300068 5CHILLI 161 2 | 24SP | 300194 2CHILLI 69 300068 5CHILLI 161 1: 300194 2CHILLI 69.0 300068 5CHILLI 161 1 | 56 | 56 | 106.02 |  |  |  | Upgrade 2CHILLI 69/161kV ckt 2 to minimum 60MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 1188.5 | 1188.5 | 105.57 |  |  |  | Upgrade AS KING3 - EAU CL 3 345kV ckt 1 to minimum 1255MVA/1307MVA RateA/RateB rating. | 20SP 24WP 24SP | External | 0 | 12
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 110.74 |  |  |  | Upgrade 3WOODWARD% - 3DIERKS! 115kV ckt 1 to minimum 109MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 29SP 24WP 24SP 24L 19WP 20G | Base Case | 269 | 269 | 102.8 |  |  |  | Upgrade 5MARYVL - 5NODWAY 161kV ckt 1 to minimum 277MVA/365MVA RateA/RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 17
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 601028 EAU CL 3 345 997642 EAU CL 3 161 9 | 24WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 104.36 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 350MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 29SP 20G | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | 240 | 240 | 111.14 |  |  |  | Upgrade BARTON5 - LIME CK L2 5 161kV ckt 1 to minimum 267MVA RateB rating. | 29SP 20G | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 20SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 108.36 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 596MVA RateB rating. | 20SP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 20SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 110.87 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 610MVA RateB rating. | 20SP | Internal | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 24WP 19WP | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | 641 | 641 | 105.64 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 1 to minimum 678MVA RateB rating. | 24WP 19WP | External | 6 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 20SP | P23:500:EES-EAI:ARK_NU:B5106 | 396 | 396 | 112.01 |  |  |  | Upgrade 5RUSSELVL.E! - 5RUSSELVL.N 161kV ckt 1 to minimum 444MVA RateB rating. | 20SP | External | 3 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 602021 EAU CLA5 161 997646 EAU CL 3 161 9 | 24L | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 108.17 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 362MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 112.16 |  |  |  | Upgrade 4E_OPELUSAS! - 4COLTON 138kV ckt 1 to minimum 253MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 24WP | P12:345:WERE:STRA-IATAN_345_1:: | 1195 | 1195 | 102.38 |  |  |  | Upgrade STRANGR7 - IATAN 7 345kV ckt 2 to minimum 1224MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300194 2CHILLI 69.0 300068 5CHILLI 161 2 | 24SP | 300194 2CHILLI 69 300068 5CHILLI 161 1: 300194 2CHILLI 69.0 300068 5CHILLI 161 1 | 56 | 56 | 106.02 |  |  |  | Upgrade 2CHILLI 69/161kV ckt 2 to minimum 60MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 29SP 24L | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 150 | 150 | 106.58 |  |  |  | Upgrade MPWSPLIT - DENMARK5 161kV ckt 1 to minimum 160MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | ALL | Base Case | 262 | 288 | 111.07 |  |  |  | Upgrade WABACO 5 - ROCHSTR5 161kV ckt 1 to minimum 292MVA/392MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 235 | 235 | 100.77 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 1 to minimum 237MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 19WP | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 113.4 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 687MVA RateB rating. | 19WP | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 24SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 101.24 |  |  |  | Upgrade HUC-MCLEOD 4 230/115kV ckt 1 to minimum 190MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 20SP 29SP 24SP | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | 201 | 221 | 118.11 |  |  |  | Upgrade SENECA 5 - GRANGRAE 161kV ckt 1 to minimum 262MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 29SP 24WP 24SP | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | 1195 | 1195 | 108.71 |  |  |  | Upgrade ST JOE 3 - EASTOWN7 345kV ckt 1 to minimum 1300MVA RateB rating. |  | Internal | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 24WP 19WP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 143 | 157.3 | 104.53 |  |  |  | Upgrade ETCO 7 - FORBES 7 115kV ckt 1 to minimum 165MVA RateB rating. | 19WP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 29SP 24WP | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | 96 | 106 | 102.22 |  |  |  | Upgrade RICE 8 69/161kV ckt 1 to minimum 109MVA RateB rating. | 24WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 618600 GRE-MCGREGR7 115 618601 GRE-KIMBRLY7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 102.01 |  |  |  | Upgrade GRE-MCGREGR7 - GRE-KIMBRLY7 115kV ckt 1 to minimum 87MVA RateB rating. |  | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 143.52 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 2 to minimum 603MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 29SP 24WP 24SP 19WP | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 251 | 251 | 114.9 |  |  |  | Upgrade 4DELCAMBRE - 4MORIL! 138kV ckt 1 to minimum 289MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 106.07 |  |  |  | Upgrade 4CANKTON% - 4COLTON 138kV ckt 1 to minimum 239MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | 20G | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | 864 | 864 | 105.2 |  |  |  | Upgrade OBRIEN 3 - HIGHLND 3 345kV ckt 1 to minimum 909MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 20SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 110.8 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 554MVA RateB rating. | 20SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300073 5GENTRY 161 300104 5NODWAY 161 1 | ALL | Base Case | 252 | 252 | 108.31 |  |  |  | Upgrade 5GENTRY - 5NODWAY 161kV ckt 1 to minimum 273MVA/248MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 17
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300531 2GEORGE 69.0 300082 5GEORGE 161 1 | 29SP | 300541 2SEDALI 69 300117 5SEDALA 161 1: 300541 2SEDALI 69.0 300117 5SEDALA 161 1 | 56 | 56 | 102.56 |  |  |  | Upgrade 2GEORGE 69/161kV ckt 1 to minimum 58MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 29SP 24SP 20G | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | 372 | 372 | 109.69 |  |  |  | Upgrade 5THMHILB1 - 5MOBTAP 161kV ckt 1 to minimum 409MVA RateB rating. | 29SP 24SP 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | ALL | Base Case | 956 | 1152 | 129.35 |  |  |  | Upgrade HILLS-DT-RX3 - HILLS 3 345kV ckt Z to minimum 1237MVA/1502MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 30
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337542 3ELD MONSNTO 115 337543 3ELDORADO.W 115 1 | 29SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 100.11 |  |  |  | Upgrade 3ELD MONSNTO - 3ELDORADO.W 115kV ckt 1 to minimum 160MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 29SP | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | 339 | 339 | 103.83 |  |  |  | Upgrade 6ESSO% - 6DELMONT 230kV ckt 1 to minimum 352MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 20SP 29SP 24SP | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | 84 | 84 | 108.07 |  |  |  | Upgrade 2LAMR 69/161kV ckt 1 to minimum 91MVA RateB rating. | 20SP 29SP 24SP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 29SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | 500 | 500 | 108.74 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 1 to minimum 544MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 24L 19WP | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | 96 | 96 | 113.18 |  |  |  | Upgrade M-TOWN 5 161/35kV ckt 1 to minimum 109MVA RateB rating. | 19WP | External | 0 | 4
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 24L 20G | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | 152 | 171 | 151.15 |  |  |  | Upgrade MARYVLE5 - BRADDYVILLE5 161kV ckt 1 to minimum 259MVA RateB rating. | 24L 20G | Internal | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 646209 S1209 5 161 646231 S1231 5 161 1 | 20SP 29SP 24WP 24SP 19WP 20G | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | 238 | 238 | 139.39 |  |  |  | Upgrade S1209 5 - S1231 5 161kV ckt 1 to minimum 332MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP 20G | Internal | 0 | 23
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 19WP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | 500 | 550 | 107.61 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 592MVA RateB rating. | 19WP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 239 | 239 | 111.52 |  |  |  | Upgrade MOORELK7 - RIVRSID7 115kV ckt 1 to minimum 267MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 24SP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 430.2 | 430.2 | 105.52 |  |  |  | Upgrade GRE-COAL CR4 - GRE-STANTON4 230kV ckt 1 to minimum 454MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 20SP 29SP 24SP | Base Case | 302 | 332 | 106.12 |  |  |  | Upgrade SENECA 5 - GENOA 5 161kV ckt 1 to minimum 321MVA/363MVA RateA/RateB rating. | 20SP 29SP 24SP | External | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 24SP | Base Case | 182 | 182 | 105.27 |  |  |  | Upgrade HIBBARD7 - WNTR ST7 115kV ckt 1 to minimum 192MVA/202MVA RateA/RateB rating. |  | External | 0 | 4
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 24L | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1210.7 | 1210.7 | 141.53 |  |  |  | Upgrade 8WILLOW_GL% - 8WATERFO 500kV ckt 1 to minimum 1714MVA RateB rating. | 24L | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 20SP 29SP 24SP | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 108.98 |  |  |  | Upgrade 2STURGN 69/161kV ckt 1 to minimum 28MVA RateB rating. | 20SP 29SP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337542 3ELD MONSNTO 115 337543 3ELDORADO.W 115 1 | 29SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 100.11 |  |  |  | Upgrade 3ELD MONSNTO - 3ELDORADO.W 115kV ckt 1 to minimum 160MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620263 FORMN 7 115 997493 230/115 115 1 | 24WP | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | 112 | 140 | 110.62 |  |  |  | Upgrade FORMN 7 - 230/115 115kV ckt 1 to minimum 155MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | ALL | Base Case | 926 | 1010 | 129.65 |  |  |  | Upgrade BONDRNT3 - MNTZUMA3 345kV ckt 1 to minimum 1201MVA/1337MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 25
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 20SP | P13:69-115-13:GRE-XEL-XEL:AUTO-SINGLE:GRE-STBONI8:GRE-STBONI7:GRE-STBONI2T:2 | 70 | 70 | 103.94 |  |  |  | Upgrade GRE-ST BONI7 115/69kV ckt 1 to minimum 73MVA RateB rating. | 20SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 24WP | P23:345:OTP:JAMESTN3:3145:V2020 | 319 | 351 | 102.75 |  |  |  | Upgrade HANKSON4 - WAHPETN4 230kV ckt 1 to minimum 361MVA RateB rating. | 24WP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 20SP 29SP 24WP 24SP 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 120.63 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 2 to minimum 700MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 24SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | 500 | 500 | 107.27 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 1 to minimum 537MVA RateB rating. | 24SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 266 | 266 | 113.9 |  |  |  | Upgrade 3WHT BLUFF! - 3HENSLEY 115kV ckt 1 to minimum 303MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 20SP 29SP 24SP | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | 230 | 230 | 111.74 |  |  |  | Upgrade BIGSTON7 - HIWY12 7 115kV ckt 1 to minimum 258MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 24WP 19WP | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | 100 | 100 | 119.65 |  |  |  | Upgrade DMOINES5 161/69kV ckt 1 to minimum 120MVA RateB rating. | 24WP 19WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 29SP 24WP 19WP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 189 | 220.9 | 110.68 |  |  |  | Upgrade FIFTHST7 - MAIN ST7 115kV ckt 1 to minimum 245MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 20G | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 650 | 715 | 114.76 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 821MVA RateB rating. | 20G | Internal | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 602021 EAU CLA5 161 997656 EAU CL 3 161 9 | 20G | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 117.74 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 394MVA RateB rating. | 20G | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 29SP 24WP 24SP 24L 19WP | P23:345:MEC:GRIMES 901 | 1247 | 1319 | 119.24 |  |  |  | Upgrade GRIMES 3 - SYCAMOR3 345kV ckt 2 to minimum 1573MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 9
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 29SP 24WP 24SP 19WP 20G | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | 1000 | 1136 | 122.56 |  |  |  | Upgrade ST JOE 3 - NASHUA 7 345kV ckt 1 to minimum 1393MVA RateB rating. | 29SP 24WP 24SP 19WP | Internal | 0 | 13
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 20G | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 400 | 440 | 105.97 |  |  |  | Upgrade SIBLEY 5 - SIBLEY11 161kV ckt 11 to minimum 467MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | ALL | Base Case | 81 | 81 | 103.04 |  |  |  | Upgrade BLRSTWN7 - PRAR CK7 115kV ckt 1 to minimum 84MVA/103MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 34
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337753 8HS EHV% 500 337740 3HS EHV-E! 115 1 | 20SP | P23:HV-EHV:EES::8HS EHV%:3 | 550 | 550 | 105.01 |  |  |  | Upgrade 8HS EHV% 500/115kV ckt 1 to minimum 578MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 24SP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 430.2 | 430.2 | 105.52 |  |  |  | Upgrade GRE-COAL CR4 - GRE-STANTON4 230kV ckt 1 to minimum 454MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 29SP | P23:345:MEC:LOUISA 924 | 1189 | 1189 | 113.93 |  |  |  | Upgrade WALCOTT3 - SUB 92 3 345kV ckt 1 to minimum 1355MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 34 | 34 | 100.11 |  |  |  | Upgrade TURK RV8 69/161kV ckt 1 to minimum 35MVA/41MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 23
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 603020 MAPLE R7 115 997609 MAPLE RIVER 69.0 1 | 24WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 128.02 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 180MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 113.4 |  |  |  | Upgrade 5LATHRP - 5MOCITY 161kV ckt 1 to minimum 258MVA RateB rating. | 20G | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 29SP 24SP | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | 97.9 | 97.9 | 105.69 |  |  |  | Upgrade GRE-CMRTJCT7 - GRE-CORMRNT7 115kV ckt 1 to minimum 104MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 19WP 20G | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | 120 | 131 | 223.01 |  |  |  | Upgrade BEULAH 7 - COYOTE 7 115kV ckt 1 to minimum 293MVA RateB rating. | 19WP 20G | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603002 WILMART7 115 603188 EASTWD18 115 1 | 20SP 29SP 24SP | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | 224.7 | 247.1 | 104 |  |  |  | Upgrade WILMART7 - EASTWD18 115kV ckt 1 to minimum 257MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 24L 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 357 | 390 | 133.2 |  |  |  | Upgrade ST JOE 5 - WOODBIN5 161kV ckt 1 to minimum 520MVA RateB rating. | 24L 20G | Internal | 0 | 4
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1: 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | 162 | 162 | 108.92 |  |  |  | Upgrade 5MT HOME - 5SOUTHLAND# 161kV ckt 1 to minimum 177MVA RateB rating. | 29SP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 112.16 |  |  |  | Upgrade 4E_OPELUSAS! - 4COLTON 138kV ckt 1 to minimum 253MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997052 GLENHAM TR1 115 1 | 19WP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 110.31 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 35MVA RateB rating. | 19WP | External | 1 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 24WP 19WP | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 441 | 441 | 107.25 |  |  |  | Upgrade 6BLPNT! - 6GYPSY% 230kV ckt 1 to minimum 473MVA RateB rating. | 24WP 19WP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603020 MAPLE R7 115 997616 MAPLE RIVER 69.0 1 | 19WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 118.72 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 167MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | ALL | Base Case | 252 | 252 | 113.9 |  |  |  | Upgrade 5GENTRY - 5FAIRPT 161kV ckt 1 to minimum 288MVA/272MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 21
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 29SP | P23:345:MEC:HILLS 934 | 84 | 84 | 102.55 |  |  |  | Upgrade E CALMS7 115/161kV ckt 1 to minimum 87MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 29SP 24SP | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | 94.8 | 94.8 | 114.6 |  |  |  | Upgrade GRE-TAMARAC7 - GRE-CORMRNT7 115kV ckt 1 to minimum 109MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 20G | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 650 | 715 | 113.92 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 815MVA RateB rating. | 20G | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 29SP 24SP | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | 94.8 | 94.8 | 114.6 |  |  |  | Upgrade GRE-TAMARAC7 - GRE-CORMRNT7 115kV ckt 1 to minimum 109MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 24WP | Base Case | 26 | 32.5 | 107.68 |  |  |  | Upgrade BROWNSV4 230/42kV ckt 1 to minimum 28MVA/36MVA RateA/RateB rating. | 24WP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 344282 5CAPE GIR2 161 351006 5JOPPA SR 161 1 | 24SP | P23:345:AMIL::JOPPA:V5 | 250 | 297 | 104.6 |  |  |  | Upgrade 5CAPE GIR2 - 5JOPPA SR 161kV ckt 1 to minimum 311MVA RateB rating. | 24SP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 118.5 |  |  |  | Upgrade 4E_OPELUSAS! - 4CHAMPAGNE! 138kV ckt 1 to minimum 267MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 29SP 24SP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 430.2 | 430.2 | 103.13 |  |  |  | Upgrade GRE-COAL CR4 - GRE-STANTON4 230kV ckt 1 to minimum 444MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 121.9 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 9
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1049 | 1049 | 147.27 |  |  |  | Upgrade 8WATERFO 500/230kV ckt 1 to minimum 1545MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 20SP 19WP | P13:161-69:EES-EAI:HERGET:AT1 | 100 | 112 | 118.43 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 133MVA RateB rating. | 20SP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 29SP 24SP | P23:345:MEC:SYCAMORE 905 | 373 | 395 | 105.4 |  |  |  | Upgrade GRNGRTP5 - 100 54 5 161kV ckt 1 to minimum 417MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 20SP | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | 310 | 310 | 100.1 |  |  |  | Upgrade 5BATESVLE AR - 5MOOREFIELD 161kV ckt 1 to minimum 311MVA RateB rating. | 20SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 345221 5MOBERLY 161 345409 5OVERTON 161 1 | 29SP | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | 204 | 242 | 100.95 |  |  |  | Upgrade 5MOBERLY - 5OVERTON 161kV ckt 1 to minimum 245MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.66 |  |  |  | Upgrade ST JOE 5 - ST. JOSEPH33 161kV ckt 33 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 29SP | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 106 | 106 | 106.99 |  |  |  | Upgrade 3RIVERTON - 3RILLA! 115kV ckt 1 to minimum 114MVA RateB rating. | 29SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 19WP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 135.17 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 95MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 24SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 115.56 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 387MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631198 COLBY3 345 631202 COLBY5 161 1 | 29SP 24WP 24SP 19WP 20G | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | 450 | 450 | 110.96 |  |  |  | Upgrade COLBY3 345/161kV ckt 1 to minimum 500MVA RateB rating. | 29SP 24SP 19WP | External | 0 | 15
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 29SP 24SP | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | 56 | 56 | 108.05 |  |  |  | Upgrade 2LOCUST 69/161kV ckt 1 to minimum 61MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 19WP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | 330 | 334.6 | 113.15 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 379MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 29SP 24SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 214.1 | 214.1 | 107.58 |  |  |  | Upgrade BAILEY RD7 - GLENMONT 115kV ckt 1 to minimum 231MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 115.08 |  |  |  | Upgrade 5MPLTAP - 5LATHRP 161kV ckt 1 to minimum 262MVA RateB rating. | 20G | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 29SP | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 560 | 560 | 101.2 |  |  |  | Upgrade 8MT_OLIVE% 500/230kV ckt 1 to minimum 567MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 29SP 24SP | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | 272 | 272 | 142.96 |  |  |  | Upgrade EMERY 5 - FLOYD 5 161kV ckt 1 to minimum 389MVA RateB rating. | 29SP 24SP | External | 0 | 8
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 24L 20G | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | 152 | 171 | 151.15 |  |  |  | Upgrade MARYVLE5 - BRADDYVILLE5 161kV ckt 1 to minimum 259MVA RateB rating. | 24L 20G | Internal | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 24L 19WP | P23:345:MEC:SYCAMORE 905 | 335 | 335 | 106.85 |  |  |  | Upgrade 100 54 5 - JOHNSTON 5 161kV ckt 1 to minimum 358MVA RateB rating. | 19WP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 29SP 24SP | Base Case | 78 | 78 | 109.21 |  |  |  | Upgrade FLDWDTP7 - MDWLNDS7 115kV ckt 1 to minimum 86MVA/122MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 11
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 20SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 113.77 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 20SP | External | 2 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 105.29 |  |  |  | Upgrade 3SHERRILL - 3ENGLAND# 115kV ckt 1 to minimum 104MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 19WP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 105.23 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 33MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 24SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 121.72 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 871MVA RateB rating. | 24SP | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 20SP | P23:345:XEL:8N22 SHC | 1332.6 | 1332.6 | 101.45 |  |  |  | Upgrade FIELD_S3 - CRANDAL 3 345kV ckt 1 to minimum 1352MVA RateB rating. |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 640065 AXTELL 3 345 997459 AXTELL T1 115 1 | 24WP | P42:345:NPPD:BKR-AXT-3308 | 336 | 336 | 107.02 |  |  |  | Upgrade AXTELL 3 345/115kV ckt 1 to minimum 360MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 646209 S1209 5 161 646347 S1347 161 1 | 29SP 24WP 24SP 24L 19WP | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | 217 | 217 | 128.97 |  |  |  | Upgrade S1209 5 - S1347 161kV ckt 1 to minimum 280MVA RateB rating. |  | Internal | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 29SP | P23:345:MEC:LOUISA 924 | 1189 | 1189 | 113.93 |  |  |  | Upgrade WALCOTT3 - SUB 92 3 345kV ckt 1 to minimum 1355MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 127.22 |  |  |  | Upgrade ST JOE 5 - AVENUECTY 5 161kV ckt 1 to minimum 254MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 20G | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 400 | 400 | 110.85 |  |  |  | Upgrade OTTUMWA3 345/161kV ckt 1 to minimum 444MVA RateB rating. | 20G | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 20SP 29SP 24SP 24L 20G | P13:161-69:ITCM:BVR CH5 T1:IA-EC | 127 | 127 | 139.14 |  |  |  | Upgrade 8TH ST.5 - GALENA 5 161kV ckt 1 to minimum 177MVA RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 17
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 29SP | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | 500 | 550 | 101.95 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 561MVA RateB rating. |  | Internal | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 20SP 29SP 24WP 24SP 19WP | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 122.02 |  |  |  | Upgrade 2KOLBS_2! 69/230kV ckt 2 to minimum 195MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 24SP 24L 19WP 20G | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 325 | 325 | 130.81 |  |  |  | Upgrade REASNOR5 - RISING SUN 5 161kV ckt 1 to minimum 426MVA RateB rating. | 24L 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 103.71 |  |  |  | Upgrade GRE-KIMBRLY7 - GRE-AITKIN 7 115kV ckt 1 to minimum 88MVA RateB rating. |  | External | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 24L | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 147.99 |  |  |  | Upgrade EASTOWN7 345/161kV ckt 11 to minimum 652MVA RateB rating. | 24L | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 20SP | Base Case | 800 | 1084 | 107.16 |  |  |  | Upgrade ARROWHD4 - AWHD PST 230kV ckt 1 to minimum 858MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 24WP 19WP 20G | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 92 | 92 | 109.26 |  |  |  | Upgrade 16L TAP7 - COTTNTP7 115kV ckt 1 to minimum 101MVA RateB rating. | 24WP 19WP 20G | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 29SP 24SP 19WP 20G | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 137.81 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 3 to minimum 35MVA RateB rating. | 29SP 24SP 19WP 20G | External | 0 | 11
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 29SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 111.53 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 558MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 20SP 29SP 24WP 24SP 19WP | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 128.03 |  |  |  | Upgrade 2KOLBS_1! 69/230kV ckt 1 to minimum 204MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 29SP 24WP 24SP 19WP | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | 1195 | 1195 | 110.25 |  |  |  | Upgrade STRANGR7 - IATAN 7 345kV ckt 1 to minimum 1318MVA RateB rating. | 24WP | Internal | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 29SP 24SP | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 123 | 123 | 100.79 |  |  |  | Upgrade BVR CHN J1 8 69/161kV ckt 1 to minimum 124MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | ALL | Base Case | 223 | 223 | 142.67 |  |  |  | Upgrade ADAMS 5 - BVR CRK5 161kV ckt 1 to minimum 319MVA/378MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.66 |  |  |  | Upgrade ST JOE 5 - ST. JOSEPH33 161kV ckt 33 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 29SP 24SP | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | 143.4 | 143.4 | 112.61 |  |  |  | Upgrade YORKTON 4 230/138kV ckt 1 to minimum 162MVA RateB rating. | 29SP 24SP | External | 6 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 681519 STONEMAN 161 699010 NED 161 161 1 | 20SP 24SP | Base Case | 201 | 221 | 104.44 |  |  |  | Upgrade STONEMAN - NED 161 161kV ckt 1 to minimum 210MVA/263MVA RateA/RateB rating. | 20SP 24SP | External | 14 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | 1195 | 1195 | 102.43 |  |  |  | Upgrade 7FAIRPT - COOPER 3 345kV ckt 1 to minimum 1225MVA RateB rating. |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 997593 HIL1 115 1 | 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 124.7 |  |  |  | Upgrade HILLTOP7 - HIL1 115kV ckt 1 to minimum 291MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 19WP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 100.59 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 705MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | 1195 | 1195 | 102.43 |  |  |  | Upgrade 7FAIRPT - COOPER 3 345kV ckt 1 to minimum 1225MVA RateB rating. |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 29SP | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 560 | 560 | 101.2 |  |  |  | Upgrade 8MT_OLIVE% 500/230kV ckt 1 to minimum 567MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | 100 | 112 | 129.2 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 145MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337753 8HS EHV% 500 337685 3HS EHV-W! 115 1 | 20SP | P23:HV-EHV:EES::8HS EHV%:5 | 550 | 550 | 104.9 |  |  |  | Upgrade 8HS EHV% 500/115kV ckt 1 to minimum 577MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 646254 S1254 5 161 646281 S1281 5 161 1 | 29SP 24WP 24SP 24L 19WP 20G | P1-2 POI - S1363 | 298 | 298 | 140 |  |  |  | Upgrade S1254 5 - S1281 5 161kV ckt 1 to minimum 418MVA RateB rating. |  | Internal | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 29SP 24WP 24SP 19WP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 188.8 | 220.5 | 113.73 |  |  |  | Upgrade ALDRICH7 - FIFTHST7 115kV ckt 1 to minimum 251MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 4
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 110.62 |  |  |  | Upgrade 3DIERKS! - 3SHERRILL 115kV ckt 1 to minimum 109MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 29SP 24SP | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | 100 | 100 | 107.16 |  |  |  | Upgrade JEFF 8 69/161kV ckt 1 to minimum 108MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 20SP 29SP 24WP 24SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 275 | 291 | 129.56 |  |  |  | Upgrade WABACO 5 - ALMA 5 161kV ckt 1 to minimum 378MVA RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 20SP 29SP 24SP | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 33.6 | 41 | 121.78 |  |  |  | Upgrade BELLCTR5 161/69kV ckt 2 to minimum 50MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 7
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 107.27 |  |  |  | Upgrade 4E_OPELUSAS! - 4CHAMPAGNE! 138kV ckt 1 to minimum 242MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 24L | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 147.99 |  |  |  | Upgrade EASTOWN7 345/161kV ckt 11 to minimum 652MVA RateB rating. | 24L | Internal | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 24L 20G | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 199 | 199 | 126.34 |  |  |  | Upgrade CLRNDA 5 - BRADDYVILLE5 161kV ckt 1 to minimum 252MVA RateB rating. | 24L 20G | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 20SP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 148.4 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 104MVA RateB rating. | 20SP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 29SP 20G | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 258 | 258 | 107.08 |  |  |  | Upgrade TRAER 5 - DYSART 5 161kV ckt 1 to minimum 277MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP 19WP | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 56 | 56 | 146.59 |  |  |  | Upgrade 2HOLDEN 69/161kV ckt 1 to minimum 83MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.85 |  |  |  | Upgrade ST JOE 5 - ST. JOSEPH22 161kV ckt 22 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | ALL | Base Case | 212 | 212 | 128.86 |  |  |  | Upgrade WEBSTER5 - WRIGHT 5 161kV ckt 1 to minimum 274MVA/346MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 38
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 29SP | P23:345:MEC:HILLS 934 | 84 | 84 | 102.55 |  |  |  | Upgrade E CALMS7 115/161kV ckt 1 to minimum 87MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 29SP | Base Case | 36 | 36 | 116.33 |  |  |  | Upgrade BL.PLN.5 161/69kV ckt 1 to minimum 42MVA/45MVA RateA/RateB rating. | 29SP | External | 7 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 319 | 351 | 103.4 |  |  |  | Upgrade HANKSON4 - WAHPETN4 230kV ckt 1 to minimum 330MVA/386MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 19
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 24WP 24SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 110.7 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 78MVA RateB rating. | 24WP 24SP | External | 4 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 108.63 |  |  |  | Upgrade 3ARCH ST - 3SARDIS# 115kV ckt 1 to minimum 275MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 29SP 24SP | P23:345:XEL:8M36 CNC | 1195.1 | 1195.1 | 111.73 |  |  |  | Upgrade COON CK3 - KOLMNLK3 345kV ckt 1 to minimum 1336MVA RateB rating. | 29SP 24SP | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 29SP 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 114.36 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 1 to minimum 301MVA RateB rating. | 29SP 24SP | External | 2 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 20SP 29SP 24SP | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 109.52 |  |  |  | Upgrade 2STURGN 69/161kV ckt 2 to minimum 28MVA RateB rating. | 20SP 29SP 24SP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 20SP 29SP 24SP 20G | Base Case | 1000 | 1136 | 101.27 |  |  |  | Upgrade HAWTH 7 - NASHUA 7 345kV ckt 1 to minimum 1013MVA/1354MVA RateA/RateB rating. | 29SP 24SP | Internal | 0 | 11
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 239 | 239 | 111.52 |  |  |  | Upgrade MOORELK7 - RIVRSID7 115kV ckt 1 to minimum 267MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 602021 EAU CLA5 161 997642 EAU CL 3 161 9 | 24WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 106.05 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 355MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 34 | 34 | 100.11 |  |  |  | Upgrade TURK RV8 69/161kV ckt 1 to minimum 35MVA/41MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 23
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 20SP 29SP 24WP 24SP 19WP | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 123.51 |  |  |  | Upgrade 2KOLBS_2! 69/230kV ckt 2 to minimum 197MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 24WP 24SP | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 500 | 550 | 110.55 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 609MVA RateB rating. | 24WP 24SP | Internal | 0 | 7
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 127.41 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 2 to minimum 739MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.89 |  |  |  | Upgrade ST JOE 3 345/161kV ckt 22 to minimum 357MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 29SP 24SP | P23:345:AMMO::ZACHARY:2 | 172 | 172 | 118.18 |  |  |  | Upgrade 5SRIVER - 5EMERSN 161kV ckt 1 to minimum 204MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 997593 HIL1 115 1 | 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 124.7 |  |  |  | Upgrade HILLTOP7 - HIL1 115kV ckt 1 to minimum 291MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 19WP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 137.91 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 97MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 24L | 81377: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 112.77 |  |  |  | Upgrade NORTWST7 - MATHWSN7 345kV ckt 1 to minimum 1348MVA RateB rating. | 24L | Internal | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 132.41 |  |  |  | Upgrade MARYVLE5 - MIDWAY_5 161kV ckt 1 to minimum 264MVA RateB rating. | 20G | Internal | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 20SP 29SP 24WP 24SP 19WP | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 117.6 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 3 to minimum 30MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 24L | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 150 | 150 | 106.58 |  |  |  | Upgrade MPWSPLIT - DENMARK5 161kV ckt 1 to minimum 160MVA RateB rating. | 24L | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 24WP 19WP | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | 61 | 77.8 | 103.5 |  |  |  | Upgrade 2ADAIR 2 69/161kV ckt 1 to minimum 81MVA RateB rating. | 24WP 19WP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 29SP 24WP 24SP 19WP | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | 117.1 | 118.3 | 132.83 |  |  |  | Upgrade FLOYD 5 161/69kV ckt 1 to minimum 158MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 24SP | P12:161:DPC:AUTO-SINGLE:GENOA5:HARMONY5:1 | 240 | 264 | 105.05 |  |  |  | Upgrade LANSING L1 5 - GENOA 5 161kV ckt 1 to minimum 278MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 24L 20G | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 199 | 199 | 126.34 |  |  |  | Upgrade CLRNDA 5 - BRADDYVILLE5 161kV ckt 1 to minimum 252MVA RateB rating. | 24L 20G | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 29SP 24WP 24SP 19WP | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | 233 | 233 | 121.22 |  |  |  | Upgrade ADAMS 5 - HAYWARD L1 5 161kV ckt 1 to minimum 283MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | ALL | Base Case | 212 | 212 | 128.86 |  |  |  | Upgrade WEBSTER5 - WRIGHT 5 161kV ckt 1 to minimum 274MVA/346MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 38
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 20SP 24WP 24SP 19WP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 478 | 478 | 128.73 |  |  |  | Upgrade GRE-STANTON4 - SQBUTTE4 230kV ckt 1 to minimum 616MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 20SP 24SP | 71569: 601019 COON CK3 345 997666 90199-A 115 10 603068 COON CK7 115 997666 90199-A 115 10 605017 CNCTER29 34.5 997666 90199-A 115 10 601011 SHERCO 3 345 601019 COON CK3 345 1 601011 SHERCO 3 345 615327 GRE-BUNKER 3 345 2 601019 COON CK3 345 615327 GRE-BUNKER 3 345 2 615327 GRE-BUNKER 3 345 997571 345/230 230 1 | 242.8 | 242.8 | 125.49 |  |  |  | Upgrade GRE-BUNKER 4 - GRE-ELK RIV4 230kV ckt 1 to minimum 305MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 19WP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 102.65 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 719MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 29SP | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 6: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 102.39 |  |  |  | Upgrade GRAVL ISLE 8 69/161kV ckt 5 to minimum 83MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 29SP 24WP 24SP 19WP | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | 84 | 84 | 124.39 |  |  |  | Upgrade LIBERTY5 161/69kV ckt 1 to minimum 105MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 24WP | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | 241 | 241 | 104.6 |  |  |  | Upgrade 4STONGAT! - 4MID CO% 138kV ckt 1 to minimum 253MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 20SP 29SP 24SP 24L 20G | P12:345:MEC:WALCOTT-HILLS-LOUISA | 73 | 73 | 120.54 |  |  |  | Upgrade SUTLIFF7 - CALAMUS7 115kV ckt 1 to minimum 88MVA RateB rating. | 20SP 29SP 24SP 24L | External | 0 | 20
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 20SP 29SP 24SP 24L 20G | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | 200 | 200 | 122.87 |  |  |  | Upgrade HUNTLEY5 - FREEBORN5 161kV ckt 1 to minimum 246MVA RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 293 | 334 | 105.32 |  |  |  | Upgrade NAVY 5 - TERRACE5 161kV ckt 1 to minimum 352MVA RateB rating. | 24SP | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 24WP 19WP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 143 | 157.3 | 104.53 |  |  |  | Upgrade ETCO 7 - FORBES 7 115kV ckt 1 to minimum 165MVA RateB rating. | 19WP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 29SP 24SP | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 159 | 159 | 117.59 |  |  |  | Upgrade FLDWDTP7 - BLCKBRY7 115kV ckt 1 to minimum 187MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 29SP 24WP 24SP 19WP | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 30 | 30 | 187.18 |  |  |  | Upgrade 2MARYVL 69/161kV ckt 1 to minimum 57MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 20SP 24SP | 71569: 601019 COON CK3 345 997666 90199-A 115 10 603068 COON CK7 115 997666 90199-A 115 10 605017 CNCTER29 34.5 997666 90199-A 115 10 601011 SHERCO 3 345 601019 COON CK3 345 1 601011 SHERCO 3 345 615327 GRE-BUNKER 3 345 2 601019 COON CK3 345 615327 GRE-BUNKER 3 345 2 615327 GRE-BUNKER 3 345 997571 345/230 230 1 | 242.8 | 242.8 | 125.49 |  |  |  | Upgrade GRE-BUNKER 4 - GRE-ELK RIV4 230kV ckt 1 to minimum 305MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 24L 19WP | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | 96 | 96 | 113.18 |  |  |  | Upgrade M-TOWN 5 161/35kV ckt 1 to minimum 109MVA RateB rating. | 19WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 29SP 24SP | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | 280 | 308 | 120.06 |  |  |  | Upgrade 5PALMYR_AI - 5MARBLE N 161kV ckt 1 to minimum 370MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 29SP 24SP | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | 230 | 230 | 105.87 |  |  |  | Upgrade HIWY12 7 - ORTONVL7 115kV ckt 1 to minimum 244MVA RateB rating. | 29SP 24SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 20SP 24SP | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 105.25 |  |  |  | Upgrade 2WSTPL3 69/161kV ckt 1 to minimum 59MVA RateB rating. | 20SP 24SP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | ALL | Base Case | 262 | 288 | 111.07 |  |  |  | Upgrade WABACO 5 - ROCHSTR5 161kV ckt 1 to minimum 292MVA/392MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 29SP 24WP 19WP | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | 335 | 335 | 104.84 |  |  |  | Upgrade LIME CK L1 5 - LIME CK L2 5 161kV ckt Z to minimum 352MVA RateB rating. | 29SP 19WP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 20SP 29SP 24WP 24SP | Base Case | 229 | 229 | 118.53 |  |  |  | Upgrade BRLGTN 5 - WEVER5 161kV ckt 1 to minimum 272MVA/342MVA RateA/RateB rating. | 20SP 29SP | External | 0 | 16
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 29SP | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 197 | 197 | 106.84 |  |  |  | Upgrade HENRYCO5 - JEFF 5 161kV ckt 1 to minimum 211MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 24WP 24L 19WP 20G | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | 956 | 1152 | 111.32 |  |  |  | Upgrade BONDRNT3 - SYCAMOR3 345kV ckt 1 to minimum 1283MVA RateB rating. | 24WP 24L 19WP 20G | External | 0 | 16
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 104.05 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 1 to minimum 274MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 601028 EAU CL 3 345 997656 EAU CL 3 161 9 | 20G | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 114.21 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 383MVA RateB rating. | 20G | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 24WP 19WP | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1055 | 1319 | 104.02 |  |  |  | Upgrade GRIMES 3 - SYCAMOR3 345kV ckt 1 to minimum 1373MVA RateB rating. | 24WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 29SP 24WP 24SP | P23:345:XEL:8P33 KOL | 222.7 | 222.7 | 109.39 |  |  |  | Upgrade ROSE PL7 - TERMINL7 115kV ckt 1 to minimum 244MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 19WP | P13:161-69:EES-EAI:HERGET:AT2 | 100 | 112 | 121.34 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 136MVA RateB rating. | 19WP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 29SP | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | 995 | 995 | 105.28 |  |  |  | Upgrade HAZLTON3 - MITCHLCO3 345kV ckt 1 to minimum 1048MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 19WP | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 117.63 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 712MVA RateB rating. | 19WP | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 29SP 24L 20G | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 240 | 240 | 123.88 |  |  |  | Upgrade PARNEL 5 - POWESHK5 161kV ckt 1 to minimum 298MVA RateB rating. | 29SP 24L 20G | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 20SP 29SP 24WP 24SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 275 | 291 | 129.56 |  |  |  | Upgrade WABACO 5 - ALMA 5 161kV ckt 1 to minimum 378MVA RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 12
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 20SP 24WP 24SP 19WP | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 117.51 |  |  |  | Upgrade 6IRONMAN% - 6GYPSY% 230kV ckt 1 to minimum 610MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 20SP 19WP | P13:161-69:EES-EAI:HERGET:AT2 | 100 | 112 | 118.09 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 133MVA RateB rating. | 20SP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 20SP 29SP 24SP 24L 20G | Base Case | 1073 | 1195 | 109.2 |  |  |  | Upgrade ST JOE 3 - COOPER 3 345kV ckt 1 to minimum 1172MVA/1454MVA RateA/RateB rating. | 29SP 24SP 24L 20G | Internal | 0 | 14
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603110 TERMINL7 115 997649 90198-B 115 10 | 29SP | P23:345:XEL:8P33 KOL | 672 | 734 | 113.3 |  |  |  | Upgrade TERMINL7 - 90198-B 115kV ckt 10 to minimum 832MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1049 | 1049 | 166.19 |  |  |  | Upgrade 8WATERFO 500/230kV ckt 1 to minimum 1744MVA RateB rating. | 24L 19WP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 20SP 29SP 24WP 24SP 19WP | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | 217 | 217 | 123.78 |  |  |  | Upgrade S1221 5 - S1231 5 161kV ckt 1 to minimum 269MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | Internal | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 24SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | 550 | 605 | 111.84 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 677MVA RateB rating. | 24SP | Internal | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 24WP 24SP | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 126.69 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 906MVA RateB rating. | 24SP | Internal | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 106.07 |  |  |  | Upgrade 4CANKTON% - 4COLTON 138kV ckt 1 to minimum 239MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 20SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1210.7 | 1210.7 | 125.55 |  |  |  | Upgrade 8WILLOW_GL% - 8WATERFO 500kV ckt 1 to minimum 1521MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 268.1 | 268.1 | 105.26 |  |  |  | Upgrade RIVRSID7 - BRKLNPK7 115kV ckt 1 to minimum 283MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 29SP | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 257 | 257 | 105.38 |  |  |  | Upgrade 3DOWNSVILLE - 3STERL2% 115kV ckt 1 to minimum 271MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 29SP 24SP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 430.2 | 430.2 | 103.13 |  |  |  | Upgrade GRE-COAL CR4 - GRE-STANTON4 230kV ckt 1 to minimum 444MVA RateB rating. | 29SP 24SP | External | 2 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 225 | 225 | 104.96 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 2 to minimum 237MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 29SP 24WP 24SP 19WP | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 159 | 159 | 111.06 |  |  |  | Upgrade 3WYATT! - 3PARNELL RD 115kV ckt 1 to minimum 177MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 12
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 123.42 |  |  |  | Upgrade EASTOWN5 - EASTOWNE11 161kV ckt 11 to minimum 544MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 29SP 24WP 24SP 19WP | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 159 | 159 | 111.06 |  |  |  | Upgrade 3WYATT! - 3PARNELL RD 115kV ckt 1 to minimum 177MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 12
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 20SP 29SP 24WP 24SP 19WP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 478 | 478 | 144.55 |  |  |  | Upgrade GRE-STANTON4 - SQBUTTE4 230kV ckt 1 to minimum 691MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 10 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 225 | 225 | 104.77 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 2 to minimum 236MVA RateB rating. | 20SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 20SP 29SP 24SP | P11:024:DPC:ALMA2:6 | 201 | 221.1 | 116.34 |  |  |  | Upgrade WABACO 5 - ROCHSTR5 161kV ckt 1 to minimum 258MVA RateB rating. | 20SP 29SP 24SP | External | 18 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 29SP | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 206 | 206 | 107.67 |  |  |  | Upgrade 4SPLENDR! - 4JACINTO% 138kV ckt 1 to minimum 222MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 24WP 24L 19WP 20G | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | 956 | 1152 | 111.32 |  |  |  | Upgrade BONDRNT3 - SYCAMOR3 345kV ckt 1 to minimum 1283MVA RateB rating. | 24WP 24L 19WP 20G | External | 0 | 16
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 127.59 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 1 to minimum 741MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | ALL | Base Case | 956 | 1010 | 105.66 |  |  |  | Upgrade MNTZUMA3 - DIAMOND TRL3 345kV ckt 1 to minimum 1011MVA/1306MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 26
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 603020 MAPLE R7 115 997609 MAPLE RIVER 69.0 1 | 24WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 128.02 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 180MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 20SP 24SP 24L 20G | Base Case | 203 | 203 | 107.77 |  |  |  | Upgrade 5FAIRPT - 5HICKCK 161kV ckt 1 to minimum 219MVA/255MVA RateA/RateB rating. | 20SP 24L 20G | External | 0 | 16
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615135 G619TAM7 115 618203 GRE-TAMARAC7 115 1 | 20SP | Base Case | 50 | 50 | 100.94 |  |  |  | Upgrade G619TAM7 - GRE-TAMARAC7 115kV ckt 1 to minimum 51MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 29SP 24WP 24SP 19WP 20G | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | 307 | 307 | 118.46 |  |  |  | Upgrade WAPELLO5 - OTTUMWA5 161kV ckt 1 to minimum 364MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | ALL | Base Case | 72 | 72 | 104.1 |  |  |  | Upgrade ADAMS 8 69/161kV ckt 1 to minimum 75MVA/102MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 33
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 127.83 |  |  |  | Upgrade EASTOWN7 345/161kV ckt 11 to minimum 563MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997476 DGG9T1 161 1 | 24SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 104.27 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 730MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 29SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 103.11 |  |  |  | Upgrade HUC-MCLEOD 7 - 230/115 115kV ckt 1 to minimum 193MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 319 | 351 | 103.4 |  |  |  | Upgrade HANKSON4 - WAHPETN4 230kV ckt 1 to minimum 330MVA/386MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 19
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 29SP 24SP | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | 272 | 272 | 142.96 |  |  |  | Upgrade EMERY 5 - FLOYD 5 161kV ckt 1 to minimum 389MVA RateB rating. | 29SP 24SP | External | 0 | 8
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 29SP 24SP | P24:345:ITCM:LAKEFLD 885 FUT:MN | 112 | 112 | 126.07 |  |  |  | Upgrade MAGNLIA5 - ELK L1 5 161kV ckt 1 to minimum 142MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 29SP | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | 84 | 84 | 122.31 |  |  |  | Upgrade TRAER 5 161/69kV ckt 1 to minimum 103MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 159.32 |  |  |  | Upgrade 3WHT BLUFF! - 3WRIGHTSVLE! 115kV ckt 1 to minimum 404MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 20SP 29SP 24SP | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | 131 | 131 | 111.08 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 1 to minimum 146MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601024 TERMINL3 345 997650 90198-B 115 10 | 24SP | P23:345:XEL:8P33 KOL | 672 | 734 | 109.3 |  |  |  | Upgrade TERMINL3 345/115kV ckt 10 to minimum 803MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 29SP 24WP 19WP | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | 41.7 | 60 | 107.19 |  |  |  | Upgrade MONONA 5 161/69kV ckt 1 to minimum 65MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | ALL | Base Case | 956 | 1152 | 129.99 |  |  |  | Upgrade DIAMOND TRL3 - HILLS-DT-RX3 345kV ckt 1 to minimum 1243MVA/1540MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 30
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 29SP | P13:500-161:EES-EAI:ARK_NU:AT3 | 600 | 600 | 100.46 |  |  |  | Upgrade 8P.HILL% 500/161kV ckt 1 to minimum 603MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 29SP | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 123.59 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 414MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 20SP 29SP 24WP 24SP | Base Case | 229 | 229 | 118.53 |  |  |  | Upgrade BRLGTN 5 - WEVER5 161kV ckt 1 to minimum 272MVA/342MVA RateA/RateB rating. | 20SP 29SP | External | 0 | 16
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620263 FORMN 7 115 997493 230/115 115 1 | 24WP | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | 112 | 140 | 110.62 |  |  |  | Upgrade FORMN 7 - 230/115 115kV ckt 1 to minimum 155MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 29SP 24WP 24SP | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 223 | 223 | 119.8 |  |  |  | Upgrade 5HUNTSDL - 5OVERTON 161kV ckt 1 to minimum 268MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 24SP | P23:345:MEC:OAK GROVE 901 | 314 | 314 | 106.53 |  |  |  | Upgrade SB 56 5 - SB 85 5 161kV ckt 1 to minimum 335MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 24L | Base Case | 42 | 42 | 102.91 |  |  |  | Upgrade FONDULAC - HIBBARD7 115kV ckt 1 to minimum 44MVA/47MVA RateA/RateB rating. | 24L | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 24SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | 550 | 605 | 116.66 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 706MVA RateB rating. | 24SP | Internal | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 24SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 101.46 |  |  |  | Upgrade HUC-MCLEOD 7 - 230/115 115kV ckt 1 to minimum 190MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 158.26 |  |  |  | Upgrade 3WHT BLUFF! - 3WRIGHTSVLE! 115kV ckt 1 to minimum 401MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 20SP 29SP 24SP | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | 84 | 84 | 106.78 |  |  |  | Upgrade 2CDRCRST 69/161kV ckt 1 to minimum 90MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 20SP 29SP 24WP 24SP 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 120.8 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 1 to minimum 701MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 347840 5NIOTA 161 631216 WEVER5 161 1 | 20SP 29SP 24SP 24L | Base Case | 175 | 175 | 101.09 |  |  |  | Upgrade 5NIOTA - WEVER5 161kV ckt 1 to minimum 177MVA/265MVA RateA/RateB rating. | 20SP 29SP 24SP | External | 0 | 17
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 29SP 24WP | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | 96 | 96 | 105.48 |  |  |  | Upgrade 2TURKEYCRK 69/161kV ckt 1 to minimum 102MVA RateB rating. | 29SP 24WP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 29SP 24WP 24SP 19WP 20G | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | 56 | 56 | 134.34 |  |  |  | Upgrade 2OSBORN 69/161kV ckt 1 to minimum 76MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 29SP 24WP 24SP 19WP | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 114.37 |  |  |  | Upgrade WAPELLO5 - OTTUMWA5 161kV ckt 2 to minimum 384MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 19WP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 111.61 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 79MVA RateB rating. | 19WP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 600178 J460_GEN2 34.5 601088 BLZNG STR1 3 345 2 | 20SP | Base Case | 100 | 120 | 100.95 |  |  |  | Upgrade J460_GEN2 35/345kV ckt 2 to minimum 101MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997475 DGG9T1 161 1 | 29SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 105.36 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 738MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 24SP | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | 70 | 80.5 | 102.98 |  |  |  | Upgrade RIV FLS7 115/69kV ckt 5 to minimum 83MVA RateB rating. | 24SP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | ALL | Base Case | 201 | 201 | 114.28 |  |  |  | Upgrade FRANKLN5 - WALL LK5 161kV ckt 1 to minimum 230MVA/245MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 20G | External | 0 | 32
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 29SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 121.59 |  |  |  | Upgrade GRE-CHUBLAK7 - CHL345-115-1 115kV ckt 1 to minimum 545MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 997592 HIL1 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 112.08 |  |  |  | Upgrade HILLTOP7 - HIL1 115kV ckt 1 to minimum 262MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 24WP 19WP | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | 100 | 100 | 119.65 |  |  |  | Upgrade DMOINES5 161/69kV ckt 1 to minimum 120MVA RateB rating. | 24WP 19WP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603110 TERMINL7 115 997650 90198-B 115 10 | 24SP | P23:345:XEL:8P33 KOL | 672 | 734 | 110.59 |  |  |  | Upgrade TERMINL7 - 90198-B 115kV ckt 10 to minimum 812MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 123.32 |  |  |  | Upgrade 6TEZCUCO% - 6IRONMAN% 230kV ckt 1 to minimum 641MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 24WP | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | 80 | 88 | 108.24 |  |  |  | Upgrade EDGETAP7 - PEL RPD7 115kV ckt 1 to minimum 96MVA RateB rating. | 24WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 24WP 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 500 | 550 | 108.95 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 600MVA RateB rating. | 24WP 24SP | Internal | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 29SP | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 110.3 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 668MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 640066 AXTELL 7 115 997459 AXTELL T1 115 1 | 24WP | P42:345:NPPD:BKR-AXT-3308 | 336 | 336 | 102.87 |  |  |  | Upgrade AXTELL 7 - AXTELL T1 115kV ckt 1 to minimum 346MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 29SP 24WP 24SP | P23:345:ITCM:HCKRYCK:FUT2 | 352 | 444 | 121.6 |  |  |  | Upgrade HCKRYCK5 161/345kV ckt 1 to minimum 540MVA RateB rating. | 29SP | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 19WP | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 117.63 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 712MVA RateB rating. | 19WP | Internal | 0 | 4
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 107.99 |  |  |  | Upgrade 3MABLVALE-E! - 3SARDIS# 115kV ckt 1 to minimum 274MVA RateB rating. | 20G | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 20SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 145.48 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 102MVA RateB rating. | 20SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 608686 15TH AV7 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 80 | 80 | 108.56 |  |  |  | Upgrade HILLTOP7 - 15TH AV7 115kV ckt 1 to minimum 87MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997052 GLENHAM TR1 115 1 | 19WP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 110.31 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 35MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 20SP | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 90 | 90 | 103.97 |  |  |  | Upgrade POTLTCH7 - CLOQUET7 115kV ckt 1 to minimum 94MVA RateB rating. | 20SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608616 HILLTOP4 230 997592 HIL1 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 110.15 |  |  |  | Upgrade HILLTOP4 230/115kV ckt 1 to minimum 257MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 29SP | Base Case | 36 | 36 | 116.33 |  |  |  | Upgrade BL.PLN.5 161/69kV ckt 1 to minimum 42MVA/45MVA RateA/RateB rating. | 29SP | External | 7 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | ALL | Base Case | 956 | 1152 | 129.35 |  |  |  | Upgrade HILLS-DT-RX3 - HILLS 3 345kV ckt Z to minimum 1237MVA/1502MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 30
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 29SP | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 106.19 |  |  |  | Upgrade HAWTHN5 - HAWTHORN22 161kV ckt 22 to minimum 643MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 29SP 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233.8 | 121.34 |  |  |  | Upgrade 98L TAP4 - HILLTOP4 230kV ckt 1 to minimum 284MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997045 GLENHAM TR1 115 1 | 29SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 115.88 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 29SP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 29SP | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | 500 | 550 | 101.95 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 561MVA RateB rating. |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 24L 20G | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 334 | 334 | 139.77 |  |  |  | Upgrade EAST 5 - EASTOWN5 161kV ckt 1 to minimum 467MVA RateB rating. | 24L | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 263.7 | 263.7 | 108.73 |  |  |  | Upgrade GRE-BUNKER 4 - GRE-BLAINE 4 230kV ckt 1 to minimum 287MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 29SP 24WP | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | 96 | 96 | 105.48 |  |  |  | Upgrade 2TURKEYCRK 69/161kV ckt 1 to minimum 102MVA RateB rating. | 29SP 24WP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 24WP 24SP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 137.21 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 769MVA RateB rating. | 24WP 24SP | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 29SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 101.17 |  |  |  | Upgrade 4E_OPELUSAS! - 4COLTON 138kV ckt 1 to minimum 228MVA RateB rating. | 29SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620263 FORMN 7 115 997492 230/115 115 1 | 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1: 620327 HANKSON4 230 620363 FORMAN 4 230 1 | 112 | 132 | 105.6 |  |  |  | Upgrade FORMN 7 - 230/115 115kV ckt 1 to minimum 140MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 20SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 111.51 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 79MVA RateB rating. | 20SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300531 2GEORGE 69.0 300082 5GEORGE 161 1 | 29SP | 300541 2SEDALI 69 300117 5SEDALA 161 1: 300541 2SEDALI 69.0 300117 5SEDALA 161 1 | 56 | 56 | 102.56 |  |  |  | Upgrade 2GEORGE 69/161kV ckt 1 to minimum 58MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 128.84 |  |  |  | Upgrade 3WOODWARD% - 3DIERKS! 115kV ckt 1 to minimum 127MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 29SP 24SP | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | 259 | 285 | 120.95 |  |  |  | Upgrade BIGSTON4 - BROWNSV4 230kV ckt 1 to minimum 345MVA RateB rating. | 29SP 24SP | External | 0 | 5
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 29SP | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 257 | 257 | 105.38 |  |  |  | Upgrade 3DOWNSVILLE - 3STERL2% 115kV ckt 1 to minimum 271MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 29SP | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 560 | 560 | 118.68 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 665MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 132.41 |  |  |  | Upgrade MARYVLE5 - MIDWAY_5 161kV ckt 1 to minimum 264MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603002 WILMART7 115 603188 EASTWD18 115 1 | 20SP 29SP 24SP | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | 224.7 | 247.1 | 104 |  |  |  | Upgrade WILMART7 - EASTWD18 115kV ckt 1 to minimum 257MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 19WP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 121.69 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 19WP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 24SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 121.72 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 871MVA RateB rating. | 24SP | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 24WP 24SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 113.11 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 24WP 24SP | External | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 300 | 330 | 107.85 |  |  |  | Upgrade ST JOE 5 - ST. JOSEPH22 161kV ckt 22 to minimum 356MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 29SP 24SP | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 123 | 123 | 100.79 |  |  |  | Upgrade BVR CHN J1 8 69/161kV ckt 1 to minimum 124MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | 100 | 112 | 121.55 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 29SP 24WP 19WP | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | 84 | 84 | 128.05 |  |  |  | Upgrade VIELE 5 161/69kV ckt 1 to minimum 108MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 29SP | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 169 | 169 | 111 |  |  |  | Upgrade HENRYCO5 - DENMARK5 161kV ckt 1 to minimum 188MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 19WP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 109.38 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 77MVA RateB rating. | 19WP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 29SP 24SP 20G | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | 372 | 372 | 109.69 |  |  |  | Upgrade 5THMHILB1 - 5MOBTAP 161kV ckt 1 to minimum 409MVA RateB rating. | 29SP 24SP 20G | External | 0 | 5
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 24L 20G | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | 199 | 199 | 111.67 |  |  |  | Upgrade BUNGE 5 - HASTING5 161kV ckt 1 to minimum 223MVA RateB rating. |  | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337753 8HS EHV% 500 337740 3HS EHV-E! 115 1 | 20SP | P23:HV-EHV:EES::8HS EHV%:3 | 550 | 550 | 105.01 |  |  |  | Upgrade 8HS EHV% 500/115kV ckt 1 to minimum 578MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 29SP 24WP 24SP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 266 | 266 | 110.3 |  |  |  | Upgrade 3WHT BLUFF! - 3HENSLEY 115kV ckt 1 to minimum 294MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 24WP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 108.77 |  |  |  | Upgrade 3ARCH ST - 3SARDIS# 115kV ckt 1 to minimum 276MVA RateB rating. | 24WP 19WP 20G | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 20SP 29SP 24SP | P11:024:DPC:ALMA2:6 | 201 | 221.1 | 116.34 |  |  |  | Upgrade WABACO 5 - ROCHSTR5 161kV ckt 1 to minimum 258MVA RateB rating. | 20SP 29SP 24SP | External | 18 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 29SP 24SP | P24:345:ITCM:LAKEFLD 885 FUT:MN | 141 | 141 | 127.11 |  |  |  | Upgrade ROCK CO5 - MAGNLIA5 161kV ckt 1 to minimum 180MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 24WP 24SP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 137.36 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 770MVA RateB rating. | 24WP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608616 HILLTOP4 230 997593 HIL1 115 1 | 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 121.39 |  |  |  | Upgrade HILLTOP4 230/115kV ckt 1 to minimum 283MVA RateB rating. | 24SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 20SP 24SP | Base Case | 223 | 248 | 101.2 |  |  |  | Upgrade TRK RIV5 - STONEMAN 161kV ckt 1 to minimum 226MVA/253MVA RateA/RateB rating. | 20SP 24SP | External | 7 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 24SP | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | 95.6 | 95.6 | 100.7 |  |  |  | Upgrade WMU-PRIAM 7 115/69kV ckt 1 to minimum 97MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 29SP 24SP 19WP 20G | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 137.81 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 3 to minimum 35MVA RateB rating. | 29SP 24SP 19WP 20G | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 29SP 24WP 24SP 20G | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | 1099 | 1195 | 123.7 |  |  |  | Upgrade STRANGR7 - 87TH 7 345kV ckt 1 to minimum 1479MVA RateB rating. | 29SP 24WP 24SP 20G | Internal | 0 | 11
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 519 | 519 | 141.08 |  |  |  | Upgrade 6IRONMAN% - 6GYPSY% 230kV ckt 1 to minimum 733MVA RateB rating. | 24L | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 127.59 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 1 to minimum 741MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 29SP 24WP 24SP 19WP | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 251 | 251 | 115.64 |  |  |  | Upgrade 4DELCAMBRE - 4MORIL! 138kV ckt 1 to minimum 291MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 24WP | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | 560 | 669 | 110.86 |  |  |  | Upgrade BLACKHAWK 3 345/161kV ckt 1 to minimum 742MVA RateB rating. | 24WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 29SP 24WP 19WP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 189 | 220.9 | 110.68 |  |  |  | Upgrade FIFTHST7 - MAIN ST7 115kV ckt 1 to minimum 245MVA RateB rating. | 29SP 24WP 19WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 29SP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 145.93 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 103MVA RateB rating. | 29SP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 29SP 24WP 24SP 19WP | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | 450 | 450 | 137.46 |  |  |  | Upgrade KILLDEER3 345/161kV ckt 1 to minimum 619MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 24WP 19WP | Base Case | 26 | 32.5 | 108.94 |  |  |  | Upgrade BROWNSV4 230/42kV ckt 1 to minimum 29MVA RateA rating. | 24WP 19WP | External | 5 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 19WP | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | 223 | 223 | 106.76 |  |  |  | Upgrade ADAMS 5 - BVR CRK5 161kV ckt 1 to minimum 239MVA RateB rating. | 19WP | External | 3 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 29SP 24WP 24SP 19WP | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 251 | 251 | 115.64 |  |  |  | Upgrade 4DELCAMBRE - 4MORIL! 138kV ckt 1 to minimum 291MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 20SP 29SP 24SP 24L 20G | P13:161-69:ITCM:BVR CH5 T1:IA-EC | 127 | 127 | 139.14 |  |  |  | Upgrade 8TH ST.5 - GALENA 5 161kV ckt 1 to minimum 177MVA RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 17
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 29SP | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 560 | 560 | 118.68 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 665MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 20SP 24WP 24SP 19WP | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | 478 | 478 | 128.73 |  |  |  | Upgrade GRE-STANTON4 - SQBUTTE4 230kV ckt 1 to minimum 616MVA RateB rating. | 20SP 24WP 24SP 19WP | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608642 VERNDLE7 115 619701 GRE-ALDRICH7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 77 | 84.7 | 101.85 |  |  |  | Upgrade VERNDLE7 - GRE-ALDRICH7 115kV ckt 1 to minimum 87MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | ALL | Base Case | 335 | 335 | 116.02 |  |  |  | Upgrade 5OVERTON - 5OVERTON 2 161kV ckt Z to minimum 389MVA/429MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 20
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 105.29 |  |  |  | Upgrade 3SHERRILL - 3ENGLAND# 115kV ckt 1 to minimum 104MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 24WP 24SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 117.09 |  |  |  | Upgrade GRE-CHUBLAK3 345/115kV ckt 1 to minimum 525MVA RateB rating. | 24WP 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603103 SCOTTCO7 115 997635 SCOTTCO3 115 9 | 29SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 114.95 |  |  |  | Upgrade SCOTTCO7 - SCOTTCO3 115kV ckt 9 to minimum 746MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 72 | 72 | 104.09 |  |  |  | Upgrade ADAMS 8 69/161kV ckt 1 to minimum 75MVA/100MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 31 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601055 SCOTTCO3 345 997636 SCOTTCO3 115 9 | 24SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 109.25 |  |  |  | Upgrade SCOTTCO3 345/115kV ckt 9 to minimum 709MVA RateB rating. | 24SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 29SP | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 123 | 123 | 100.04 |  |  |  | Upgrade BVR CHN J1 8 69/161kV ckt 1 to minimum 124MVA RateB rating. |  | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 29SP 24SP | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 327 | 327 | 115.53 |  |  |  | Upgrade TOLEDO 5 - M-TOWN 5 161kV ckt 1 to minimum 378MVA RateB rating. | 29SP | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 29SP 24SP | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | 172 | 172 | 115.85 |  |  |  | Upgrade 5SRIVER - 5PALMYR_AI 161kV ckt 1 to minimum 200MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 20SP 29SP 24SP | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | 230 | 230 | 111.74 |  |  |  | Upgrade BIGSTON7 - HIWY12 7 115kV ckt 1 to minimum 258MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608642 VERNDLE7 115 619701 GRE-ALDRICH7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 77 | 84.7 | 101.85 |  |  |  | Upgrade VERNDLE7 - GRE-ALDRICH7 115kV ckt 1 to minimum 87MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 20SP 29SP 24SP | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | 84 | 84 | 106.78 |  |  |  | Upgrade 2CDRCRST 69/161kV ckt 1 to minimum 90MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 29SP | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 327 | 327 | 109.63 |  |  |  | Upgrade TOLEDO 5 - BL.PLN.5 161kV ckt 1 to minimum 359MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 24WP 24SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 117.09 |  |  |  | Upgrade GRE-CHUBLAK3 345/115kV ckt 1 to minimum 525MVA RateB rating. | 24WP 24SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 19WP | P13:161-69:EES-EAI:HERGET:AT2 | 100 | 112 | 121.34 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 136MVA RateB rating. | 19WP | External | 3 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 601028 EAU CL 3 345 997642 EAU CL 3 161 9 | 24WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 104.36 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 350MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300073 5GENTRY 161 300104 5NODWAY 161 1 | ALL | Base Case | 252 | 252 | 108.31 |  |  |  | Upgrade 5GENTRY - 5NODWAY 161kV ckt 1 to minimum 273MVA/248MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 17
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 608686 15TH AV7 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 80 | 80 | 108.56 |  |  |  | Upgrade HILLTOP7 - 15TH AV7 115kV ckt 1 to minimum 87MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 19WP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 100.59 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 705MVA RateB rating. |  | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | 29SP | 92681: 515300 FTSMTHE5 161 515301 FTSMTHW5 161 1 515300 FTSMTHE5 161 515301 FTSMTHW5 161 2 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 515301 FTSMTHW5 161 998255 FTSMITH4 161 4 515301 FTSMTHW5 161 998254 FTSMITH5 161 5 515299 BEVYTAP5 161 515300 FTSMTHE5 161 1 515300 FTSMTHE5 161 515310 QUANXTP5 161 1 515300 FTSMTHE5 161 515345 COLONY 5 161 1 515300 FTSMTHE5 161 998257 FTSMITH3 161 3 515300 FTSMTHE5 161 998256 FTSMTH6 161 6 | 106 | 106 | 103.09 |  |  |  | Upgrade 3CHEETAH% - 3HS VILLAGE 115kV ckt 1 to minimum 110MVA RateB rating. | 29SP | External | 1 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 29SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 101.17 |  |  |  | Upgrade 4E_OPELUSAS! - 4COLTON 138kV ckt 1 to minimum 228MVA RateB rating. | 29SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 24WP 24SP 19WP | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | 74.7 | 74.7 | 108.76 |  |  |  | Upgrade LIME CK L1 5 161/69kV ckt 1 to minimum 82MVA RateB rating. | 24WP 24SP 19WP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 523961 POTTER_CO 7 345 998118 WAUK 90343-A 230 1 | 24L | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | 516 | 559 | 103.24 |  |  |  | Upgrade POTTER_CO 7 345/230kV ckt 1 to minimum 578MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 29SP | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | 95.6 | 95.6 | 104.17 |  |  |  | Upgrade WMU-PRIAM 7 115/69kV ckt 1 to minimum 100MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 20SP 24SP 24L 20G | Base Case | 203 | 203 | 107.77 |  |  |  | Upgrade 5FAIRPT - 5HICKCK 161kV ckt 1 to minimum 219MVA/255MVA RateA/RateB rating. | 20SP 24L 20G | External | 0 | 16
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 19WP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 121.69 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 19WP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 24SP | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | 330 | 330 | 106.37 |  |  |  | Upgrade LORE 5 - TRK RIV5 161kV ckt 1 to minimum 352MVA RateB rating. |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 24WP 24SP 24L | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | 335 | 335 | 128.98 |  |  |  | Upgrade HAZLTON L1 5 - BLACKHAWK 5 161kV ckt 1 to minimum 433MVA RateB rating. | 24WP | External | 0 | 9
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 29SP | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | 995 | 995 | 105.28 |  |  |  | Upgrade HAZLTON3 - MITCHLCO3 345kV ckt 1 to minimum 1048MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 346156 1HITT 34.5 344270 5HITT 161 1 | 20SP 29SP 24SP | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | 56 | 56 | 113.91 |  |  |  | Upgrade 1HITT 35/161kV ckt 1 to minimum 64MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 19WP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 330 | 334.6 | 119.37 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 400MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 20SP 29SP 24WP 24SP | Base Case | 108 | 108 | 110.38 |  |  |  | Upgrade GRE-JOHNJCT7 - ORTONVL7 115kV ckt 1 to minimum 120MVA/162MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 21
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997055 GLENHAM TR1 115 1 | 20SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 102.54 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 32MVA RateB rating. | 20SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 29SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 121.26 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 406MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 29SP 20G | P23:345:MEC:LOUISA 964 | 1195 | 1304 | 102.78 |  |  |  | Upgrade HILLS 3 - SUB 92 3 345kV ckt 1 to minimum 1341MVA RateB rating. | 29SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 20SP 29SP 24WP 24SP 24L 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 120.63 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 2 to minimum 700MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 20SP 29SP 24SP | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | 310 | 310 | 107.53 |  |  |  | Upgrade 5MOOREFIELD - 5ISES% 161kV ckt 1 to minimum 334MVA RateB rating. | 20SP 29SP 24SP | External | 9 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 601028 EAU CL 3 345 997646 EAU CL 3 161 9 | 24L | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 105.12 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 352MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 29SP 24SP 24L 20G | P23:345:MEC:SYCAMORE 905 | 373 | 395 | 123.44 |  |  |  | Upgrade GRIMES 5 - GRNGRTP5 161kV ckt 1 to minimum 488MVA RateB rating. | 29SP 24SP 24L 20G | External | 0 | 4
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 601028 EAU CL 3 345 997656 EAU CL 3 161 9 | 20G | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 114.21 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 383MVA RateB rating. | 20G | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 20SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 111.51 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 79MVA RateB rating. | 20SP | External | 2 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 19WP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 111.61 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 79MVA RateB rating. | 19WP | External | 2 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 29SP 24SP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470.5 | 517.5 | 121.94 |  |  |  | Upgrade 98L TAP4 - IRONRNG4 230kV ckt 1 to minimum 632MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 24L | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 145.02 |  |  |  | Upgrade EASTOWN5 - EASTOWNE11 161kV ckt 11 to minimum 639MVA RateB rating. | 24L | Internal | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 29SP 24WP 24SP 19WP 20G | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 113.14 |  |  |  | Upgrade 3HENSLEY - 3ARCH ST 115kV ckt 1 to minimum 287MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 29SP 24SP | Base Case | 78 | 85.8 | 106.48 |  |  |  | Upgrade BURNETT7 - GRE-KNFFLTP7 115kV ckt 1 to minimum 84MVA/120MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 29SP | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 276 | 276 | 122.18 |  |  |  | Upgrade ABBOTT 5 - TRAER 5 161kV ckt 1 to minimum 338MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997049 GLENHAM TR1 115 1 | 29SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 113.07 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 20SP 24SP | Base Case | 690 | 690 | 178.94 |  |  |  | Upgrade RAUN 3 345/24kV ckt 1 to minimum 1235MVA RateA rating. | 20SP 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 24WP 19WP | Base Case | 26 | 32.5 | 108.94 |  |  |  | Upgrade BROWNSV4 230/42kV ckt 1 to minimum 29MVA RateA rating. | 24WP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 29SP | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 560 | 560 | 118.27 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 663MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 24L | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 145.02 |  |  |  | Upgrade EASTOWN5 - EASTOWNE11 161kV ckt 11 to minimum 639MVA RateB rating. | 24L | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 29SP 24SP | P23:345:MEC:OAK GROVE 901 | 248 | 248 | 124.01 |  |  |  | Upgrade SB 18 5 - SB 85 5 161kV ckt 1 to minimum 308MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 24WP 24SP 24L | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | 335 | 335 | 128.98 |  |  |  | Upgrade HAZLTON L1 5 - BLACKHAWK 5 161kV ckt 1 to minimum 433MVA RateB rating. | 24WP | External | 0 | 9
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 29SP 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 114.36 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 2 to minimum 301MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 281.6 | 281.6 | 120.4 |  |  |  | Upgrade COON CK7 - TWIN LK7 115kV ckt 1 to minimum 340MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 29SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | 500 | 500 | 108.74 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 1 to minimum 544MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 24WP | Base Case | 26 | 32.5 | 107.68 |  |  |  | Upgrade BROWNSV4 230/42kV ckt 1 to minimum 28MVA/36MVA RateA/RateB rating. | 24WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 29SP | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | 95.6 | 95.6 | 104.17 |  |  |  | Upgrade WMU-PRIAM 7 115/69kV ckt 1 to minimum 100MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 29SP 24SP 19WP 20G | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 137.9 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 2 to minimum 35MVA RateB rating. | 29SP 24SP 19WP 20G | External | 0 | 11
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 29SP | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | 120 | 120 | 102.22 |  |  |  | Upgrade 3BERNICE - 3JNCTN CITY! 115kV ckt 1 to minimum 123MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 235 | 235 | 100.59 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 1 to minimum 237MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 20SP 29SP 24SP | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 33.6 | 41 | 121.78 |  |  |  | Upgrade BELLCTR5 161/69kV ckt 2 to minimum 50MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 19WP 20G | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 92 | 92 | 105.15 |  |  |  | Upgrade COTTNTP7 - GRE-BERGNTP7 115kV ckt 1 to minimum 97MVA RateB rating. | 19WP 20G | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 24WP 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 500 | 550 | 108.95 |  |  |  | Upgrade HAWTHN5 - HAWTHORN20 161kV ckt 20 to minimum 600MVA RateB rating. | 24WP 24SP | Internal | 0 | 8
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 24L | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 203 | 203 | 102.26 |  |  |  | Upgrade 5CHILLI - 5HICKCK 161kV ckt 1 to minimum 208MVA RateB rating. |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 29SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 102.27 |  |  |  | Upgrade HUC-MCLEOD 4 230/115kV ckt 1 to minimum 192MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 29SP 24WP 19WP | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | 335 | 335 | 104.84 |  |  |  | Upgrade LIME CK L1 5 - LIME CK L2 5 161kV ckt Z to minimum 352MVA RateB rating. | 29SP 19WP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 144.89 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 102MVA RateB rating. | 24WP 24SP | External | 0 | 11
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 101.76 |  |  |  | Upgrade 3MABLVALE-E! - 3SARDIS# 115kV ckt 1 to minimum 258MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 122.38 |  |  |  | Upgrade MIDWAY_5 - AVENUECTY 5 161kV ckt 1 to minimum 244MVA RateB rating. | 20G | Internal | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 225 | 225 | 104.96 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 2 to minimum 237MVA RateB rating. | 20SP | External | 1 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 64 | 64 | 125.49 |  |  |  | Upgrade 2HOLDEN 69/161kV ckt 1 to minimum 81MVA RateB rating. | 20SP 29SP 24WP 24SP | External | 8 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 20SP 29SP 24SP | Base Case | 302 | 332 | 106.12 |  |  |  | Upgrade SENECA 5 - GENOA 5 161kV ckt 1 to minimum 321MVA/363MVA RateA/RateB rating. | 20SP 29SP 24SP | External | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 29SP 24WP 24SP 19WP 20G | Base Case | 785 | 785 | 101.37 |  |  |  | Upgrade MINGO 7 - REDWILO3 345kV ckt 1 to minimum 796MVA/809MVA RateA/RateB rating. | 29SP 24SP 19WP | Internal | 0 | 13
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 24SP | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 293 | 318 | 100.3 |  |  |  | Upgrade TERRACE5 - BARBER 5 161kV ckt 1 to minimum 319MVA RateB rating. |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 29SP | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 5: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 102.39 |  |  |  | Upgrade GRAVL ISLE 8 69/161kV ckt 6 to minimum 83MVA RateB rating. | 29SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 24WP | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | 241 | 241 | 104.6 |  |  |  | Upgrade 4STONGAT! - 4MID CO% 138kV ckt 1 to minimum 253MVA RateB rating. | 24WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 29SP 24SP | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | 386 | 416 | 109.82 |  |  |  | Upgrade ELEESV 6 - RODEMR 6 230kV ckt 1 to minimum 457MVA RateB rating. | 29SP 24SP | External | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 20SP 29SP 24SP | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | 310 | 310 | 107.53 |  |  |  | Upgrade 5MOOREFIELD - 5ISES% 161kV ckt 1 to minimum 334MVA RateB rating. | 20SP 29SP 24SP | External | 9 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 20SP 29SP 24SP 24L 20G | Base Case | 227 | 227 | 101.46 |  |  |  | Upgrade 5FAIRPT - 5OSBORN 161kV ckt 1 to minimum 231MVA/311MVA RateA/RateB rating. | 20SP 24SP 24L 20G | External | 0 | 15
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 20SP 29SP 24SP 24L 20G | Base Case | 227 | 227 | 101.46 |  |  |  | Upgrade 5FAIRPT - 5OSBORN 161kV ckt 1 to minimum 231MVA/311MVA RateA/RateB rating. | 20SP 24SP 24L 20G | External | 0 | 15
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 346156 1HITT 34.5 344270 5HITT 161 1 | 20SP 29SP 24SP | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | 56 | 56 | 113.91 |  |  |  | Upgrade 1HITT 35/161kV ckt 1 to minimum 64MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 113.4 |  |  |  | Upgrade 5LATHRP - 5MOCITY 161kV ckt 1 to minimum 258MVA RateB rating. | 20G | External | 0 | 4
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 19WP | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | 223 | 223 | 106.76 |  |  |  | Upgrade ADAMS 5 - BVR CRK5 161kV ckt 1 to minimum 239MVA RateB rating. | 19WP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 20SP 24SP | Base Case | 690 | 690 | 178.94 |  |  |  | Upgrade RAUN 3 345/24kV ckt 1 to minimum 1235MVA RateA rating. | 20SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635601 GRIMES 5 161 997475 DGG9T1 161 1 | 29SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 105.36 |  |  |  | Upgrade GRIMES 5 - DGG9T1 161kV ckt 1 to minimum 738MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 29SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 113.8 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 29SP | External | 2 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 140.83 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 1 to minimum 592MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 144.89 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 102MVA RateB rating. | 24WP 24SP | External | 0 | 11
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 20SP 29SP 24SP 24L 20G | P12:345:MEC:WALCOTT-HILLS-LOUISA | 73 | 73 | 120.54 |  |  |  | Upgrade SUTLIFF7 - CALAMUS7 115kV ckt 1 to minimum 88MVA RateB rating. | 20SP 29SP 24SP 24L | External | 0 | 20
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | ALL | Base Case | 201 | 201 | 114.28 |  |  |  | Upgrade FRANKLN5 - WALL LK5 161kV ckt 1 to minimum 230MVA/245MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 20G | External | 0 | 32
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 24WP 24SP | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 126.69 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 906MVA RateB rating. | 24SP | Internal | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 29SP 20G | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | 240 | 240 | 111.14 |  |  |  | Upgrade BARTON5 - LIME CK L2 5 161kV ckt 1 to minimum 267MVA RateB rating. | 29SP 20G | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 29SP 24WP 24SP 24L 20G | P23:345:ITCM:HCKRYCK:FUT2 | 325 | 325 | 172.33 |  |  |  | Upgrade LORE 5 - HCKRYCK5 161kV ckt 1 to minimum 561MVA RateB rating. | 29SP 24WP 24L 20G | External | 0 | 13
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 24L 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 212 | 212 | 120.36 |  |  |  | Upgrade JASPER 5 - NEANKNY5 161kV ckt 1 to minimum 256MVA RateB rating. | 24L 20G | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 19WP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 102.65 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 719MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997476 DGG9T1 161 1 | 24SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 104.27 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 730MVA RateB rating. | 24SP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 20SP 24SP | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 105.25 |  |  |  | Upgrade 2WSTPL3 69/161kV ckt 1 to minimum 59MVA RateB rating. | 20SP 24SP | External | 4 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 29SP 24SP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470.5 | 517.5 | 121.94 |  |  |  | Upgrade 98L TAP4 - IRONRNG4 230kV ckt 1 to minimum 632MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 20SP 29SP 24SP 24L 20G | Base Case | 1073 | 1195 | 109.2 |  |  |  | Upgrade ST JOE 3 - COOPER 3 345kV ckt 1 to minimum 1172MVA/1454MVA RateA/RateB rating. | 29SP 24SP 24L 20G | Internal | 0 | 14
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 1188.5 | 1188.5 | 105.57 |  |  |  | Upgrade AS KING3 - EAU CL 3 345kV ckt 1 to minimum 1255MVA/1307MVA RateA/RateB rating. | 20SP 24WP 24SP | External | 0 | 12
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 29SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 121.28 |  |  |  | Upgrade GRE-CHUBLAK3 345/115kV ckt 1 to minimum 544MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 602021 EAU CLA5 161 997643 EAU CL 3 161 9 | 19WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 118.07 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 396MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 29SP 24SP | Base Case | 78 | 78 | 108.33 |  |  |  | Upgrade MDWLNDS7 - BURNETT7 115kV ckt 1 to minimum 85MVA/95MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 11
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 24L | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 441 | 441 | 128.58 |  |  |  | Upgrade 6BLPNT! - 6GYPSY% 230kV ckt 1 to minimum 568MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 29SP | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 560 | 560 | 118.27 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 663MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 24WP 24SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 113.11 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 24WP 24SP | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 20SP 29SP 24WP 24SP 19WP | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 117.68 |  |  |  | Upgrade 2KINGDM 69/161kV ckt 2 to minimum 30MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 29SP 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 114.36 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 2 to minimum 301MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 29SP 24SP | P23:345:MEC:OAK GROVE 901 | 248 | 248 | 124.01 |  |  |  | Upgrade SB 18 5 - SB 85 5 161kV ckt 1 to minimum 308MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 24SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | 500 | 500 | 107.27 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 1 to minimum 537MVA RateB rating. | 24SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 29SP 24SP | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | 143.4 | 143.4 | 112.61 |  |  |  | Upgrade YORKTON 4 230/138kV ckt 1 to minimum 162MVA RateB rating. | 29SP 24SP | External | 6 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 29SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 121.61 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 870MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 19WP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 330 | 334.6 | 119.37 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 400MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 29SP | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 650 | 715 | 121.61 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 870MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 29SP 24WP 24SP | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | 84 | 84 | 103.57 |  |  |  | Upgrade 2LAMR 69/161kV ckt 1 to minimum 87MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 110.62 |  |  |  | Upgrade 3DIERKS! - 3SHERRILL 115kV ckt 1 to minimum 109MVA RateB rating. | 20SP 29SP 24SP | External | 3 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 29SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | 70 | 70 | 113.8 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 80MVA RateB rating. | 29SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | ALL | Base Case | 90 | 90 | 126.79 |  |  |  | Upgrade M-TOWN 7 - BLRSTWN7 115kV ckt 1 to minimum 115MVA/146MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 32
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 600180 J587_GEN2 34.5 603305 J587 BLZSTR2 115 2 | 20SP | Base Case | 100 | 120 | 100.85 |  |  |  | Upgrade J587_GEN2 35/115kV ckt 2 to minimum 101MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 347840 5NIOTA 161 631216 WEVER5 161 1 | 20SP 29SP 24SP 24L | Base Case | 175 | 175 | 101.09 |  |  |  | Upgrade 5NIOTA - WEVER5 161kV ckt 1 to minimum 177MVA/265MVA RateA/RateB rating. | 20SP 29SP 24SP | External | 0 | 17
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 20SP 29SP 24SP | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | 131 | 131 | 111.08 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 1 to minimum 146MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 600178 J460_GEN2 34.5 601088 BLZNG STR1 3 345 2 | 20SP | Base Case | 100 | 120 | 100.95 |  |  |  | Upgrade J460_GEN2 35/345kV ckt 2 to minimum 101MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 24WP 24SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 142.02 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 100MVA RateB rating. | 24WP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 20SP 19WP | P13:161-69:EES-EAI:HERGET:AT1 | 100 | 112 | 118.43 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 133MVA RateB rating. | 20SP 19WP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 29SP | P23:345:MEC:LOUISA 924 | 956 | 1152 | 106.06 |  |  |  | Upgrade SB 56 3 - WALCOTT3 345kV ckt 1 to minimum 1222MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 29SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 103.11 |  |  |  | Upgrade HUC-MCLEOD 7 - 230/115 115kV ckt 1 to minimum 193MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 20SP 24SP | Base Case | 223 | 248 | 101.2 |  |  |  | Upgrade TRK RIV5 - STONEMAN 161kV ckt 1 to minimum 226MVA/253MVA RateA/RateB rating. | 20SP 24SP | External | 7 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 29SP 24WP 20G | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 162 | 162 | 151.87 |  |  |  | Upgrade VIELE 5 - DENMARK5 161kV ckt 1 to minimum 247MVA RateB rating. | 29SP 24WP | External | 0 | 8
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 101.76 |  |  |  | Upgrade 3MABLVALE-E! - 3SARDIS# 115kV ckt 1 to minimum 258MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 301422 2LEE 69.0 631216 WEVER5 161 1 | 29SP | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | 84 | 84 | 113.38 |  |  |  | Upgrade 2LEE 69/161kV ckt 1 to minimum 96MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 24SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 109.41 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 367MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 24SP | Base Case | 182 | 182 | 105.27 |  |  |  | Upgrade HIBBARD7 - WNTR ST7 115kV ckt 1 to minimum 192MVA/202MVA RateA/RateB rating. |  | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 24WP 24SP | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | 500 | 550 | 110.55 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 609MVA RateB rating. | 24WP 24SP | Internal | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 24SP 24L 20G | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 196 | 196 | 154.33 |  |  |  | Upgrade HAZLTON L2 5 - WASHBRN5 161kV ckt 1 to minimum 303MVA RateB rating. | 24L 20G | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 344535 7ENON 345 345230 7MONTGMRY 345 1 | 29SP | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | 956 | 956 | 100.78 |  |  |  | Upgrade 7ENON - 7MONTGMRY 345kV ckt 1 to minimum 964MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 29SP 24WP 24SP | P23:345:XEL:8P33 KOL | 222.7 | 222.7 | 109.39 |  |  |  | Upgrade ROSE PL7 - TERMINL7 115kV ckt 1 to minimum 244MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 20SP 29SP 24WP 24SP | Base Case | 92 | 92 | 104.26 |  |  |  | Upgrade GRE-JOHNJCT7 - MORRIS 7 115kV ckt 1 to minimum 96MVA/133MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP | External | 0 | 18
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 24WP 24SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 110.7 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 78MVA RateB rating. | 24WP 24SP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 24WP 24SP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 137.36 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 770MVA RateB rating. | 24WP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 29SP 24WP 24SP 19WP 20G | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | 25 | 25 | 127.76 |  |  |  | Upgrade 2STURGN 69/161kV ckt 2 to minimum 32MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 14
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP 19WP | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 56 | 56 | 146.59 |  |  |  | Upgrade 2HOLDEN 69/161kV ckt 1 to minimum 83MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 29SP 24SP | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | 326 | 326 | 115.62 |  |  |  | Upgrade ARNOLD 5 - DWNTWN IND5 161kV ckt 1 to minimum 377MVA RateB rating. | 29SP 24SP | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 20SP | P23:500:EES-EAI:ARK_NU:B5106 | 396 | 396 | 112.01 |  |  |  | Upgrade 5RUSSELVL.E! - 5RUSSELVL.N 161kV ckt 1 to minimum 444MVA RateB rating. | 20SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 24WP | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | 80 | 88 | 108.24 |  |  |  | Upgrade EDGETAP7 - PEL RPD7 115kV ckt 1 to minimum 96MVA RateB rating. | 24WP | External | 0 | 3
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 20G | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 650 | 715 | 114.76 |  |  |  | Upgrade NASHUA 7 345/161kV ckt 11 to minimum 821MVA RateB rating. | 20G | Internal | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 29SP | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | 143.4 | 143.4 | 104.18 |  |  |  | Upgrade YORKTON 4 230/138kV ckt 1 to minimum 150MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 24SP | Base Case | 144 | 144 | 101.59 |  |  |  | Upgrade HOYT LK7 - 43L TAP7 115kV ckt 1 to minimum 147MVA/150MVA RateA/RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 29SP 24SP | Base Case | 78 | 78 | 108.33 |  |  |  | Upgrade MDWLNDS7 - BURNETT7 115kV ckt 1 to minimum 85MVA/95MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 11
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 24L 20G | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 334 | 334 | 139.77 |  |  |  | Upgrade EAST 5 - EASTOWN5 161kV ckt 1 to minimum 467MVA RateB rating. | 24L | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | ALL | Base Case | 956 | 1152 | 129.99 |  |  |  | Upgrade DIAMOND TRL3 - HILLS-DT-RX3 345kV ckt 1 to minimum 1243MVA/1540MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 30
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608616 HILLTOP4 230 997593 HIL1 115 1 | 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 121.39 |  |  |  | Upgrade HILLTOP4 230/115kV ckt 1 to minimum 283MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 20SP 29SP 24SP 24L 20G | Base Case | 206 | 206 | 110.64 |  |  |  | Upgrade WRIGHT 5 - WALL LK5 161kV ckt 1 to minimum 228MVA/270MVA RateA/RateB rating. | 20SP 29SP 24SP 24L 20G | External | 0 | 27
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 29SP | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | 227 | 227 | 104.61 |  |  |  | Upgrade 5BIG CK - 5WARENTN 161kV ckt 1 to minimum 238MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615135 G619TAM7 115 618203 GRE-TAMARAC7 115 1 | 20SP | Base Case | 50 | 50 | 100.94 |  |  |  | Upgrade G619TAM7 - GRE-TAMARAC7 115kV ckt 1 to minimum 51MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 24SP | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 77 | 84.7 | 103.71 |  |  |  | Upgrade GRE-KIMBRLY7 - GRE-AITKIN 7 115kV ckt 1 to minimum 88MVA RateB rating. |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 29SP 24SP | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 327 | 327 | 115.53 |  |  |  | Upgrade TOLEDO 5 - M-TOWN 5 161kV ckt 1 to minimum 378MVA RateB rating. | 29SP | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 29SP 24SP 24L 19WP 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 311 | 311 | 122.77 |  |  |  | Upgrade POWESHK5 - REASNOR5 161kV ckt 1 to minimum 382MVA RateB rating. | 29SP 24SP 24L 19WP 20G | External | 0 | 20
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | 446 | 446 | 104.64 |  |  |  | Upgrade SIBLEY 5 - SIBLEYPL 161kV ckt 1 to minimum 467MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 602021 EAU CLA5 161 997646 EAU CL 3 161 9 | 24L | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 108.17 |  |  |  | Upgrade EAU CLA5 - EAU CL 3 161kV ckt 9 to minimum 362MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | ALL | Base Case | 72 | 72 | 104.1 |  |  |  | Upgrade ADAMS 8 69/161kV ckt 1 to minimum 75MVA/102MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 33
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608672 HILLTOP7 115 997592 HIL1 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 112.08 |  |  |  | Upgrade HILLTOP7 - HIL1 115kV ckt 1 to minimum 262MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 24L 19WP | P23:345:MEC:SYCAMORE 905 | 335 | 335 | 106.85 |  |  |  | Upgrade 100 54 5 - JOHNSTON 5 161kV ckt 1 to minimum 358MVA RateB rating. | 19WP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 141.17 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 2 to minimum 593MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 640065 AXTELL 3 345 997459 AXTELL T1 115 1 | 24WP | P42:345:NPPD:BKR-AXT-3308 | 336 | 336 | 107.02 |  |  |  | Upgrade AXTELL 3 345/115kV ckt 1 to minimum 360MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 24L | Base Case | 42 | 42 | 102.91 |  |  |  | Upgrade FONDULAC - HIBBARD7 115kV ckt 1 to minimum 44MVA/47MVA RateA/RateB rating. | 24L | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 20SP 29SP 24SP | P12:345:MEC:WALCOTT-HILLS-LOUISA | 80 | 80 | 112.35 |  |  |  | Upgrade PRAR CK7 - SUTLIFF7 115kV ckt 1 to minimum 90MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620263 FORMN 7 115 997492 230/115 115 1 | 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1: 620327 HANKSON4 230 620363 FORMAN 4 230 1 | 112 | 132 | 105.6 |  |  |  | Upgrade FORMN 7 - 230/115 115kV ckt 1 to minimum 140MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 29SP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 143.05 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 101MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 123.42 |  |  |  | Upgrade EASTOWN5 - EASTOWNE11 161kV ckt 11 to minimum 544MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 158.26 |  |  |  | Upgrade 3WHT BLUFF! - 3WRIGHTSVLE! 115kV ckt 1 to minimum 401MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 29SP | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | 84 | 84 | 122.31 |  |  |  | Upgrade TRAER 5 161/69kV ckt 1 to minimum 103MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 635600 GRIMES 3 345 997475 DGG9T1 161 1 | 29SP | P23:345:MEC:SYCAMORE 905 | 560 | 700 | 108.41 |  |  |  | Upgrade GRIMES 3 345/161kV ckt 1 to minimum 759MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 19WP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 105.23 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 33MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 29SP 24SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 107.9 |  |  |  | Upgrade 3ELD DONAN - 3ELD MONSNTO 115kV ckt 1 to minimum 172MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 29SP 24SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233.8 | 121.34 |  |  |  | Upgrade 98L TAP4 - HILLTOP4 230kV ckt 1 to minimum 284MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 29SP 24WP 24SP 19WP 20G | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | 25 | 25 | 126.93 |  |  |  | Upgrade 2STURGN 69/161kV ckt 1 to minimum 32MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 14
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 20G | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 650 | 715 | 113.92 |  |  |  | Upgrade NASHUA-5 - NASHUA11 161kV ckt 11 to minimum 815MVA RateB rating. | 20G | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 24SP 24L 20G | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | 325 | 325 | 106.86 |  |  |  | Upgrade DMOINES5 - RISING SUN 5 161kV ckt 1 to minimum 348MVA RateB rating. | 24L | External | 0 | 10
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 400 | 440 | 127.83 |  |  |  | Upgrade EASTOWN7 345/161kV ckt 11 to minimum 563MVA RateB rating. | 20G | Internal | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 29SP 24SP | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | 225 | 225 | 107.27 |  |  |  | Upgrade 4E_OPELUSAS! - 4CHAMPAGNE! 138kV ckt 1 to minimum 242MVA RateB rating. | 29SP 24SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 29SP | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 299 | 299 | 107.21 |  |  |  | Upgrade ABBOTT 5 - M-TOWN 5 161kV ckt 1 to minimum 321MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | 20SP | Base Case | 325 | 325 | 144.6 |  |  |  | Upgrade 1THLG2 22.0/161kV ckt 1 to minimum 470MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | ALL | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 141.17 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 2 to minimum 593MVA RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 7
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 29SP | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 5: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 102.39 |  |  |  | Upgrade GRAVL ISLE 8 69/161kV ckt 6 to minimum 83MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 121.9 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 137MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 9
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 29SP 24WP 24SP 19WP | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 30 | 30 | 187.18 |  |  |  | Upgrade 2MARYVL 69/161kV ckt 1 to minimum 57MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 10
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 20SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 214.1 | 214.1 | 107.16 |  |  |  | Upgrade REDROCK7 - GLENMONT 115kV ckt 1 to minimum 230MVA RateB rating. | 20SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 29SP 24SP | P23:345:MEC:SYCAMORE 905 | 373 | 395 | 105.4 |  |  |  | Upgrade GRNGRTP5 - 100 54 5 161kV ckt 1 to minimum 417MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 29SP 24WP 24SP 19WP 20G | Base Case | 785 | 785 | 101.37 |  |  |  | Upgrade MINGO 7 - REDWILO3 345kV ckt 1 to minimum 796MVA/809MVA RateA/RateB rating. | 29SP 24SP 19WP | Internal | 0 | 13
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 29SP | P23:345:GRE:PVS 19JB1 | 500 | 500 | 110.69 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 1 to minimum 554MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 20SP 29SP 24WP 24SP 19WP | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 72 | 72 | 176.07 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 2 to minimum 127MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 20 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 661035 GLENHAM7 115 997045 GLENHAM TR1 115 1 | 29SP | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | 25 | 31 | 115.88 |  |  |  | Upgrade GLENHAM7 - GLENHAM TR1 115kV ckt 1 to minimum 36MVA RateB rating. | 29SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 24SP 24L 20G | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 196 | 196 | 154.33 |  |  |  | Upgrade HAZLTON L2 5 - WASHBRN5 161kV ckt 1 to minimum 303MVA RateB rating. | 24L 20G | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 29SP 24SP | Base Case | 78 | 85.8 | 106.48 |  |  |  | Upgrade BURNETT7 - GRE-KNFFLTP7 115kV ckt 1 to minimum 84MVA/120MVA RateA/RateB rating. | 29SP 24SP | External | 0 | 10
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 29SP 24WP 24SP 19WP 20G | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | 1000 | 1136 | 122.56 |  |  |  | Upgrade ST JOE 3 - NASHUA 7 345kV ckt 1 to minimum 1393MVA RateB rating. | 29SP 24WP 24SP 19WP | Internal | 0 | 13
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608642 VERNDLE7 115 615567 GRE-WINGRIV7 115 1 | 20SP | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | 98 | 107.8 | 107.64 |  |  |  | Upgrade VERNDLE7 - GRE-WINGRIV7 115kV ckt 1 to minimum 117MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 29SP | Base Case | 1195 | 1195 | 104.97 |  |  |  | Upgrade HAZLTON3 - HCKRYCK3 345kV ckt 1 to minimum 1255MVA/1392MVA RateA/RateB rating. | 29SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 29SP 24SP | P23:345:XEL:8P4 ASK | 229.9 | 252.8 | 103.19 |  |  |  | Upgrade BAYTOWN7 - LONG LK7 115kV ckt 1 to minimum 261MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 29SP 24WP 24SP 19WP | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 114.37 |  |  |  | Upgrade WAPELLO5 - OTTUMWA5 161kV ckt 2 to minimum 384MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601019 COON CK3 345 601024 TERMINL3 345 1 | 20SP 29SP 24SP | P23:345:XEL:8M38 CNC | 1195.1 | 1195.1 | 118.5 |  |  |  | Upgrade COON CK3 - TERMINL3 345kV ckt 1 to minimum 1417MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 29SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 102.27 |  |  |  | Upgrade HUC-MCLEOD 4 230/115kV ckt 1 to minimum 192MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601019 COON CK3 345 601024 TERMINL3 345 1 | 20SP 29SP 24SP | P23:345:XEL:8M38 CNC | 1195.1 | 1195.1 | 118.5 |  |  |  | Upgrade COON CK3 - TERMINL3 345kV ckt 1 to minimum 1417MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 9
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 19WP | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | 500 | 550 | 110.91 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 20 to minimum 611MVA RateB rating. | 19WP | Internal | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 606 | 606 | 106.51 |  |  |  | Upgrade 5FAIRPT 161/345kV ckt 3 to minimum 646MVA RateB rating. |  | External | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 24WP 19WP | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | 641 | 641 | 105.64 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 2 to minimum 678MVA RateB rating. | 24WP 19WP | External | 6 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 301422 2LEE 69.0 631216 WEVER5 161 1 | 29SP | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | 84 | 84 | 113.38 |  |  |  | Upgrade 2LEE 69/161kV ckt 1 to minimum 96MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 29SP | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 123.59 |  |  |  | Upgrade ADAMS 3 345/161kV ckt 9 to minimum 414MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 20SP | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | 310 | 310 | 100.1 |  |  |  | Upgrade 5BATESVLE AR - 5MOOREFIELD 161kV ckt 1 to minimum 311MVA RateB rating. | 20SP | External | 3 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 20SP | 637035 J524 161 3WXFMR J524 1: 637035 J524 161 997470 J524 34.5 1 637032 J524 COL2 34.5 997470 J524 34.5 1 637034 J524 TERT 13.2 997470 J524 34.5 1 | 560 | 560 | 103.38 |  |  |  | Upgrade WEBSTER5 - WEB AB 161kV ckt 1 to minimum 579MVA RateB rating. | 20SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 29SP | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | 550 | 605 | 110.3 |  |  |  | Upgrade HAWTH 7 345/161kV ckt 22 to minimum 668MVA RateB rating. | 29SP | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 29SP 24WP 24SP 19WP 20G | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | 25 | 25 | 126.93 |  |  |  | Upgrade 2STURGN 69/161kV ckt 1 to minimum 32MVA RateB rating. | 29SP 24WP 24SP 19WP 20G | External | 0 | 14
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 646254 S1254 5 161 646281 S1281 5 161 1 | 20SP 29SP 24WP 24SP 19WP | P1-2 POI - S1363 | 298 | 298 | 121.85 |  |  |  | Upgrade S1254 5 - S1281 5 161kV ckt 1 to minimum 364MVA RateB rating. |  | Internal | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 29SP 24SP | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 107.69 |  |  |  | Upgrade 98L TAP4 - ARROWHD4 230kV ckt 1 to minimum 557MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 20SP 29SP 24WP 24SP 19WP | Base Case | 70 | 80.5 | 100.8 |  |  |  | Upgrade RIV FLS7 115/69kV ckt 5 to minimum 71MVA/106MVA RateA/RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 13
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 344535 7ENON 345 345230 7MONTGMRY 345 1 | 29SP | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | 956 | 956 | 100.78 |  |  |  | Upgrade 7ENON - 7MONTGMRY 345kV ckt 1 to minimum 964MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 19WP | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 560 | 560 | 123.06 |  |  |  | Upgrade WEBSTER3 345/161kV ckt 1 to minimum 690MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 29SP 24SP | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | 259 | 285 | 120.95 |  |  |  | Upgrade BIGSTON4 - BROWNSV4 230kV ckt 1 to minimum 345MVA RateB rating. | 29SP 24SP | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 29SP | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | 169 | 169 | 111 |  |  |  | Upgrade HENRYCO5 - DENMARK5 161kV ckt 1 to minimum 188MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 29SP 24SP | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 263.7 | 263.7 | 108.73 |  |  |  | Upgrade GRE-BUNKER 4 - GRE-BLAINE 4 230kV ckt 1 to minimum 287MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 24WP | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | 241 | 241 | 101.35 |  |  |  | Upgrade 4STONGAT! - 4MID CO% 138kV ckt 1 to minimum 245MVA RateB rating. | 24WP | External | 0 | 1
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 580 | 580 | 127.41 |  |  |  | Upgrade 6WATFRD% - 6GYPSY% 230kV ckt 2 to minimum 739MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 29SP | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | 70 | 70 | 111.54 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 79MVA RateB rating. | 29SP | External | 2 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 600180 J587_GEN2 34.5 603305 J587 BLZSTR2 115 2 | 20SP | Base Case | 100 | 120 | 100.85 |  |  |  | Upgrade J587_GEN2 35/115kV ckt 2 to minimum 101MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | ALL | Base Case | 335 | 335 | 116.02 |  |  |  | Upgrade 5OVERTON - 5OVERTON 2 161kV ckt Z to minimum 389MVA/429MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 24L 19WP 20G | External | 0 | 20
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 29SP 24WP 24SP | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | 227 | 227 | 109.07 |  |  |  | Upgrade 5CLINTN - 5HOLDEN 161kV ckt 1 to minimum 248MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 29SP 24WP | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | 1000 | 1136 | 102.49 |  |  |  | Upgrade IATAN 7 - G17-030-TAP 345kV ckt 1 to minimum 1165MVA RateB rating. |  | Internal | 0 | 4
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 235 | 235 | 100.77 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 1 to minimum 237MVA RateB rating. | 20SP | External | 1 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 29SP | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | 123 | 123 | 100.04 |  |  |  | Upgrade BVR CHN J1 8 69/161kV ckt 1 to minimum 124MVA RateB rating. |  | External | 2 | 0
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 24WP 19WP | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | 441 | 441 | 107.25 |  |  |  | Upgrade 6BLPNT! - 6GYPSY% 230kV ckt 1 to minimum 473MVA RateB rating. | 24WP 19WP | External | 2 | 0
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 420 | 420 | 140.83 |  |  |  | Upgrade 8WHT BLUFF% 500/115kV ckt 1 to minimum 592MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603103 SCOTTCO7 115 997636 SCOTTCO3 115 9 | 24SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 111.95 |  |  |  | Upgrade SCOTTCO7 - SCOTTCO3 115kV ckt 9 to minimum 727MVA RateB rating. | 24SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 20SP 29SP 24WP 24SP 19WP | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | 1049 | 1049 | 147.27 |  |  |  | Upgrade 8WATERFO 500/230kV ckt 1 to minimum 1545MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 601028 EAU CL 3 345 997646 EAU CL 3 161 9 | 24L | P23:345:XEL:8E5 ECL BS | 300 | 334.6 | 105.12 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 352MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 29SP 24WP 24SP | P23:345:ITCM:HCKRYCK:FUT2 | 352 | 444 | 121.6 |  |  |  | Upgrade HCKRYCK5 161/345kV ckt 1 to minimum 540MVA RateB rating. | 29SP | External | 0 | 7
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 20SP 29SP 24WP 24SP | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 64 | 64 | 125.49 |  |  |  | Upgrade 2HOLDEN 69/161kV ckt 1 to minimum 81MVA RateB rating. | 20SP 29SP 24WP 24SP | External | 8 | 0
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 20G | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 184 | 199 | 122.38 |  |  |  | Upgrade MIDWAY_5 - AVENUECTY 5 161kV ckt 1 to minimum 244MVA RateB rating. | 20G | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 29SP 24SP | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1195 | 1209 | 116.2 |  |  |  | Upgrade OAKGROV3 - SUB 93 3 345kV ckt 1 to minimum 1405MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 19WP | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | 70 | 70 | 135.17 |  |  |  | Upgrade GRE-SPRGCK25 161/69kV ckt 2 to minimum 95MVA RateB rating. | 19WP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 603020 MAPLE R7 115 997616 MAPLE RIVER 69.0 1 | 19WP | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 129 | 140 | 118.72 |  |  |  | Upgrade MAPLE R7 115/69kV ckt 1 to minimum 167MVA RateB rating. | 19WP | External | 0 | 1
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 24L | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | 641 | 641 | 122.13 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 1 to minimum 783MVA RateB rating. | 24L | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 19WP 20G | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 92 | 92 | 105.15 |  |  |  | Upgrade COTTNTP7 - GRE-BERGNTP7 115kV ckt 1 to minimum 97MVA RateB rating. | 19WP 20G | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608616 HILLTOP4 230 997592 HIL1 115 1 | 29SP | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 187 | 233 | 110.15 |  |  |  | Upgrade HILLTOP4 230/115kV ckt 1 to minimum 257MVA RateB rating. | 29SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 24L 20G | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 334 | 334 | 148.55 |  |  |  | Upgrade EAST 5 - WOODBIN5 161kV ckt 1 to minimum 497MVA RateB rating. | 24L 20G | Internal | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 29SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 109.73 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 549MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 24WP 19WP | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | 641 | 641 | 105.64 |  |  |  | Upgrade 6FRISCO! - 6TEZCUCO% 230kV ckt 2 to minimum 678MVA RateB rating. | 24WP 19WP | External | 6 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 20SP 29SP 24WP 24SP 19WP | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | 67.2 | 71 | 122.47 |  |  |  | Upgrade BELLCTR5 161/69kV ckt 1 to minimum 87MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 11
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 20SP | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 225 | 225 | 104.77 |  |  |  | Upgrade CONDIE 4 230/138kV ckt 2 to minimum 236MVA RateB rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 588307 ASGI1706-XFM 34.5 588306 ASGI1706 161 1 | 20SP | Base Case | 104 | 130 | 118.65 |  |  |  | Upgrade ASGI1706-XFM 35/161kV ckt 1 to minimum 124MVA RateA rating. | 20SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 20SP 29SP 24WP 24SP 19WP | Base Case | 223 | 248 | 120.75 |  |  |  | Upgrade TRK RIV5 - STONEMAN 161kV ckt 1 to minimum 270MVA/327MVA RateA/RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 16
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601024 TERMINL3 345 997649 90198-B 115 10 | 29SP | P23:345:XEL:8P33 KOL | 672 | 734 | 111.11 |  |  |  | Upgrade TERMINL3 345/115kV ckt 10 to minimum 816MVA RateB rating. | 29SP | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 20SP 29SP 24SP | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 108.98 |  |  |  | Upgrade 2STURGN 69/161kV ckt 1 to minimum 28MVA RateB rating. | 20SP 29SP | External | 5 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 20SP | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 90 | 90 | 103.97 |  |  |  | Upgrade POTLTCH7 - CLOQUET7 115kV ckt 1 to minimum 94MVA RateB rating. | 20SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 24WP | P12:345:WERE:STRA-IATAN_345_1:: | 1195 | 1195 | 102.38 |  |  |  | Upgrade STRANGR7 - IATAN 7 345kV ckt 2 to minimum 1224MVA RateB rating. |  | Internal | 0 | 2
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 20SP 29SP 24WP 24SP 19WP | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 122.02 |  |  |  | Upgrade 2KOLBS_2! 69/230kV ckt 2 to minimum 195MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 29SP | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | 70 | 70 | 145.93 |  |  |  | Upgrade GRE-SPRGCK15 161/69kV ckt 1 to minimum 103MVA RateB rating. | 29SP | External | 0 | 5
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 29SP | P12:115:EES-EAI:EL_EHV:ELDEST | 159 | 159 | 104.69 |  |  |  | Upgrade 3ELD DONAN - 3ELD MONSNTO 115kV ckt 1 to minimum 167MVA RateB rating. | 29SP | External | 3 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 29SP 24SP | P24:345:ITCM:LAKEFLD 885 FUT:MN | 141 | 141 | 127.11 |  |  |  | Upgrade ROCK CO5 - MAGNLIA5 161kV ckt 1 to minimum 180MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 24SP | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | 187 | 187 | 101.46 |  |  |  | Upgrade HUC-MCLEOD 7 - 230/115 115kV ckt 1 to minimum 190MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 20SP 29SP 24WP 24SP 19WP | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 123.51 |  |  |  | Upgrade 2KOLBS_2! 69/230kV ckt 2 to minimum 197MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 0 | 5
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 20SP 29SP 24WP 24SP 19WP | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 122.88 |  |  |  | Upgrade 2KOLBS_1! 69/230kV ckt 1 to minimum 196MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 29SP 24SP | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | 56 | 56 | 103.99 |  |  |  | Upgrade 2HICKRY 69/161kV ckt 1 to minimum 59MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 29SP 24SP | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | 100 | 100 | 107.16 |  |  |  | Upgrade JEFF 8 69/161kV ckt 1 to minimum 108MVA RateB rating. | 29SP 24SP | External | 0 | 4
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 24WP 19WP | P24:345:AMMO::MCCREDIE:1 | 335 | 335 | 111.22 |  |  |  | Upgrade 5OVERTON - 5OVERTON 2 161kV ckt Z to minimum 373MVA RateB rating. | 19WP | External | 6 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 640066 AXTELL 7 115 997459 AXTELL T1 115 1 | 24WP | P42:345:NPPD:BKR-AXT-3308 | 336 | 336 | 102.87 |  |  |  | Upgrade AXTELL 7 - AXTELL T1 115kV ckt 1 to minimum 346MVA RateB rating. |  | Internal | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 20SP 29SP 24SP | P23:500:EES-EAI:WH_BLF:B7914 | 98 | 98 | 110.74 |  |  |  | Upgrade 3WOODWARD% - 3DIERKS! 115kV ckt 1 to minimum 109MVA RateB rating. | 20SP 29SP 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 29SP 24WP 24SP 19WP | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | 450 | 450 | 137.46 |  |  |  | Upgrade KILLDEER3 345/161kV ckt 1 to minimum 619MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 24SP | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | 500 | 500 | 108.24 |  |  |  | Upgrade GRE-PL VLLY5 - 345-161 161kV ckt 2 to minimum 542MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 29SP 24SP | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 159 | 159 | 117.59 |  |  |  | Upgrade FLDWDTP7 - BLCKBRY7 115kV ckt 1 to minimum 187MVA RateB rating. | 29SP 24SP | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 601055 SCOTTCO3 345 997636 SCOTTCO3 115 9 | 24SP | P23:345:XEL:8M57 SCO | 648.9 | 648.9 | 109.25 |  |  |  | Upgrade SCOTTCO3 345/115kV ckt 9 to minimum 709MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 20SP 29SP 24WP 24SP 19WP | Base Case | 70 | 80.5 | 100.8 |  |  |  | Upgrade RIV FLS7 115/69kV ckt 5 to minimum 71MVA/106MVA RateA/RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 13
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 29SP 24SP 19WP 20G | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | 297 | 297 | 116.64 |  |  |  | Upgrade S HAYS6 - GRTBEND6 230kV ckt 1 to minimum 347MVA RateB rating. | 29SP 24SP 20G | Internal | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 29SP | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | 299 | 299 | 107.21 |  |  |  | Upgrade ABBOTT 5 - M-TOWN 5 161kV ckt 1 to minimum 321MVA RateB rating. | 29SP | External | 0 | 3
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 20SP 29SP 24WP 24SP 19WP | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 72 | 72 | 176.07 |  |  |  | Upgrade WAPELLO5 161/69kV ckt 2 to minimum 127MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 20 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 20SP 29SP 24SP 20G | Base Case | 84 | 84 | 111.05 |  |  |  | Upgrade THOMSON7 - POTLTCH7 115kV ckt 1 to minimum 94MVA/97MVA RateA/RateB rating. | 20SP 29SP 24SP 20G | External | 0 | 12
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 20SP 29SP 24WP 24SP 19WP | P23:500:EES-EAI:WH_BLF:B7914 | 253 | 253 | 159.32 |  |  |  | Upgrade 3WHT BLUFF! - 3WRIGHTSVLE! 115kV ckt 1 to minimum 404MVA RateB rating. | 20SP 29SP 24WP 24SP 19WP | External | 5 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 24SP | P23:345:MEC:OAK GROVE 901 | 314 | 314 | 106.53 |  |  |  | Upgrade SB 56 5 - SB 85 5 161kV ckt 1 to minimum 335MVA RateB rating. |  | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 20SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 214.1 | 214.1 | 107.16 |  |  |  | Upgrade REDROCK7 - GLENMONT 115kV ckt 1 to minimum 230MVA RateB rating. | 20SP | External | 0 | 3
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 20SP 24SP | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 105.35 |  |  |  | Upgrade 2WSTPL3 69/161kV ckt 2 to minimum 59MVA RateB rating. | 20SP 24SP | External | 4 | 0
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 20G | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 56 | 56 | 101.88 |  |  |  | Upgrade 2HENRY 69/161kV ckt 1 to minimum 58MVA RateB rating. | 20G | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 29SP 24SP | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | 97.9 | 97.9 | 105.69 |  |  |  | Upgrade GRE-CMRTJCT7 - GRE-CORMRNT7 115kV ckt 1 to minimum 104MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 29SP 24SP | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | 230 | 230 | 105.87 |  |  |  | Upgrade HIWY12 7 - ORTONVL7 115kV ckt 1 to minimum 244MVA RateB rating. | 29SP 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 29SP | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | 300 | 334.6 | 121.26 |  |  |  | Upgrade ADAMS 5 - ADAMS 3 161kV ckt 9 to minimum 406MVA RateB rating. | 29SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 29SP 24WP 24SP | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 223 | 223 | 115.33 |  |  |  | Upgrade 5HUNTSDL - 5PERCHE 161kV ckt 1 to minimum 258MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 29SP 24SP | P24:345:ITCM:LAKEFLD 885 FUT:MN | 112 | 112 | 126.07 |  |  |  | Upgrade MAGNLIA5 - ELK L1 5 161kV ckt 1 to minimum 142MVA RateB rating. | 29SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 29SP 24WP 24SP 19WP | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | 84 | 84 | 124.39 |  |  |  | Upgrade LIBERTY5 161/69kV ckt 1 to minimum 105MVA RateB rating. | 29SP 24WP 24SP 19WP | External | 0 | 12
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 29SP 24WP 24SP | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | 100 | 112 | 129.57 |  |  |  | Upgrade 5JB HERGETT! 161/69kV ckt 1 to minimum 146MVA RateB rating. | 29SP 24WP 24SP | External | 9 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 29SP 24SP | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | 336 | 336 | 125.16 |  |  |  | Upgrade 5PALMYR_AI 161/345kV ckt 1 to minimum 421MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 20G | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | 297 | 297 | 114.49 |  |  |  | Upgrade S HAYS6 - GRTBEND6 230kV ckt 1 to minimum 341MVA RateB rating. | 20G | Internal | 0 | 2
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 20SP 24SP | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 105.35 |  |  |  | Upgrade 2WSTPL3 69/161kV ckt 2 to minimum 59MVA RateB rating. | 20SP 24SP | External | 4 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 29SP 24SP | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470 | 517 | 122.35 |  |  |  | Upgrade ARROWHD4 - FORBES 4 230kV ckt 1 to minimum 633MVA RateB rating. | 29SP 24SP | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 29SP 24SP | P11:24:DPC:AUTO-SINGLE:JPM:6 | 214.1 | 214.1 | 107.58 |  |  |  | Upgrade BAILEY RD7 - GLENMONT 115kV ckt 1 to minimum 231MVA RateB rating. | 29SP 24SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 29SP | Base Case | 1195 | 1195 | 104.97 |  |  |  | Upgrade HAZLTON3 - HCKRYCK3 345kV ckt 1 to minimum 1255MVA/1392MVA RateA/RateB rating. | 29SP | External | 0 | 6
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 24WP | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | 239 | 239 | 100.14 |  |  |  | Upgrade CHEMOLT7 - COTTAGE7 115kV ckt 1 to minimum 240MVA RateB rating. |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 29SP | Base Case | 36 | 36 | 142.71 |  |  |  | Upgrade BL.PLN.5 161/69kV ckt 1 to minimum 52MVA/55MVA RateA/RateB rating. | 29SP | External | 0 | 7
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 300107 5OSBORN 161 301310 5REX 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 127.88 |  |  |  | Upgrade 5OSBORN - 5REX 161kV ckt 1 to minimum 291MVA RateB rating. | 24L 20G | External | 0 | 6
S1 | GEN_025_028 | 00LVER | ERIS | Thermal | 601028 EAU CL 3 345 997643 EAU CL 3 161 9 | 19WP | P23:345:XEL:8E5 ECL BS | 330 | 334.6 | 114.94 |  |  |  | Upgrade EAU CL 3 345/161kV ckt 9 to minimum 385MVA RateB rating. | 19WP | External | 1 | 0
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 603110 TERMINL7 115 997650 90198-B 115 10 | 24SP | P23:345:XEL:8P33 KOL | 672 | 734 | 110.59 |  |  |  | Upgrade TERMINL7 - 90198-B 115kV ckt 10 to minimum 812MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_043_044_045 | 09NR | NRIS | Thermal | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 24L | 81377: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 112.77 |  |  |  | Upgrade NORTWST7 - MATHWSN7 345kV ckt 1 to minimum 1348MVA RateB rating. | 24L | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 29SP 24WP 24SP | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 223 | 223 | 115.33 |  |  |  | Upgrade 5HUNTSDL - 5PERCHE 161kV ckt 1 to minimum 258MVA RateB rating. | 29SP 24WP 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 29SP 24SP | P23:345:AMMO::ZACHARY:2 | 172 | 172 | 118.18 |  |  |  | Upgrade 5SRIVER - 5EMERSN 161kV ckt 1 to minimum 204MVA RateB rating. | 29SP | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 24WP 24SP | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | 448 | 448 | 117.17 |  |  |  | Upgrade GRE-CHUBLAK7 - CHL345-115-1 115kV ckt 1 to minimum 525MVA RateB rating. | 24WP 24SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 24SP | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 104.05 |  |  |  | Upgrade BEATTY 4 - ABERDEEN 4 230kV ckt 1 to minimum 274MVA RateB rating. | 24SP | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 29SP | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 106 | 106 | 106.99 |  |  |  | Upgrade 3RIVERTON - 3RILLA! 115kV ckt 1 to minimum 114MVA RateB rating. | 29SP | External | 0 | 4
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 24WP | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | 560 | 669 | 110.86 |  |  |  | Upgrade BLACKHAWK 3 345/161kV ckt 1 to minimum 742MVA RateB rating. | 24WP | External | 0 | 3
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 300107 5OSBORN 161 301310 5REX 161 1 | 24L 20G | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | 227 | 227 | 127.88 |  |  |  | Upgrade 5OSBORN - 5REX 161kV ckt 1 to minimum 291MVA RateB rating. | 24L 20G | External | 0 | 6
S1 | GEN_043_044_045 | 00LVER | ERIS | Thermal | 344282 5CAPE GIR2 161 351006 5JOPPA SR 161 1 | 24SP | P23:345:AMIL::JOPPA:V5 | 250 | 297 | 104.6 |  |  |  | Upgrade 5CAPE GIR2 - 5JOPPA SR 161kV ckt 1 to minimum 311MVA RateB rating. | 24SP | External | 1 | 0
S2 | GEN_043_044_045 | 00NR | NRIS | Thermal | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 24SP | Base Case | 78 | 114 | 102.34 |  |  |  | Upgrade THOMSON7 - FONDULAC 115kV ckt 1 to minimum 80MVA/118MVA RateA/RateB rating. |  | External | 0 | 2
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 24SP | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | 500 | 500 | 105.33 |  |  |  | Upgrade GRE-PL VLLY3 345/161kV ckt 2 to minimum 527MVA RateB rating. | 24SP | External | 0 | 2
S2 | GEN_025_028 | 09NR | NRIS | Thermal | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 24L | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 405 | 405 | 101.43 |  |  |  | Upgrade 6ROMEVL! - 6CONVNT! 230kV ckt 1 to minimum 411MVA RateB rating. | 24L | External | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Thermal | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 24SP | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | 95.6 | 95.6 | 100.7 |  |  |  | Upgrade WMU-PRIAM 7 115/69kV ckt 1 to minimum 97MVA RateB rating. | 24SP | External | 0 | 3
S2 | GEN_025_028 | 00NR | NRIS | Non-Converge | Non-Converge | 20SP 29SP 24WP 24SP 19WP 20G | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  |  | NConv |  |  |  |  | 20SP 29SP 24WP 24SP 19WP | NA | 0 | 1227
S2 | GEN_043_044_045 | 00NR | NRIS | Non-Converge | Non-Converge | 20SP 29SP 24WP 24SP 19WP 20G | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  |  | NConv |  |  |  |  | 20SP 29SP 24WP 24SP 19WP | NA | 0 | 1255
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G15088_1 345.0kV | 20SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8986 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S3459 3 345.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9309 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TOLEDO 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8981 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TIFFIN 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8645 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S994 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7102 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RIVFLSN7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8957 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-163 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9427 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5NEWARK 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9182 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LOAD 115.0kV | 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8517 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1345 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9382 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROCKCK7 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9187 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BVR CRK 3 345.0kV | 20SP | Base Case |  |  |  | 0.9363 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DIAMOND TRL3 345.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8489 | 0.95 | 1.05 |  |  | External | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MOORE 3 345.0kV | 20SP | Base Case |  |  |  | 0.9371 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COLBY 3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8565 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NESCTY 3 115.0kV | 20SP 24SP | Base Case |  |  |  | 0.921 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BVR CHN L1 5 161.0kV | 20SP | Base Case |  |  |  | 0.9309 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SELKIRK3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8265 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CRYSTAL5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8876 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SO.GVW.5 161.0kV | 20SP | Base Case |  |  |  | 0.9273 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FAIRFAX5 161.0kV | 20SP 29SP | Base Case |  |  |  | 0.9031 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EIC 5 161.0kV | 20SP | Base Case |  |  |  | 0.9072 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 29LEIGHTON7 115.0kV | 20SP | Base Case |  |  |  | 0.9452 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G17-052-TAP 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8238 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HOXIE 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8585 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB 91 3 345.0kV | 20SP | Base Case |  |  |  | 0.9253 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRAINVL5 161.0kV | 20SP | Base Case |  |  |  | 0.9311 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 85 5 161.0kV | 20SP | Base Case |  |  |  | 0.9104 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-115 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9191 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5MPLTAP 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8704 | 0.95 | 1.05 |  |  | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRASWCP7 115.0kV | 20SP | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 |  |  |  | 1.0505 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PLKCTY5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8584 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NW68HOLDRG3 345.0kV | 20SP | Base Case |  |  |  | 0.9416 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | QUINTON3 115.0kV | 20SP | Base Case |  |  |  | 0.9492 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1249 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.945 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WASHBRN5 161.0kV | 20SP | Base Case |  |  |  | 0.9312 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SYRACUS3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.7994 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KNLWRTH5 161.0kV | 20SP | Base Case |  |  |  | 0.9496 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EASTRLK5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8562 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5MEADVL 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8789 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COONRPDS G 69.0kV | 20SP | Base Case |  |  |  | 0.9435 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SHAULISRD5 161.0kV | 20SP | Base Case |  |  |  | 0.9369 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HILLS-DT-RX3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8686 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 4VAN N 3 115.0kV | 20SP | Base Case |  |  |  | 0.9483 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5THMHILB1 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8885 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MNTZUMA3 345.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8522 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRAER 5 161.0kV | 20SP | Base Case |  |  |  | 0.9249 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 40&GERTIE 7 115.0kV | 20SP | Base Case |  |  |  | 0.9478 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S3458 3 345.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.948 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALBANY 6 138.0kV | 20SP | Base Case |  |  |  | 0.9444 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WINDSR 5 161.0kV | 20SP | Base Case |  |  |  | 0.9234 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | E MADSN2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9266 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRK RIV5 161.0kV | 20SP | Base Case |  |  |  | 0.8825 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 56&Q 7 115.0kV | 20SP | Base Case |  |  |  | 0.9454 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | UNIONTP5 161.0kV | 20SP | Base Case |  |  |  | 0.9342 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G15052_1 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9454 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EAUCLAIRCAP7 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8803 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CRYSTLCVCAP7 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8878 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB A 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8975 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G15088_T 345.0kV | 20SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8986 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RHOADES3 115.0kV | 20SP | Base Case |  |  |  | 0.949 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MANNING3 115.0kV | 20SP 24WP | Base Case |  |  |  | 0.931 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 990TP 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8797 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5THMHLB4 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8887 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OAKGROV5 161.0kV | 20SP | Base Case |  |  |  | 0.9194 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WATHENA2 69.0kV | 20SP 29SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1399 5 161.0kV | 20SP 29SP 24SP 20G | Base Case |  |  |  | 0.9286 | 0.95 | 1.05 |  |  | Internal | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 12&CLAY3 115.0kV | 20SP | Base Case |  |  |  | 0.9485 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 4VAN S 3 115.0kV | 20SP | Base Case |  |  |  | 0.9483 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | UNVERFRT8 69.0kV | 20SP | Base Case |  |  |  | 0.9471 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GOODLND3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8572 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BIG BOW 3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8504 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DR NE 5 161.0kV | 20SP | Base Case |  |  |  | 0.9294 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HCKRYCK3 345.0kV | 20SP | Base Case |  |  |  | 0.893 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NATBEEF3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8836 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WNTRST 5 161.0kV | 20SP | Base Case |  |  |  | 0.9113 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ASHAWA5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.854 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRAR CK7 115.0kV | 20SP | Base Case |  |  |  | 0.9414 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RIVERDL4 230.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8397 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1222 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9424 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | POWESHK5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8722 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB 92 3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.886 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SCOTCTY3 115.0kV | 20SP 24WP | Base Case |  |  |  | 0.9364 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BARRON 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8826 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HILLSIE5 161.0kV | 20SP | Base Case |  |  |  | 0.8805 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STONEMAN 161.0kV | 20SP | Base Case |  |  |  | 0.8806 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 47 5 161.0kV | 20SP | Base Case |  |  |  | 0.9176 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MRSHLND5 161.0kV | 20SP | Base Case |  |  |  | 0.9448 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TEKAMAH5 161.0kV | 24SP | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 |  |  |  | 0.9321 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BEVERLY 3 345.0kV | 29SP | P23:345:MEC:LOUISA 964 |  |  |  | 0.8491 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | REASNOR5 161.0kV | 20SP | Base Case |  |  |  | 0.8812 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TCE8 69.0kV | 20SP | Base Case |  |  |  | 0.9397 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | POPLK_5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8838 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LUDELL 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8497 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1366 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7538 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1258 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8475 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LORE 5 161.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8997 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 70 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8967 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WTCLF 3 115.0kV | 20SP 29SP 24WP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8523 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1244 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7531 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WHT 56 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8845 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LUDELLT3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8497 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB 93 3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9041 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WESTBORO 3 345.0kV | 20SP | Base Case |  |  |  | 0.9443 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PAWNEE 3 115.0kV | 20SP | Base Case |  |  |  | 0.944 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DIGHTON3 115.0kV | 20SP 24WP 24SP | Base Case |  |  |  | 0.9294 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MAPLE J2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9276 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5LATHRP 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8741 | 0.95 | 1.05 |  |  | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SE POLK 3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8628 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JEFRSRD5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8818 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CRLRIDG5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8622 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALABAMA5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9064 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7OVERTON 345.0kV | 20SP 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8979 | 0.9 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HAZLTON L1 5 161.0kV | 20SP | Base Case |  |  |  | 0.9363 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MARMTNE5 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8475 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5OSCEOL 161.0kV | 20SP | Base Case |  |  |  | 0.9296 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1256 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9429 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HENRYCO5 161.0kV | 19WP | P23:345:MEC:WALCOTT 914 |  |  |  | 0.8865 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 18 5 161.0kV | 20SP | Base Case |  |  |  | 0.9183 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB E IC 5 161.0kV | 20SP 29SP 24WP 24SP | Base Case |  |  |  | 0.8582 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KIN MOR8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8758 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CHASE 3 115.0kV | 20SP 29SP 24WP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8299 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HILLS 3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8691 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SWAVRLY5 161.0kV | 20SP | Base Case |  |  |  | 0.9151 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S962 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8575 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MC REAC2 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9188 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KETCHEM7 345.0kV | 20SP 24WP 24L 20G | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  |  |  | 0.8622 | 0.9 | 1.05 |  |  | Internal | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HOYT 7 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9498 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1229 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9455 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DRAGER5 161.0kV | 20SP | Base Case |  |  |  | 0.9487 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 100DUG 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8532 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | P1 MPT PRI 345.0kV | 20SP | Base Case |  |  |  | 0.9485 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AMES 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8592 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | YORK 5 161.0kV | 20SP | Base Case |  |  |  | 0.9205 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEVADA 5 161.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.885 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB Y IC 5 161.0kV | 20SP 29SP 24WP 24SP | Base Case |  |  |  | 0.8584 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRANSFORMER 345.0kV | 20SP | Base Case |  |  |  | 0.9477 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PIONEER3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8825 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RIVER RUN5 161.0kV | 20SP 29SP | Base Case |  |  |  | 0.9037 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5CLINTN 161.0kV | 20SP | Base Case |  |  |  | 0.9383 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5OSBORN 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8619 | 0.95 | 1.05 |  |  | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WILLIAMSBRG5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8586 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RIV FLS7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8821 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FIRTH 7 115.0kV | 20SP | Base Case |  |  |  | 0.9377 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEWHAL5 161.0kV | 20SP 29SP | Base Case |  |  |  | 0.8839 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RILEY 5 161.0kV | 20SP | Base Case |  |  |  | 0.9469 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | J344_COLH 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8792 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BRKRIDG5 161.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ENRON 8 69.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | E-LIBER3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8839 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEANKNY5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8593 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 8TH ST.5 161.0kV | 20SP | Base Case |  |  |  | 0.9237 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB 77 5 161.0kV | 20SP | Base Case |  |  |  | 0.908 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SANTAFJ2 69.0kV | 20SP | Base Case |  |  |  | 0.9496 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 2&N 7 115.0kV | 20SP | Base Case |  |  |  | 0.9467 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1232 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9415 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | APANOSE5 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.9049 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1298 5 161.0kV | 24SP | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 |  |  |  | 0.9329 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FC1A 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9362 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STON PT7 115.0kV | 20SP | Base Case |  |  |  | 0.936 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRESTO 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.879 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PINE LK7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8839 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MANNGT 3 115.0kV | 20SP 24WP | Base Case |  |  |  | 0.9323 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1214 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9453 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LUFKIN 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8813 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EAU CL 3 345.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.81 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OLDSETTLERS7 115.0kV | 20SP | Base Case |  |  |  | 0.9256 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RIVFL T7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8965 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PERRY 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8765 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RANSOM 2 69.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8668 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ST JOE 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9079 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MORGN VLLY 3 345.0kV | 29SP 24WP | P23:345:MEC:LOUISA 964 |  |  |  | 0.8524 | 0.9 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OTTUMWA3 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.8798 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1297 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9452 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RISING SUN 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8804 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5ZACKARY 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9099 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SHEAS LK 7 115.0kV | 24SP | P23:345:XEL:8S81 SSL |  |  |  | 0.8696 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRQN_WIND5 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8327 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLUMILS5 161.0kV | 20SP | Base Case |  |  |  | 0.9474 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LARNED3 115.0kV | 20SP | Base Case |  |  |  | 0.943 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PLTSMTH8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8417 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAVANAH2 69.0kV | 20SP 24WP | Base Case |  |  |  | 0.9429 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MT VERN5 161.0kV | 20SP | Base Case |  |  |  | 0.9046 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLSPE 5 161.0kV | 20SP | Base Case |  |  |  | 0.938 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TXPHSF 3 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8196 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5MOCITY 161.0kV | 20SP | Base Case |  |  |  | 0.9317 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUGRCRK5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8607 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IND PRK5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9081 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ULYSPLT3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8667 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BRUNSWK5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9293 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SLMNFRK3 115.0kV | 20SP 24WP 24SP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8461 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MRSHLJT5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9152 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1291 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9471 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OTTUMWA5 161.0kV | 20SP | Base Case |  |  |  | 0.9161 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BEVERLY5 161.0kV | 20SP | Base Case |  |  |  | 0.9026 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DMOINES5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8568 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MECCORD3 345.0kV | 20SP | Base Case |  |  |  | 0.9495 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EARLHAM5 161.0kV | 20SP | Base Case |  |  |  | 0.912 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5NODWAY 161.0kV | 20SP | Base Case |  |  |  | 0.9481 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | A16-010_SUB 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.7904 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S6866 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7362 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TREMVAL5 161.0kV | 20SP | Base Case |  |  |  | 0.9055 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAC629 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7023 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-013 345.0kV | 20SP 29SP 24WP 24SP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8309 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAGENER 3 345.0kV | 20SP | Base Case |  |  |  | 0.9478 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HLSBORO5 161.0kV | 20SP | Base Case |  |  |  | 0.8687 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GR ISLD4 230.0kV | 20SP 24SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8439 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 60TH ST5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8568 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAC623 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.735 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5ADAIR1 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8828 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NORWLK5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8663 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IPSCO 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8998 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SWAVCAP5 161.0kV | 20SP | Base Case |  |  |  | 0.9151 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S973 8 69.0kV | 20SP 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8873 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BITRSWT5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8627 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S3454 3 345.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9443 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 2ND ELM2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9272 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 16 WABASH 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8531 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S968 8 69.0kV | 20SP | Base Case |  |  |  | 0.9347 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S965 8 69.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8944 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5BUTLER 161.0kV | 20SP 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8783 | 0.9 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 31 5 161.0kV | 20SP | Base Case |  |  |  | 0.9229 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TCE TAP8 69.0kV | 20SP | Base Case |  |  |  | 0.9428 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MIAMI_ 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9142 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1216 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9375 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1253 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9406 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 17&HOLDRGE7 115.0kV | 20SP | Base Case |  |  |  | 0.9444 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAVLY JC8 69.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OBER T 3 115.0kV | 20SP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8709 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NCU903 8 69.0kV | 20SP 24SP | Base Case |  |  |  | 0.902 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SWITZER5 161.0kV | 20SP | Base Case |  |  |  | 0.9488 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HIAWATA5 161.0kV | 20SP | Base Case |  |  |  | 0.9171 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MALTABN5 161.0kV | 20SP | Base Case |  |  |  | 0.9149 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CALAMUS7 115.0kV | 20SP | Base Case |  |  |  | 0.9288 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G15052_T 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9454 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ASH GRV8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8935 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | METRO E5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8571 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7HPW-N 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.9024 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SE POLK 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8577 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KERPER 5 161.0kV | 20SP | Base Case |  |  |  | 0.9213 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-032 345.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.787 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 49 5 161.0kV | 20SP | Base Case |  |  |  | 0.9277 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROCK CK5 161.0kV | 20SP | Base Case |  |  |  | 0.925 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAXTAP 3 115.0kV | 20SP | Base Case |  |  |  | 0.948 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CLINTON5 161.0kV | 20SP | Base Case |  |  |  | 0.9382 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DRCOMP 5 161.0kV | 20SP | Base Case |  |  |  | 0.9304 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRIMES 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.857 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALBANY 5 161.0kV | 20SP | Base Case |  |  |  | 0.9307 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRINNEL3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8476 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5HIGBEE 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8791 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1236 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9389 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STERLNG7 115.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8972 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ANITA 5 161.0kV | 20SP | Base Case |  |  |  | 0.9481 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TIFFIN 3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8684 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BELLCTR5 161.0kV | 20SP | Base Case |  |  |  | 0.8812 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AVENUECTY 5 161.0kV | 20SP 29SP 24WP 24SP 19WP | Base Case |  |  |  | 0.8794 | 0.95 | 1.05 |  |  | Internal | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MGLN TP8 69.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8928 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1226 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9391 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EAST BALDWN5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8824 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CNTRVIL5 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.863 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAPELLO5 161.0kV | 20SP | Base Case |  |  |  | 0.9121 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WILOWRV7 115.0kV | 20SP | 71599.0 |  |  |  | 0.8978 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MADISON3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8774 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRAVL ISLE 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8789 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STON PT5 161.0kV | 20SP | Base Case |  |  |  | 0.8983 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 91&A 7 115.0kV | 20SP | Base Case |  |  |  | 0.949 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SYCAMOR3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8592 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BONDRNT3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8524 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | J416_WF3 345.0kV | 20SP 29SP | Base Case |  |  |  | 0.8923 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5HARRSBRG 161.0kV | 20SP 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8879 | 0.9 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOPER 5 161.0kV | 20SP | Base Case |  |  |  | 0.9333 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S971 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8829 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S3455 3 345.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9438 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRESTOT5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8792 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | E CALMS7 115.0kV | 20SP | Base Case |  |  |  | 0.9395 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-008 345.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8796 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NW5&BENTON7 115.0kV | 20SP | Base Case |  |  |  | 0.9461 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S964 8 69.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8942 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NW68HOLDRG7 115.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CNTRGRV5 161.0kV | 20SP | Base Case |  |  |  | 0.9197 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BL.PLN.5 161.0kV | 20SP 29SP | Base Case |  |  |  | 0.8916 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HCKRYCK5 161.0kV | 20SP | Base Case |  |  |  | 0.9303 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOPER_602 8 69.0kV | 20SP 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8876 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JULIAN 5 161.0kV | 20SP | Base Case |  |  |  | 0.9198 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1341 5 161.0kV | 24SP | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 |  |  |  | 0.932 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DUNCAN 5 161.0kV | 20SP | Base Case |  |  |  | 0.9385 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SANTAFE2 69.0kV | 20SP | Base Case |  |  |  | 0.9496 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | W BROCK8 69.0kV | 20SP 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8919 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NORWLK3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8678 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | P2 MPT PRI 345.0kV | 20SP | Base Case |  |  |  | 0.9488 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S904 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8473 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALTONA 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8577 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALXNDR 3 115.0kV | 20SP | Base Case |  |  |  | 0.9319 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HARBNGR7 345.0kV | 29SP | P12:345:WERE:87TH-STRA_345:: |  |  |  | 0.8981 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SALEM L1 5 161.0kV | 20SP | Base Case |  |  |  | 0.9367 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FORVER 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8601 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BNE HARISON5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8738 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5CHILLI 161.0kV | 20SP 24WP 24SP | Base Case |  |  |  | 0.8647 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NE 54 AVE 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8566 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RALSTON8 69.0kV | 20SP | Base Case |  |  |  | 0.9443 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CARPENTER 7 345.0kV | 29SP | P12:345:WERE:87TH-STRA_345:: |  |  |  | 0.8981 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TC-WHITING 3 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.7904 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5HINTON 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8965 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAWNRID3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8597 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TC-MCMURRY 3 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8716 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SIB REA1 345.0kV | 20SP 24WP | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  |  |  | 0.8771 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-088 345.0kV | 20SP 24WP 24L 20G | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  |  |  | 0.8622 | 0.9 | 1.05 |  |  | Internal | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KELLY 5 161.0kV | 20SP | Base Case |  |  |  | 0.9401 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S967 8 69.0kV | 20SP | Base Case |  |  |  | 0.9294 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PALMER3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8071 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLSPS 5 161.0kV | 20SP | Base Case |  |  |  | 0.9407 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MAGELLN8 69.0kV | 20SP 20G | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8995 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S995 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.6904 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RALSTONT8 69.0kV | 20SP | Base Case |  |  |  | 0.9444 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STROTHR5 161.0kV | 20SP | Base Case |  |  |  | 0.9475 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1221 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9455 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5SRIVER 161.0kV | 20SP | Base Case |  |  |  | 0.9468 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CIRCLVL3 115.0kV | 20SP | Base Case |  |  |  | 0.9477 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SQUARED7 115.0kV | 20SP | Base Case |  |  |  | 0.9394 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RCK ELM5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8892 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1233 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9458 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUTLIFF7 115.0kV | 20SP | Base Case |  |  |  | 0.9322 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5THMHLB3 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8886 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EASTOWN7 345.0kV | 20SP 24WP | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 |  |  |  | 0.8732 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 20PIONEERS7 115.0kV | 20SP | Base Case |  |  |  | 0.9495 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SETAB 7 345.0kV | 20SP 29SP 24WP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8736 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SENECA 5 161.0kV | 20SP | Base Case |  |  |  | 0.8859 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HIAWATA7 115.0kV | 20SP | Base Case |  |  |  | 0.9333 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S993 8 69.0kV | 20SP 20G | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 |  |  |  | 0.8922 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRICNTY L2 5 161.0kV | 20SP | Base Case |  |  |  | 0.9071 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TAP2 115.0kV | 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.854 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 84LEIGHTON7 115.0kV | 20SP | Base Case |  |  |  | 0.9494 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAFBW5 161.0kV | 20SP | Base Case |  |  |  | 0.9069 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SIBLEYPL 161.0kV | 20SP | Base Case |  |  |  | 0.9417 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PK_GOAB3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8546 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5MOBTAP 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8767 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S985 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8475 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RICHMND5 161.0kV | 20SP | Base Case |  |  |  | 0.9213 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BNE JCT5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8717 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BERTRAM7 115.0kV | 20SP | Base Case |  |  |  | 0.9291 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 56&ELK TAP7 115.0kV | 20SP | Base Case |  |  |  | 0.9478 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HAYNE3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8902 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAKE RD5 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.9049 | 0.95 | 1.05 |  |  | Internal | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SW27&F 7 115.0kV | 20SP | Base Case |  |  |  | 0.9467 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARBR HL 3 345.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8906 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7FAIRPT 345.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.894 | 0.95 | 1.05 |  |  | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRIBUNE3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.798 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 112 5 161.0kV | 20SP | Base Case |  |  |  | 0.9327 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PENTAGN3 115.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S3451 3 345.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9368 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TECUMSH8 69.0kV | 20SP | Base Case |  |  |  | 0.9301 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5CARBID T 161.0kV | 19WP | Base Case |  |  |  | 0.9431 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ORIENT 3 345.0kV | 20SP | Base Case |  |  |  | 0.935 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 34 NW 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.858 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BEARCRK3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8129 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COGGON 5 161.0kV | 20SP | P23:345:MEC:ATCHISON CO 903 |  |  |  | 0.8992 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB T HSK 3 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.8886 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAVANNA5 161.0kV | 20SP | Base Case |  |  |  | 0.9193 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EAU CLA5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8797 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | W-LIBER3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8859 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 21&N 7 115.0kV | 20SP | Base Case |  |  |  | 0.944 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LIBERTY5 161.0kV | 20SP | Base Case |  |  |  | 0.924 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 142ST 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8557 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JOHNCR 3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.837 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SCRANTN5 161.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8975 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | UNIONCF5 161.0kV | 20SP | Base Case |  |  |  | 0.9374 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MUSCOTA2 69.0kV | 20SP | Base Case |  |  |  | 0.9483 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DEER RUN5 161.0kV | 20SP | Base Case |  |  |  | 0.9024 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GLOWAT 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8537 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 56&EVERETT7 115.0kV | 20SP | Base Case |  |  |  | 0.9449 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 31T 5 161.0kV | 20SP | Base Case |  |  |  | 0.9237 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HUXLEY 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8645 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WGRAND5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8605 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BRLGTN 5 161.0kV | 19WP | P23:345:MEC:WALCOTT 914 |  |  |  | 0.8606 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S966 8 69.0kV | 20SP | Base Case |  |  |  | 0.948 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5HICKCK 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.85 | 0.95 | 1.05 |  |  | External | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WILLOW CRK 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8549 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SEVN ML5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.864 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | THREE LAKES7 115.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8982 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | W.BRCH 7 115.0kV | 20SP | Base Case |  |  |  | 0.9325 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BUFF_DUNES 7 345.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.8287 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S HILLS 3 345.0kV | 20SP | Base Case |  |  |  | 0.9347 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LINWELD5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8569 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BONDRNT5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8587 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5LATHROP 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8702 | 0.95 | 1.05 |  |  | External | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MINGO 3 115.0kV | 20SP 24WP 24SP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8458 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IC ENRON 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8623 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 109CLK 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8527 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB J IC 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8627 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ATWOOD 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8439 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROSEHIL7 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9416 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HILLS 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.862 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SEDEAST5 161.0kV | 20SP | Base Case |  |  |  | 0.9031 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EDWARVL3 115.0kV | 20SP 19WP | Base Case |  |  |  | 0.9184 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLACKHAWK 3 345.0kV | 20SP 29SP | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW |  |  |  | 0.8962 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1237 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9387 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JOHNSON3 115.0kV | 20SP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8682 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SIBLEY 5 161.0kV | 20SP | Base Case |  |  |  | 0.9421 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MIDWY2 2 69.0kV | 20SP 24WP | Base Case |  |  |  | 0.9066 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7ZACKARY 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.9048 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEWHILLSITC3 345.0kV | 24WP | P23:345:MEC:HILLS 9114 |  |  |  | 0.8468 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CAROLTN5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9263 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RANSOM 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8703 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAUREL_5 161.0kV | 20SP | Base Case |  |  |  | 0.9359 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WEVER5 161.0kV | 19WP | P23:345:MEC:WALCOTT 914 |  |  |  | 0.8633 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NCTYSVC2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9113 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SEGNTP 3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.859 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7HPW-S 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.9053 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STFRAN 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8533 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5TURKEYCRK 161.0kV | 24WP | Base Case |  |  |  | 0.9404 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1231 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9454 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PINELKT5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8807 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PLSNT CRNR 5 161.0kV | 20SP | Base Case |  |  |  | 0.912 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 2MADISN2 69.0kV | 20SP | Base Case |  |  |  | 0.9493 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOPER 8 69.0kV | 20SP | Base Case |  |  |  | 0.9333 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GOFF 3 115.0kV | 20SP | Base Case |  |  |  | 0.9494 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BOONVIL3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8762 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SALEM 3 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.8809 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 70&CALVERT7 115.0kV | 20SP | Base Case |  |  |  | 0.9497 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAMAR7 345.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.7733 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5WINSLOW 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8917 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLACKHAWK 5 161.0kV | 20SP | Base Case |  |  |  | 0.9282 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EDMOND5 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.9043 | 0.95 | 1.05 |  |  | Internal | 0 | 5
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MARION K2 7 115.0kV | 20SP | Base Case |  |  |  | 0.9247 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ELK MND5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8907 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HASTING4 230.0kV | 20SP 24SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8541 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 76 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8983 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SHARNSP3 115.0kV | 20SP 29SP 24WP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.83 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CANADAY4 230.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8538 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 30&A 7 115.0kV | 20SP | Base Case |  |  |  | 0.9439 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PCI 5 161.0kV | 20SP 29SP | Base Case |  |  |  | 0.9013 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MCCOOL 3 345.0kV | 20SP 24SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8313 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 3 VANBU2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9265 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S6874 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.6892 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEOSHO 7 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9493 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CMRIVTP3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8964 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S6815T3 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7309 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 56 3 345.0kV | 29SP | P23:345:MEC:LOUISA 924 |  |  |  | 0.899 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 8&N 7 115.0kV | 20SP | Base Case |  |  |  | 0.9458 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GU CTR 5 161.0kV | 20SP | Base Case |  |  |  | 0.9317 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 52 5 161.0kV | 20SP | Base Case |  |  |  | 0.9096 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DENMARK5 161.0kV | 19WP | P23:345:MEC:WALCOTT 914 |  |  |  | 0.8784 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JACKSON5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8998 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PRALEE 5 161.0kV | 20SP | Base Case |  |  |  | 0.9448 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAC SO 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.735 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOPER_ESST8 69.0kV | 20SP | Base Case |  |  |  | 0.9333 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STH HILL WD 345.0kV | 20SP | Base Case |  |  |  | 0.9349 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MQOKETA5 161.0kV | 20SP | Base Case |  |  |  | 0.9056 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G17-030-TAP 345.0kV | 20SP | Base Case |  |  |  | 0.938 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BEACON 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8838 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ECKLES-161 161.0kV | 20SP | Base Case |  |  |  | 0.9433 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WHT 14 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8923 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GOVE 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8534 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ORRICK 5 161.0kV | 20SP | Base Case |  |  |  | 0.935 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALICERD5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8535 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COLBY 2 69.0kV | 20SP 29SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8421 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COFFEY7 115.0kV | 20SP | Base Case |  |  |  | 0.9315 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HALLIE 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8783 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARCHIE 5 161.0kV | 20SP | Base Case |  |  |  | 0.9377 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | VINTON 5 161.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8986 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1234 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9429 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1210 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9398 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OAKGRV 5 161.0kV | 20SP | Base Case |  |  |  | 0.9283 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5THMHLB2 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8885 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5NOVELY_SW 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8803 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SALEM L2 5 161.0kV | 20SP | Base Case |  |  |  | 0.9367 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WTCLFTP3 115.0kV | 20SP 29SP 24WP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8526 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | J476 SHENHLL 345.0kV | 20SP | Base Case |  |  |  | 0.9444 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ST JOE 3 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.9112 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 88TH 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8528 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRPR2 3 345.0kV | 19WP | P45:345:UMZW:# 1328 #: GI IN NE. |  |  |  | 0.9058 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S977 8 69.0kV | 20SP 24SP | Base Case |  |  |  | 0.9093 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | N TYLER3 115.0kV | 20SP | Base Case |  |  |  | 0.9493 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5REX 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8639 | 0.95 | 1.05 |  |  | External | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GR JCT 5 161.0kV | 20SP | Base Case |  |  |  | 0.9111 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROCKCKW5 161.0kV | 20SP | Base Case |  |  |  | 0.9248 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ONEOK 3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8453 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DIGHTNT3 115.0kV | 20SP 24WP 24SP | Base Case |  |  |  | 0.9299 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LACROS 3 115.0kV | 20SP | Base Case |  |  |  | 0.9475 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_025_028 | 00NR | NRIS | Voltage | MONOLITH 3 345.0kV | 24WP | 104888: 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640278 SHELDON7 115 997366 MOORE T1 115 1 640277 MOORE 3 345 997366 MOORE T1 115 1 640280 MOORE 9 13.8 997366 MOORE T1 115 1 |  |  |  | 0.8979 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SEDALIA5 161.0kV | 20SP | Base Case |  |  |  | 0.9073 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OBERLIN3 115.0kV | 20SP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8711 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARNOLD 5 161.0kV | 20SP | Base Case |  |  |  | 0.9252 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SPRINT25 161.0kV | 20SP | Base Case |  |  |  | 0.9468 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LKWOOD 5 161.0kV | 20SP | Base Case |  |  |  | 0.9431 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WALKMYR3 115.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.8612 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARMYPOS5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8547 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1278 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9432 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S961 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8431 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOK 5 161.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.9052 | 0.95 | 1.05 |  |  | Internal | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PARNEL 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8538 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | E-PINE 3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8839 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BREWSTR3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8542 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB P IC 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8616 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 58 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8982 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MARMTNW5 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8476 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 141 44 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8558 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRIB SW3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8009 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SWAMPFX7 115.0kV | 20SP | Base Case |  |  |  | 0.9259 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MC REAC1 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9188 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BROWNCO3 115.0kV | 20SP | Base Case |  |  |  | 0.9395 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SLMNFRK7 345.0kV | 20SP 29SP 24WP 24SP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8318 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DOUD 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8717 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CLARKCOUNTY7 345.0kV | 20SP | Base Case |  |  |  | 0.9477 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 4&MORTON 7 115.0kV | 20SP | Base Case |  |  |  | 0.9464 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BENTON 7 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9415 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SPRINT15 161.0kV | 20SP | Base Case |  |  |  | 0.9491 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ANKENY 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.856 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ALMA 5 161.0kV | 20SP | Base Case |  |  |  | 0.9323 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HERNDON3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8572 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 100 54 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8552 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1201 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9485 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G17-032-TAP 345.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.787 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JOHNSON2 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.84 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DYSART 5 161.0kV | 20SP | Base Case |  |  |  | 0.9169 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAC NO 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.7023 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WALCOTT3 345.0kV | 20SP 29SP | Base Case |  |  |  | 0.8997 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 39 3 345.0kV | 20SP | Base Case |  |  |  | 0.9335 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1280 5 161.0kV | 20SP 24SP 20G | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9161 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AMES 5 161.0kV | 20SP | Base Case |  |  |  | 0.9031 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NC SYRA8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8996 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5NORTON 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9157 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JOHNSTON 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8563 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IPSCO 3 345.0kV | 20SP 29SP | Base Case |  |  |  | 0.8979 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LUCAS 5 161.0kV | 20SP | Base Case |  |  |  | 0.9105 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CSTFRAN3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8541 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MULLNCR7 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9188 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1254 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9482 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRENFLD5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8587 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 3&VANDORN 7 115.0kV | 20SP | Base Case |  |  |  | 0.9474 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-162 345.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.9426 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 28 5 161.0kV | 20SP | Base Case |  |  |  | 0.924 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARNOLD 3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.878 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S900 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8957 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TROUT B7 115.0kV | 20SP | 71599.0 |  |  |  | 0.8978 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GODLNDT3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8575 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5LOCUST 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8378 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BEELER 3 115.0kV | 20SP 24WP 24SP | Base Case |  |  |  | 0.9223 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LEOTI 3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8403 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S963 8 69.0kV | 20SP 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8896 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ATWODSW3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8479 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 58TAP 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8992 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAFBW_SW5 161.0kV | 20SP | Base Case |  |  |  | 0.9071 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEWPORT5 161.0kV | 19WP | Base Case |  |  |  | 0.9393 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRPR1 3 345.0kV | 19WP | P45:345:UMZW:# 1328 #: GI IN NE. |  |  |  | 0.9052 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NW12&ARBOR7 115.0kV | 20SP | Base Case |  |  |  | 0.9475 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ATCHSN 3 345.0kV | 20SP | Base Case |  |  |  | 0.9434 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DUNDEE 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8998 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HARBNGR3 115.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.8618 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MUND 3 115.0kV | 20SP | Base Case |  |  |  | 0.9334 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AXTELL 3 345.0kV | 20SP 24WP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8364 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JASPER 5 161.0kV | 20SP | Base Case |  |  |  | 0.9058 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S EAST 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9147 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PR BRZ 4 230.0kV | 24SP | Base Case |  |  |  | 1.0599 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PINE LK5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8808 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1263 5 161.0kV | 20SP 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8926 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WYOMING5 161.0kV | 20SP | Base Case |  |  |  | 0.9028 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 17 5 161.0kV | 20SP | Base Case |  |  |  | 0.9299 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LUNDQST5 161.0kV | 20SP | Base Case |  |  |  | 0.9303 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CRYSTAL7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8958 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | REDCDR 5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8671 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB 91 5 161.0kV | 20SP | Base Case |  |  |  | 0.9147 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PH RUN 3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8476 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DR ENG 5 161.0kV | 20SP | Base Case |  |  |  | 0.9384 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GALENA 5 161.0kV | 20SP | Base Case |  |  |  | 0.9083 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 53 5 161.0kV | 20SP | Base Case |  |  |  | 0.9099 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WEST---5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9145 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S990 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8778 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DWNTWN IND5 161.0kV | 20SP | Base Case |  |  |  | 0.9034 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROCK CK3 345.0kV | 20SP | Base Case |  |  |  | 0.9416 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | REDWILO3 345.0kV | 20SP 29SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8621 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DELWARE5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8575 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BREMER CO5 161.0kV | 20SP | Base Case |  |  |  | 0.94 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEWTON 5 161.0kV | 20SP | Base Case |  |  |  | 0.8992 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BRDGPRT5 161.0kV | 20SP | Base Case |  |  |  | 0.9078 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ODESSA 5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9188 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HUMBOLT5 161.0kV | 20SP 29SP 24SP 20G | Base Case |  |  |  | 0.9203 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ELLIS 2 69.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8587 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NASHUA 7 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.9397 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KIN MTP8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8764 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COOPER 3 345.0kV | 20SP | Base Case |  |  |  | 0.9359 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RULETON3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8656 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MISNJCT5 161.0kV | 20SP | Base Case |  |  |  | 0.9494 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-100 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8599 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BUTLER 5 161.0kV | 20SP | Base Case |  |  |  | 0.9385 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLRSTWN7 115.0kV | 20SP | Base Case |  |  |  | 0.9447 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 4VAN 3 115.0kV | 20SP | Base Case |  |  |  | 0.9483 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-074 345.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8581 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HYDCAP 8 69.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MC REAC3 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9188 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MIDWAY_5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9066 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BOONVIL5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8725 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BVR CHN L2 5 161.0kV | 20SP | Base Case |  |  |  | 0.9307 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ARNOLD3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.866 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5SEDALA 161.0kV | 20SP | Base Case |  |  |  | 0.9085 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TECHILL5 161.0kV | 20SP | Base Case |  |  |  | 0.9324 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HOLT_REACT7 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9219 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PERRY WILLI5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8765 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5STURGN 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9358 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SHELLRCK8 69.0kV | 20SP | Base Case |  |  |  | 0.943 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAFBE5 161.0kV | 20SP | Base Case |  |  |  | 0.9062 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BIRDCTY3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8502 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MCKSBRG 5 161.0kV | 20SP | Base Case |  |  |  | 0.9407 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | VIELE 5 161.0kV | 19WP | P23:345:MEC:WALCOTT 914 |  |  |  | 0.8937 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ADAIR 5 161.0kV | 20SP | Base Case |  |  |  | 0.9447 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 7HUGHES 345.0kV | 20SP 24WP | Base Case |  |  |  | 0.899 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GR MND 5 161.0kV | 20SP | Base Case |  |  |  | 0.8998 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SYCAMOR5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8581 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5MOBERLY 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8767 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SALSBRY5 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8794 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RAYTOWN5 161.0kV | 20SP | Base Case |  |  |  | 0.9465 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S975 8 69.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.8947 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB U IC 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8614 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SALE5 161.0kV | 20SP | Base Case |  |  |  | 0.9259 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 43 5 161.0kV | 20SP | Base Case |  |  |  | 0.9198 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1217 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9382 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HYDROLN5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8677 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 74 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8997 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRIMES 3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8645 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 19&ALVO 7 115.0kV | 20SP | Base Case |  |  |  | 0.9479 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HSNVL 5 161.0kV | 20SP | Base Case |  |  |  | 0.9403 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EL FARM5 161.0kV | 20SP | Base Case |  |  |  | 0.9427 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 93&O 7 115.0kV | 20SP | Base Case |  |  |  | 0.9489 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ENEMAHA3 115.0kV | 20SP | Base Case |  |  |  | 0.9439 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PUCKET 3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8545 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5ADAIR3 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8828 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | APL RVR5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8697 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 6815TP98 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.699 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5OSCEOKC 161.0kV | 20SP | Base Case |  |  |  | 0.9296 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1305 5 161.0kV | 24SP | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 |  |  |  | 0.9325 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2016-050 345.0kV | 20SP 29SP 24WP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.826 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SAINTS RUN7 115.0kV | 20SP | Base Case |  |  |  | 0.9303 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MONROCO5 161.0kV | 20SP | Base Case |  |  |  | 0.9307 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SIBLEY 7 345.0kV | 20SP 24WP | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  |  |  | 0.8771 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WINDSOR5 161.0kV | 20SP | Base Case |  |  |  | 0.9292 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 39 5 161.0kV | 20SP | Base Case |  |  |  | 0.9232 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COFFEY5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8995 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ENT WAY 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8987 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DIAM TR WIND 345.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8491 | 0.95 | 1.05 |  |  | External | 0 | 8
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUB17-49CAP5 161.0kV | 20SP | Base Case |  |  |  | 0.9299 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G15_021_1 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.837 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 88 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8961 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5GEORGE 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9067 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NW70FAIRFD7 115.0kV | 20SP | Base Case |  |  |  | 0.948 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MCDONLD3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8463 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | RLHILLS3 345.0kV | 20SP | Base Case |  |  |  | 0.9457 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5FAIRPT 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8809 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | PAULINE3 345.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8796 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SUMNERMU8 69.0kV | 20SP | Base Case |  |  |  | 0.9496 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-052 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8238 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NORTHGATE 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8606 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 57&GARLAND7 115.0kV | 20SP | Base Case |  |  |  | 0.9471 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HAZLTON3 345.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8802 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MINGO 7 345.0kV | 20SP 29SP 24WP 24SP | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 |  |  |  | 0.8309 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KANARAD3 115.0kV | 20SP 29SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8621 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 2MADISN3 115.0kV | 20SP | Base Case |  |  |  | 0.9483 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | W LINCOLN 7 115.0kV | 20SP | Base Case |  |  |  | 0.9461 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | COULEE 5 161.0kV | 20SP | Base Case |  |  |  | 0.9484 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TEXAS_CNTY 3 115.0kV | 29SP 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8599 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LEX161 5 161.0kV | 20SP | Base Case |  |  |  | 0.9182 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STFRANT3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8542 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1235 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9416 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 59CRNHUSKR7 115.0kV | 20SP | Base Case |  |  |  | 0.947 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | STANGE 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8606 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HAZLTON L2 5 161.0kV | 20SP | Base Case |  |  |  | 0.9361 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | KARMA 5 161.0kV | 20SP | Base Case |  |  |  | 0.9111 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1227 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9412 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BERTRAM5 161.0kV | 20SP | Base Case |  |  |  | 0.9039 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 33SUPERIOR7 115.0kV | 20SP | Base Case |  |  |  | 0.9478 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OSBORN7 345.0kV | 20SP 24WP 24L 20G | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  |  |  | 0.8622 | 0.9 | 1.05 |  |  | Internal | 0 | 6
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NLIB 3 115.0kV | 24SP | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 |  |  |  | 0.8852 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5EMERSN 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9309 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FLETCHR3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.8131 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SEGUIN 3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8559 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | OAKGROV3 345.0kV | 20SP | Base Case |  |  |  | 0.9193 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NSI 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8626 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEHAWKA8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.851 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | E CALMS5 161.0kV | 20SP | Base Case |  |  |  | 0.9003 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S938 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.6856 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NORTON-5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.9157 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WOODBIN5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9068 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 78 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8989 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 103&ROKEBY3 345.0kV | 20SP | Base Case |  |  |  | 0.9468 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ST CROIG 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8901 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LEESUM 5 161.0kV | 20SP | Base Case |  |  |  | 0.9473 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAW CRK5 161.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8928 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRANGRAE 161.0kV | 20SP | Base Case |  |  |  | 0.869 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WAFBE_SW5 161.0kV | 20SP | Base Case |  |  |  | 0.907 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AUBRNT 8 69.0kV | 20SP 24SP | Base Case |  |  |  | 0.914 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | LAW CRK7 115.0kV | 20SP | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 |  |  |  | 0.8982 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BLSPW 5 161.0kV | 20SP | Base Case |  |  |  | 0.9397 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MPWSPLIT 161.0kV | 24SP 19WP | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 |  |  |  | 0.8952 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G17-030-SWYD 345.0kV | 20SP 29SP 24WP 19WP 20G | Base Case |  |  |  | 0.8821 | 0.95 | 1.05 |  |  | Internal | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CITYSVC2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9112 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | JEFF 5 161.0kV | 20SP | P42:345:OKGE:SB_OPKY7388 |  |  |  | 0.899 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | QC ENRON 5 161.0kV | 20SP | Base Case |  |  |  | 0.912 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | POSTROCK7 345.0kV | 20SP 24WP 24SP | Base Case |  |  |  | 0.941 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 56 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8995 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | AUBURN 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8871 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-090 161.0kV | 20SP | Base Case |  |  |  | 0.9189 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NORCATR3 115.0kV | 20SP 24SP | Base Case |  |  |  | 0.9355 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IRVINE_5 161.0kV | 20SP 24WP | Base Case |  |  |  | 0.8789 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MLKING 5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8535 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TRICNTY L1 5 161.0kV | 20SP | Base Case |  |  |  | 0.9071 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CFUINDP5 161.0kV | 20SP | Base Case |  |  |  | 0.9383 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | G16-050-TAP 345.0kV | 20SP 29SP 24WP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.826 | 0.9 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRNGRTP5 161.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8557 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1398 5 161.0kV | 20SP 29SP 24SP 19WP 20G | Base Case |  |  |  | 0.925 | 0.95 | 1.05 |  |  | Internal | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DRYCREK7 115.0kV | 20SP | Base Case |  |  |  | 0.9287 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MARION K1 7 115.0kV | 20SP | Base Case |  |  |  | 0.9247 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | FINNEY 7 345.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.824 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S972 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8817 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HUGOTON3 115.0kV | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0.8546 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DAKOTA_5 161.0kV | 24WP | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8367 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NATWOOD3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8478 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DRFNDRY5 161.0kV | 20SP | Base Case |  |  |  | 0.931 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GR ISLD3 345.0kV | 20SP 24SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8333 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S6815T1&T2 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.6983 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GRANGER5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8584 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S982 8 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.8797 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HARMONY5 161.0kV | 20SP | Base Case |  |  |  | 0.9239 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | F MONRO2 69.0kV | 29SP | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 |  |  |  | 0.9264 | 0.93 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GOODCTY3 115.0kV | 20SP 24WP 24SP | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 |  |  |  | 0.8527 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | UTICA R5 161.0kV | 20SP | Base Case |  |  |  | 0.9059 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5ADAIR2 161.0kV | 20SP 24WP | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 |  |  |  | 0.8828 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EAST 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9062 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 6815TP38 69.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.733 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | VIKRD CFU 5 161.0kV | 20SP | Base Case |  |  |  | 0.9383 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | CNTRLPL3 115.0kV | 20SP | Base Case |  |  |  | 0.9371 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 89 5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.8711 | 0.95 | 1.05 |  |  | External | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GR ISLD-LNX3 345.0kV | 20SP 24SP | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 |  |  |  | 0.8335 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | C.CREEK4 230.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8554 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 27FLETCHER7 115.0kV | 20SP | Base Case |  |  |  | 0.9476 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ASBURY 5 161.0kV | 20SP | Base Case |  |  |  | 0.9165 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NSI TAP3 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8632 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | TOMHAWK5 161.0kV | 20SP | Base Case |  |  |  | 0.9497 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | POSTVIL5 161.0kV | 20SP | Base Case |  |  |  | 0.9282 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ROSEHLW5 161.0kV | 20SP | Base Case |  |  |  | 0.8867 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NESSCTY3 115.0kV | 20SP 24SP | Base Case |  |  |  | 0.921 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | MIDPORT5 161.0kV | 20SP | Base Case |  |  |  | 0.9312 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WBURGE 5 161.0kV | 20SP | P42:345:OKGE:SB_REOW7312 |  |  |  | 0.8997 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | IANORTH8 69.0kV | 20SP | Base Case |  |  |  | 0.9432 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SETAB 3 115.0kV | 20SP 24WP | Base Case |  |  |  | 0.9361 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SWEET W3 345.0kV | 20SP 24SP | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 |  |  |  | 0.8535 | 0.9 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 87TH 7 345.0kV | 19WP | 104092: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  |  |  | 0.9472 | 0.95 | 1.05 |  |  | Internal | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | QUINN3 345.0kV | 20SP 29SP | Base Case |  |  |  | 0.8894 | 0.95 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | BVERVLLY 115.0kV | 20SP 24WP 24SP | P23:345:SUNC:SB_BRK482 |  |  |  | 0.8457 | 0.9 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | J475-J555POI 345.0kV | 20SP 29SP 24WP 19WP | Base Case |  |  |  | 0.8524 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | S1367 5 161.0kV | 24SP | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 |  |  |  | 0.9394 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | EASTOWN5 161.0kV | 20SP 29SP 24WP | Base Case |  |  |  | 0.9095 | 0.95 | 1.05 |  |  | Internal | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 6 ST 7 115.0kV | 20SP | Base Case |  |  |  | 0.9316 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GDMEC 3 345.0kV | 20SP 24WP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8627 | 0.9 | 1.05 |  |  | External | 0 | 2
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GEN-2017-030 345.0kV | 20SP 29SP 24WP 19WP 20G | Base Case |  |  |  | 0.8821 | 0.95 | 1.05 |  |  | Internal | 0 | 7
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | DEWITT 5 161.0kV | 20SP | P23:345:MEC:ATCHISON CO 903 |  |  |  | 0.8994 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 48 5 161.0kV | 20SP | Base Case |  |  |  | 0.912 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | SB 71 5 161.0kV | 20SP | P23:345:MEC:FALLOW AVE 903 |  |  |  | 0.8985 | 0.9 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | 5GENTRY 161.0kV | 20SP 24WP 19WP | Base Case |  |  |  | 0.8898 | 0.95 | 1.05 |  |  | External | 0 | 4
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HOLT 7 345.0kV | 20SP 24WP 24L | Base Case |  |  |  | 0.9219 | 0.95 | 1.05 |  |  | Internal | 0 | 3
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | HORIZON8 69.0kV | 20SP | Base Case |  |  |  | 0.9496 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | ADRIAN 5 161.0kV | 20SP | Base Case |  |  |  | 0.9189 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WTWEST 5 161.0kV | 20SP | Base Case |  |  |  | 0.9318 | 0.95 | 1.05 |  |  | External | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | WILLIAM3 115.0kV | 29SP | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 |  |  |  | 0.801 | 0.9 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | NEKOMA 3 115.0kV | 20SP | Base Case |  |  |  | 0.9375 | 0.95 | 1.05 |  |  | Internal | 0 | 1
S2 | GEN_043_044_045 | 00NR | NRIS | Voltage | GENOA 5 161.0kV | 20SP | Base Case |  |  |  | 0.939 | 0.95 | 1.05 |  |  | External | 0 | 1
S1 | GEN_025_028 | 00LVER | ERIS | Non-Converge | NA | 20SP0 | Under Several Contingencies - Refer to All Thermal Tap | [6 empty] | TBD
S1 | GEN_043_044_045 | 00LVER | ERIS | Non-Converge | NA | 20SP0 | Under Several Contingencies - Refer to All Thermal Tap | [6 empty] | TBD

## All Thermal
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONITORED ELEMENT | RATEA (MVA) | RATEB (MVA) | TDF | TC% LOADING (% MVA) | CONTINGENCY | Footprint | BC LOADING (% MVA) | LOADING Diff (% MVA)
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01344 | 104.37 | 81734: 337909 8ANO% 500 515305 FTSMITH8 500 1 515305 FTSMITH8 500 998257 FTSMITH3 161 3 515305 FTSMITH8 500 998256 FTSMTH6 161 6 515305 FTSMITH8 500 998255 FTSMITH4 161 4 515305 FTSMITH8 500 998253 FTSMITH1 345 1 | External | 102.19 | 2.18
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01371 | 104.37 | 81734: 337909 8ANO% 500 515305 FTSMITH8 500 1 515305 FTSMITH8 500 998257 FTSMITH3 161 3 515305 FTSMITH8 500 998256 FTSMTH6 161 6 515305 FTSMITH8 500 998255 FTSMITH4 161 4 515305 FTSMITH8 500 998253 FTSMITH1 345 1 | External | 102.19 | 2.18
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00085 | 146.33 | P23:500:EES-EAI:WH_BLF:B7914 | External | 146.33 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00088 | 146.33 | P23:500:EES-EAI:WH_BLF:B7914 | External | 146.33 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.001 | 128.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.24 | 0.01
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00101 | 128.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.24 | 0.01
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 70 | 70 | 0.00035 | 111.51 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 111.03 | 0.48
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 70 | 70 | 0.00036 | 111.51 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 111.03 | 0.48
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00086 | 102.95 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 102.2 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00088 | 102.95 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 102.2 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337753 8HS EHV% 500 337685 3HS EHV-W! 115 1 | 550 | 550 | 0.00029 | 104.9 | P23:HV-EHV:EES::8HS EHV%:5 | External | 104.96 | -0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337753 8HS EHV% 500 337685 3HS EHV-W! 115 1 | 550 | 550 | 0.00034 | 104.9 | P23:HV-EHV:EES::8HS EHV%:5 | External | 104.96 | -0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00125 | 101.32 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 100.41 | 0.91
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00123 | 101.32 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 100.41 | 0.91
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00115 | 136.56 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 135.17 | 1.39
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00121 | 136.56 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 135.17 | 1.39
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00012 | 100.1 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00019 | 100.1 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0015 | 176.07 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 174.9 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 176.07 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 174.9 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 70 | 70 | 0.00035 | 113.77 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 113.28 | 0.49
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 70 | 70 | 0.00037 | 113.77 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 113.28 | 0.49
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0022 | 104.57 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 104.11 | 0.46
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 104.57 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 104.11 | 0.46
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00136 | 111.56 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.97 | 1.59
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00134 | 111.56 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.97 | 1.59
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00032 | 128.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.79 | 0.05
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00033 | 128.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.79 | 0.05
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.77 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.77 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.77 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.77 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00411 | 117.2 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 117 | 0.2
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00421 | 117.2 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 117 | 0.2
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00136 | 111.56 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.97 | 1.59
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00134 | 111.56 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 109.97 | 1.59
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0022 | 102.29 | Base Case | External | 101.79 | 0.5
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 102.29 | Base Case | External | 101.79 | 0.5
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00153 | 106.15 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.9 | 0.25
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00156 | 106.15 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.9 | 0.25
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.0002 | 118.21 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.18 | 0.03
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00021 | 118.21 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.18 | 0.03
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00389 | 113.34 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00405 | 113.34 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01295 | 112.01 | P23:500:EES-EAI:ARK_NU:B5106 | External | 109.93 | 2.08
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01321 | 112.01 | P23:500:EES-EAI:ARK_NU:B5106 | External | 109.93 | 2.08
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00032 | 110.62 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.56 | 0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00033 | 110.62 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.56 | 0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00153 | 107.38 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.13 | 0.25
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00156 | 107.38 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.13 | 0.25
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.001 | 105.28 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 105.1 | 0.18
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00101 | 105.28 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 105.1 | 0.18
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00013 | 103.17 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 102.94 | 0.23
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00012 | 103.17 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 102.94 | 0.23
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00389 | 116.34 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 115.04 | 1.3
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00405 | 116.34 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 115.04 | 1.3
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00355 | 123.49 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 122.56 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00363 | 123.49 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 122.56 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 70 | 70 | 0.00035 | 113.77 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 113.28 | 0.49
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997543 161/69 69.0 1 | 70 | 70 | 0.00037 | 113.77 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 113.28 | 0.49
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00583 | 112.18 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00608 | 112.18 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00031 | 103.44 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 103 | 0.44
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00032 | 103.44 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 103 | 0.44
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00013 | 103.68 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 103.45 | 0.23
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00012 | 103.68 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 103.45 | 0.23
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00012 | 107.53 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00019 | 107.53 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00111 | 165.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 164.83 | 0.84
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00113 | 165.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 164.83 | 0.84
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00075 | 110.05 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 109.12 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00079 | 110.05 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 109.12 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00411 | 136.01 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 135.88 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00421 | 136.01 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 135.88 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00011 | 104.52 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 104.39 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00012 | 104.52 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 104.39 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00011 | 104.42 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 104.29 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00012 | 104.42 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 104.29 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00095 | 140.5 | P12:161:DPC:RCE-HAR5 | External | 139.33 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.001 | 140.5 | P12:161:DPC:RCE-HAR5 | External | 139.33 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00012 | 107.53 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00019 | 107.53 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997055 GLENHAM TR1 115 1 | 25 | 31 | 0.00018 | 102.54 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 102.52 | 0.02
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997055 GLENHAM TR1 115 1 | 25 | 31 | 0.00018 | 102.54 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 102.52 | 0.02
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.96 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.96 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.96 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.96 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0015 | 176.07 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 174.9 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 176.07 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 174.9 | 1.17
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00022 | 109.27 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 108.74 | 0.53
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00021 | 109.27 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 108.74 | 0.53
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01344 | 104.37 | P42:500:OKGE:SB_FTTH8585 | External | 102.19 | 2.18
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 396 | 396 | 0.01371 | 104.37 | P42:500:OKGE:SB_FTTH8585 | External | 102.19 | 2.18
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00012 | 107.53 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00019 | 107.53 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 107.61 | -0.08
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00348 | 116.28 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 115.46 | 0.82
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00356 | 116.28 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 115.46 | 0.82
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00011 | 104.42 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 104.29 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00012 | 104.42 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 104.29 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00102 | 130.7 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.7 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00103 | 130.7 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.7 | 0
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00348 | 116.28 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 115.46 | 0.82
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00356 | 116.28 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 115.46 | 0.82
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82953 | 120.75 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0022 | 104.81 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 104.36 | 0.45
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 104.81 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 104.36 | 0.45
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00086 | 102.75 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 102 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00088 | 102.75 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 102 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00012 | 100.1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00019 | 100.1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00095 | 134.31 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 133.11 | 1.2
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.001 | 134.31 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 133.11 | 1.2
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0022 | 104.57 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 104.11 | 0.46
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 104.57 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 104.11 | 0.46
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00086 | 102.75 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 102 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00088 | 102.75 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 102 | 0.75
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 70 | 70 | 0.00035 | 111.51 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 111.03 | 0.48
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997542 161/69 69.0 2 | 70 | 70 | 0.00036 | 111.51 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 111.03 | 0.48
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00159 | 135.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 134.93 | 0.17
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00162 | 135.1 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 134.93 | 0.17
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 117.52 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.48 | 0.04
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 117.52 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.48 | 0.04
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00389 | 116.34 | P11:024:DPC:ALMA2:6 | External | 115.04 | 1.3
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00405 | 116.34 | P11:024:DPC:ALMA2:6 | External | 115.04 | 1.3
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00011 | 104.52 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 104.39 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00012 | 104.52 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 104.39 | 0.13
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.0002 | 118.04 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.02 | 0.02
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00021 | 118.04 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.02 | 0.02
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00022 | 109.35 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 108.81 | 0.54
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00021 | 109.35 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 108.81 | 0.54
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 108.46 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.49 | -0.03
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 108.46 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.49 | -0.03
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00583 | 112.18 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00608 | 112.18 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00583 | 112.18 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00608 | 112.18 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 110.28 | 1.9
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00032 | 105.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.23 | 0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00033 | 105.29 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.23 | 0.06
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00354 | 108.01 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 107.08 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00362 | 108.01 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 107.08 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00159 | 115.25 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 115.1 | 0.15
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00162 | 115.25 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 115.1 | 0.15
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00012 | 100.1 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338137 5BATESVLE AR 161 338138 5MOOREFIELD 161 1 | 310 | 310 | 0.00019 | 100.1 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 100.17 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00031 | 100.25 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00032 | 100.25 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00355 | 123.49 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 122.56 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00363 | 123.49 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 122.56 | 0.93
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 117.1 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.06 | 0.04
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 117.1 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.06 | 0.04
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 337753 8HS EHV% 500 337740 3HS EHV-E! 115 1 | 550 | 550 | 0.00029 | 105.01 | P23:HV-EHV:EES::8HS EHV%:3 | External | 105.08 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337753 8HS EHV% 500 337740 3HS EHV-E! 115 1 | 550 | 550 | 0.00034 | 105.01 | P23:HV-EHV:EES::8HS EHV%:3 | External | 105.08 | -0.07
Thermal | 00LVER | S1 | 20SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00285 | 101.02 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 100.43 | 0.59
Thermal | 00LVER | S1 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00289 | 101.02 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 100.43 | 0.59
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08998 | 132.9 | Base Case | External | 131.64 | 1.26
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09182 | 132.9 | Base Case | External | 131.64 | 1.26
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00096 | 120.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 120.9 | -0.07
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00098 | 120.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 120.9 | -0.07
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 118.43 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 118.43 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00543 | 106.32 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1 | External | 100.93 | 5.39
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00575 | 106.32 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1 | External | 100.93 | 5.39
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.24331 | 116.07 | P12:161:OPPD:S1209-S1231 CKT 2 | Internal | 114.53 | 1.54
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 560 | 560 | 0.0106 | 103.37 | 636001 WEBSTER5 161 637035 J524 161 1: 636001 WEBSTER5 161 637035 J524 161 1 | External | 100.09 | 3.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 560 | 560 | 0.01099 | 103.37 | 636001 WEBSTER5 161 637035 J524 161 1: 636001 WEBSTER5 161 637035 J524 161 1 | External | 100.09 | 3.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0022 | 100.93 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 106.07 | -5.14
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0022 | 100.93 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 106.07 | -5.14
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.58 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 112.85 | -5.27
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.58 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 112.85 | -5.27
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00026 | 103.53 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 100.75 | 2.78
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00028 | 103.53 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 100.75 | 2.78
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00023 | 106.64 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.3 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00024 | 106.64 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.3 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00022 | 102.63 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 101.35 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00023 | 102.63 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 101.35 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00029 | 103.97 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 103.76 | 0.21
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00031 | 103.97 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 103.76 | 0.21
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 690 | 690 | 9e-05 | 194.28 | Base Case | External | 187.65 | 6.63
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 690 | 690 | 0.0001 | 194.28 | Base Case | External | 187.65 | 6.63
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00064 | 110.42 | Base Case | External | 109.62 | 0.8
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00066 | 110.42 | Base Case | External | 109.62 | 0.8
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00054 | 143.62 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 143 | 0.62
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00057 | 143.62 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 143 | 0.62
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00387 | 199.5 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 192.7 | 6.8
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00403 | 199.5 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 192.7 | 6.8
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00034 | 148.4 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 146.62 | 1.78
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00035 | 148.4 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 146.62 | 1.78
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00322 | 114.64 | Base Case | External | 112.06 | 2.58
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.0034 | 114.64 | Base Case | External | 112.06 | 2.58
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00697 | 107.53 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00679 | 107.53 | 93775: 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 2 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 1 659101 ANTELOPE-BE3 345 659212 DGC_____-BE3 345 2 659101 ANTELOPE-BE3 345 659218 COTEAU__-RR3 345 Z 659101 ANTELOPE-BE3 345 659384 ROUNDUP_-BE3 345 1 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 118.43 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 118.43 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00026 | 103.97 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 101.08 | 2.89
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00028 | 103.97 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 101.08 | 2.89
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608639 MNP-STP7 115 619701 GRE-ALDRICH7 115 1 | 77 | 84.7 | 4e-05 | 100.35 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608639 MNP-STP7 115 619701 GRE-ALDRICH7 115 1 | 77 | 84.7 | 5e-05 | 100.35 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03596 | 108.36 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 105.86 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.0357 | 108.36 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 105.86 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.035 | 108.8 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 106.98 | 1.82
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03473 | 108.8 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 106.98 | 1.82
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.77 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.77 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | 225 | 225 | 1e-05 | 104.77 | 672612 CONDIE 4 230 672512 CONDIE 6 138 1: 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | External | 104.77 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00054 | 139.79 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 139.56 | 0.23
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00057 | 139.79 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 139.56 | 0.23
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00039 | 119.26 | Base Case | External | 116.24 | 3.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00041 | 119.26 | Base Case | External | 116.24 | 3.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01004 | 107.86 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 106.23 | 1.63
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01056 | 107.86 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 106.23 | 1.63
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00064 | 118.14 | P23:345:XEL:8N22 SHC | External | 117.33 | 0.81
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00066 | 118.14 | P23:345:XEL:8N22 SHC | External | 117.33 | 0.81
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00098 | 123.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 123.21 | -0.07
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.001 | 123.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 123.21 | -0.07
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03628 | 101.45 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03816 | 101.45 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0024 | 117.78 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 117.11 | 0.67
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00248 | 117.78 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 117.11 | 0.67
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01619 | 103.29 | Base Case | External | 100.1 | 3.19
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01626 | 103.29 | Base Case | External | 100.1 | 3.19
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00107 | 149.12 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00116 | 149.12 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00022 | 102.63 | P11:024:DPC:ALMA2:6 | External | 101.35 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00023 | 102.63 | P11:024:DPC:ALMA2:6 | External | 101.35 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00831 | 111.86 | Base Case | External | 107.45 | 4.41
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00871 | 111.86 | Base Case | External | 107.45 | 4.41
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00267 | 110.7 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 108.34 | 2.36
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00275 | 110.7 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 108.34 | 2.36
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.02895 | 103.48 | Base Case | External | 104.03 | -0.55
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.02908 | 103.48 | Base Case | External | 104.03 | -0.55
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00151 | 157.78 | Base Case | External | 152.85 | 4.93
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00159 | 157.78 | Base Case | External | 152.85 | 4.93
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.00035 | 100.27 | P23:345:XEL:8N17 SHC | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.00037 | 100.27 | P23:345:XEL:8N17 SHC | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00242 | 133.94 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.69 | 3.25
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00236 | 133.94 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.69 | 3.25
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00408 | 117.33 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00431 | 117.33 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00408 | 117.33 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00431 | 117.33 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615135 G619TAM7 115 618203 GRE-TAMARAC7 115 1 | 50 | 50 | 1e-05 | 100.94 | Base Case | External | 100.94 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615135 G619TAM7 115 618203 GRE-TAMARAC7 115 1 | 50 | 50 | 1e-05 | 100.94 | Base Case | External | 100.94 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21536 | 112.61 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | Internal | 110.23 | 2.38
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 118.09 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 118.09 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.0003 | 121.78 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 116.83 | 4.95
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 121.78 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 116.83 | 4.95
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.07538 | 123.33 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 160.56 | -37.23
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00033 | 145.48 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 143.73 | 1.75
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00035 | 145.48 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 143.73 | 1.75
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01116 | 103.23 | Base Case | External | 102.46 | 0.77
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01107 | 103.23 | Base Case | External | 102.46 | 0.77
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00321 | 119.23 | Base Case | External | 113.21 | 6.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00329 | 119.23 | Base Case | External | 113.21 | 6.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00022 | 115.3 | P13:138-115:MP:TCH:TR4 | External | 112.8 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00024 | 115.3 | P13:138-115:MP:TCH:TR4 | External | 112.8 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 500 | 500 | 0.00304 | 110.8 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.42 | 1.38
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 500 | 500 | 0.0032 | 110.8 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.42 | 1.38
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00149 | 202.1 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 204.29 | -2.19
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00153 | 202.1 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 204.29 | -2.19
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608642 VERNDLE7 115 615567 GRE-WINGRIV7 115 1 | 98 | 107.8 | 4e-05 | 107.64 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External | 107 | 0.64
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608642 VERNDLE7 115 615567 GRE-WINGRIV7 115 1 | 98 | 107.8 | 5e-05 | 107.64 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External | 107 | 0.64
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00032 | 105.68 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.66 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00033 | 105.68 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.66 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00285 | 105.15 | Base Case | External | 110.49 | -5.34
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00288 | 105.15 | Base Case | External | 110.49 | -5.34
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 118.43 | P13:161-69:EES-EAI:HERGET:AT1 | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 118.43 | P13:161-69:EES-EAI:HERGET:AT1 | External | 118.37 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.0002 | 105.13 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.11 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.0002 | 105.13 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.11 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00149 | 111.08 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 112.28 | -1.2
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00153 | 111.08 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 112.28 | -1.2
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | 325 | 325 | 0.0071 | 144.6 | Base Case | External | 132.13 | 12.47
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | 325 | 325 | 0.00701 | 144.6 | Base Case | External | 132.13 | 12.47
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 500 | 500 | 0.00304 | 110.8 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.42 | 1.38
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997579 345-161 161 2 | 500 | 500 | 0.0032 | 110.8 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.42 | 1.38
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0024 | 117.78 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 117.11 | 0.67
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00248 | 117.78 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 117.11 | 0.67
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00027 | 100.8 | Base Case | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00028 | 100.8 | Base Case | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00399 | 119.36 | Base Case | External | 110.03 | 9.33
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.0041 | 119.36 | Base Case | External | 110.03 | 9.33
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01033 | 108.03 | P12:161:XEL:JEF-WHT | External | 106.12 | 1.91
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01086 | 108.03 | P12:161:XEL:JEF-WHT | External | 106.12 | 1.91
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 560 | 560 | 0.0106 | 103.38 | 637035 J524 161 3WXFMR J524 1: 637035 J524 161 997470 J524 34.5 1 637032 J524 COL2 34.5 997470 J524 34.5 1 637034 J524 TERT 13.2 997470 J524 34.5 1 | External | 100.09 | 3.29
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997479 WEB AB 161 1 | 560 | 560 | 0.01099 | 103.38 | 637035 J524 161 3WXFMR J524 1: 637035 J524 161 997470 J524 34.5 1 637032 J524 COL2 34.5 997470 J524 34.5 1 637034 J524 TERT 13.2 997470 J524 34.5 1 | External | 100.09 | 3.29
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 600180 J587_GEN2 34.5 603305 J587 BLZSTR2 115 2 | 100 | 120 | 3e-05 | 100.85 | Base Case | External | 100.76 | 0.09
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 600180 J587_GEN2 34.5 603305 J587 BLZSTR2 115 2 | 100 | 120 | 3e-05 | 100.85 | Base Case | External | 100.76 | 0.09
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01031 | 109.9 | P12:161:XEL:ECL-WHT | External | 108.17 | 1.73
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01084 | 109.9 | P12:161:XEL:ECL-WHT | External | 108.17 | 1.73
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03596 | 108.36 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 105.86 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.0357 | 108.36 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 105.86 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00338 | 118.11 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 119.15 | -1.04
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00353 | 118.11 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 119.15 | -1.04
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00321 | 116.45 | Base Case | External | 107.97 | 8.48
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00329 | 116.45 | Base Case | External | 107.97 | 8.48
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00107 | 140.86 | Base Case | External | 133.96 | 6.9
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00116 | 140.86 | Base Case | External | 133.96 | 6.9
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00054 | 143.62 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 143 | 0.62
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00057 | 143.62 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 143 | 0.62
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 70 | 70 | 0.0001 | 103.94 | 615060 GRE-ST BONI8 69 3WXFMR 115-69 2: 615060 GRE-ST BONI8 69.0 997580 115-69.0 69.0 2 615548 GRE-ST BONI7 115 997580 115-69.0 69.0 2 615551 GRE-STBONI2T 13.8 997580 115-69.0 69.0 2 | External | 103.09 | 0.85
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 70 | 70 | 0.00011 | 103.94 | 615060 GRE-ST BONI8 69 3WXFMR 115-69 2: 615060 GRE-ST BONI8 69.0 997580 115-69.0 69.0 2 615548 GRE-ST BONI7 115 997580 115-69.0 69.0 2 615551 GRE-STBONI2T 13.8 997580 115-69.0 69.0 2 | External | 103.09 | 0.85
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00033 | 145.48 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 143.73 | 1.75
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00035 | 145.48 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 143.73 | 1.75
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00267 | 118.35 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 116.03 | 2.32
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00275 | 118.35 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 116.03 | 2.32
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00132 | 106.59 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 104.19 | 2.4
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00139 | 106.59 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 104.19 | 2.4
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.59 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.59 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 672612 CONDIE 4 230 672512 CONDIE 6 138 1 | 235 | 235 | 1e-05 | 100.59 | 672612 CONDIE 4 230 672512 CONDIE 6 138 2: 672612 CONDIE 4 230 672512 CONDIE 6 138 2 | External | 100.59 | 0
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08998 | 130.25 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 129.96 | 0.29
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09182 | 130.25 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 129.96 | 0.29
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608642 VERNDLE7 115 619701 GRE-ALDRICH7 115 1 | 77 | 84.7 | 4e-05 | 101.85 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External | 101.08 | 0.77
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608642 VERNDLE7 115 619701 GRE-ALDRICH7 115 1 | 77 | 84.7 | 5e-05 | 101.85 | 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1: 608612 RIVERTN4 230 615566 GRE-WINGRIV4 230 1 | External | 101.08 | 0.77
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00947 | 116.87 | Base Case | External | 112.33 | 4.54
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00992 | 116.87 | Base Case | External | 112.33 | 4.54
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00149 | 111.08 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 112.28 | -1.2
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00153 | 111.08 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 112.28 | -1.2
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00022 | 102.19 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 100.91 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00023 | 102.19 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 100.91 | 1.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04834 | 130.03 | Base Case | External | 128.68 | 1.35
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04894 | 130.03 | Base Case | External | 128.68 | 1.35
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 500 | 500 | 0.00304 | 108.58 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 107.52 | 1.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 500 | 500 | 0.0032 | 108.58 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 107.52 | 1.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00064 | 104.27 | Base Case | External | 103.51 | 0.76
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00066 | 104.27 | Base Case | External | 103.51 | 0.76
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.56 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 112.58 | -5.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.56 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 112.58 | -5.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00064 | 111.33 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 110.54 | 0.79
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00066 | 111.33 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 110.54 | 0.79
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00071 | 133.29 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 132.34 | 0.95
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00073 | 133.29 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 132.34 | 0.95
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00543 | 106.32 | 631180 FREEBORN5 161 631181 G870_TAP5 161 1: 631180 FREEBORN5 161 631181 G870_TAP5 161 1 | External | 100.93 | 5.39
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00575 | 106.32 | 631180 FREEBORN5 161 631181 G870_TAP5 161 1: 631180 FREEBORN5 161 631181 G870_TAP5 161 1 | External | 100.93 | 5.39
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00034 | 148.4 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 146.62 | 1.78
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00035 | 148.4 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 146.62 | 1.78
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.0002 | 104.99 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 104.96 | 0.03
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.0002 | 104.99 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 104.96 | 0.03
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00392 | 129.56 | P11:024:DPC:ALMA2:6 | External | 126.6 | 2.96
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00407 | 129.56 | P11:024:DPC:ALMA2:6 | External | 126.6 | 2.96
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00595 | 146.89 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 135.32 | 11.57
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00613 | 146.89 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 135.32 | 11.57
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.035 | 106.36 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 104.06 | 2.3
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03473 | 106.36 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 104.06 | 2.3
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 117.92 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.9 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 117.92 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.9 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00595 | 146.89 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 135.32 | 11.57
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00613 | 146.89 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 135.32 | 11.57
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00085 | 114.18 | Base Case | External | 115.46 | -1.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00087 | 114.18 | Base Case | External | 115.46 | -1.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 800 | 1084 | 0.00465 | 107.16 | Base Case | External | 103.15 | 4.01
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 800 | 1084 | 0.00491 | 107.16 | Base Case | External | 103.15 | 4.01
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00064 | 118.11 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 117.37 | 0.74
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00066 | 118.11 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 117.37 | 0.74
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00026 | 103.58 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 100.81 | 2.77
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608667 POTLTCH7 115 608668 CLOQUET7 115 1 | 90 | 90 | 0.00028 | 103.58 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 100.81 | 2.77
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00392 | 127.82 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 124.85 | 2.97
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00407 | 127.82 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 124.85 | 2.97
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00225 | 100.43 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00233 | 100.43 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 500 | 500 | 0.00304 | 108.58 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 107.52 | 1.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997579 345-161 161 2 | 500 | 500 | 0.0032 | 108.58 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 107.52 | 1.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01644 | 147.19 | Base Case | External | 141.22 | 5.97
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.0181 | 147.19 | Base Case | External | 141.22 | 5.97
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00267 | 118.33 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 116.02 | 2.31
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00275 | 118.33 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 116.02 | 2.31
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00338 | 118.11 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 119.15 | -1.04
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00353 | 118.11 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 119.15 | -1.04
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00365 | 149.52 | Base Case | External | 145.67 | 3.85
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00384 | 149.52 | Base Case | External | 145.67 | 3.85
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.12918 | 109.2 | Base Case | Internal
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.12662 | 109.2 | Base Case | Internal
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 118.09 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 118.09 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00693 | 105.42 | Base Case | External | 104.33 | 1.09
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00675 | 105.42 | Base Case | External | 104.33 | 1.09
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00059 | 102.57 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00061 | 102.57 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00408 | 117.33 | P21:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00431 | 117.33 | P21:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 116.04 | 1.29
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00149 | 202.1 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 204.29 | -2.19
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00153 | 202.1 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 204.29 | -2.19
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04051 | 101.27 | Base Case | Internal
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.03976 | 101.27 | Base Case | Internal
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 118.09 | P13:161-69:EES-EAI:HERGET:AT2 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 118.09 | P13:161-69:EES-EAI:HERGET:AT2 | External | 118.03 | 0.06
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00578 | 150.81 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 139.71 | 11.1
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00594 | 150.81 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 139.71 | 11.1
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00132 | 107.16 | P11:024:DPC:ALMA2:6 | External | 104.77 | 2.39
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00139 | 107.16 | P11:024:DPC:ALMA2:6 | External | 104.77 | 2.39
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00267 | 110.68 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 108.33 | 2.35
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00275 | 110.68 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 108.33 | 2.35
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 70 | 70 | 0.0001 | 103.94 | P13:69-115-13:GRE-XEL-XEL:AUTO-SINGLE:GRE-STBONI8:GRE-STBONI7:GRE-STBONI2T:2 | External | 103.09 | 0.85
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615548 GRE-ST BONI7 115 997582 115-69.0 69.0 1 | 70 | 70 | 0.00011 | 103.94 | P13:69-115-13:GRE-XEL-XEL:AUTO-SINGLE:GRE-STBONI8:GRE-STBONI7:GRE-STBONI2T:2 | External | 103.09 | 0.85
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00023 | 107.1 | P11:024:DPC:ALMA2:6 | External | 105.76 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00024 | 107.1 | P11:024:DPC:ALMA2:6 | External | 105.76 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00267 | 118.35 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 116.03 | 2.32
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00275 | 118.35 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 116.03 | 2.32
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03629 | 101.43 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03817 | 101.43 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00079 | 101.24 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 101.03 | 0.21
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00077 | 101.24 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 101.03 | 0.21
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00387 | 202.86 | P11:024:DPC:ALMA2:6 | External | 195.98 | 6.88
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00403 | 202.86 | P11:024:DPC:ALMA2:6 | External | 195.98 | 6.88
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00242 | 133.94 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.69 | 3.25
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00236 | 133.94 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.69 | 3.25
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.0003 | 121.78 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 116.83 | 4.95
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 121.78 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 116.83 | 4.95
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.98 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 108.98 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0022 | 100.38 | Base Case | External | 105.74 | -5.36
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.0022 | 100.38 | Base Case | External | 105.74 | -5.36
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00392 | 129.56 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 126.6 | 2.96
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00407 | 129.56 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 126.6 | 2.96
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00387 | 202.86 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 195.98 | 6.88
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00403 | 202.86 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 195.98 | 6.88
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00225 | 106.88 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 108.98 | -2.1
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00234 | 106.88 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 108.98 | -2.1
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00132 | 107.16 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 104.77 | 2.39
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603097 REDROCK7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00139 | 107.16 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 104.77 | 2.39
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00064 | 111.33 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 110.54 | 0.79
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00066 | 111.33 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 110.54 | 0.79
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01794 | 140.69 | Base Case | External | 137.09 | 3.6
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.0196 | 140.69 | Base Case | External | 137.09 | 3.6
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00084 | 126.1 | P23:500:EES-EAI:WH_BLF:B7914 | External | 126.18 | -0.08
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00086 | 126.1 | P23:500:EES-EAI:WH_BLF:B7914 | External | 126.18 | -0.08
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00023 | 107.1 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 105.76 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997547 161/69 69.0 1 | 70 | 70 | 0.00024 | 107.1 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 105.76 | 1.34
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01001 | 107.77 | Base Case | External | 105.47 | 2.3
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00971 | 107.77 | Base Case | External | 105.47 | 2.3
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00262 | 138.1 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 140.38 | -2.28
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00271 | 138.1 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 140.38 | -2.28
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00575 | 150.35 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 139.35 | 11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0059 | 150.35 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 139.35 | 11
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03596 | 110.87 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 108.85 | 2.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.0357 | 110.87 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 108.85 | 2.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 138.14 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 135.02 | 3.12
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 138.14 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 135.02 | 3.12
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.56 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 112.58 | -5.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00228 | 107.56 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 112.58 | -5.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00031 | 107.25 | P23:500:EMI-EES:ABF_FRKLN-A | External | 107.05 | 0.2
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00031 | 107.25 | P23:500:EMI-EES:ABF_FRKLN-A | External | 107.05 | 0.2
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00496 | 108.46 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 107.5 | 0.96
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00506 | 108.46 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 107.5 | 0.96
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01048 | 142.52 | Base Case | External | 137.61 | 4.91
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01097 | 142.52 | Base Case | External | 137.61 | 4.91
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00558 | 150.84 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 137.8 | 13.04
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00575 | 150.84 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 137.8 | 13.04
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0024 | 118.12 | Base Case | External | 117.01 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00248 | 118.12 | Base Case | External | 117.01 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00025 | 133.69 | P13:115:XEL:COL TR5 AS- | External | 132.05 | 1.64
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997546 161/69 69.0 2 | 70 | 70 | 0.00027 | 133.69 | P13:115:XEL:COL TR5 AS- | External | 132.05 | 1.64
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 600178 J460_GEN2 34.5 601088 BLZNG STR1 3 345 2 | 100 | 120 | 0.00026 | 100.95 | Base Case | External | 100.68 | 0.27
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 600178 J460_GEN2 34.5 601088 BLZNG STR1 3 345 2 | 100 | 120 | 0.00027 | 100.95 | Base Case | External | 100.68 | 0.27
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00045 | 100.3 | Base Case | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00047 | 100.3 | Base Case | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00054 | 139.79 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 139.56 | 0.23
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00057 | 139.79 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 139.56 | 0.23
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 138.2 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 135.08 | 3.12
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 138.2 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 135.08 | 3.12
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.0005 | 121.88 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 119.99 | 1.89
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00053 | 121.88 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 119.99 | 1.89
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0036 | 125.79 | Base Case | External | 116.76 | 9.03
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00369 | 125.79 | Base Case | External | 116.76 | 9.03
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00062 | 101.72 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 100.61 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00068 | 101.72 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 100.61 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 588307 ASGI1706-XFM 34.5 588306 ASGI1706 161 1 | 104 | 130 | 0.0004 | 118.65 | Base Case | External | 116.31 | 2.34
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 588307 ASGI1706-XFM 34.5 588306 ASGI1706 161 1 | 104 | 130 | 0.0004 | 118.65 | Base Case | External | 116.31 | 2.34
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00267 | 110.7 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 108.34 | 2.36
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00275 | 110.7 | P13:115-161:ALTW:AUTO-SINGLE:BERTRAM7:BERTRAM5:1 | External | 108.34 | 2.36
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.18099 | 100.5 | 82346: 646201 S1201 5 161 646206 S1206 5 161 1 646201 S1201 5 161 646220 S1220 5 161 1 646201 S1201 5 161 646229 S1229 5 161 1 646201 S1201 5 161 646286 S1286 5 161 1 646201 S1201 5 161 997267 S1201 T1 69.0 1 647105 JCT205 8 69.0 647901 S901 8 69.0 1 647901 S901 8 69.0 647912 S912 8 69.0 1 647901 S901 8 69.0 645051 JONES 1G 13.8 1 647901 S901 8 69.0 645052 JONES 2G 13.8 1 647901 S901 8 69.0 997267 S1201 T1 69.0 1 | Internal
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 138.62 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 135.38 | 3.24
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 138.62 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 135.38 | 3.24
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00062 | 101.72 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 100.61 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00068 | 101.72 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 100.61 | 1.11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14476 | 139.39 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 159.72 | -20.33
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.03596 | 110.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 108.85 | 2.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997751 HAWTHORN20 161 20 | 500 | 550 | 0.0357 | 110.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 108.85 | 2.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00072 | 101.1 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00072 | 101.1 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04834 | 130.1 | Base Case | External | 128.73 | 1.37
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04894 | 130.1 | Base Case | External | 128.73 | 1.37
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00071 | 133.29 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 132.34 | 0.95
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00073 | 133.29 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 132.34 | 0.95
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00022 | 116.82 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 113.95 | 2.87
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00024 | 116.82 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 113.95 | 2.87
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00262 | 137.4 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 140.5 | -3.1
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.0027 | 137.4 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 140.5 | -3.1
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.0055 | 153.59 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 141.48 | 12.11
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00565 | 153.59 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 141.48 | 12.11
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.0001 | 111.05 | Base Case | External | 108.53 | 2.52
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00011 | 111.05 | Base Case | External | 108.53 | 2.52
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03629 | 101.43 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 1332.6 | 1332.6 | 0.03817 | 101.43 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00107 | 148.35 | 300031 1CHOTST3 16 300069 5CHOTEAU1 161 10: 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00116 | 148.35 | 300031 1CHOTST3 16 300069 5CHOTEAU1 161 10: 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | External
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 118.39 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 118.37 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 118.39 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 118.37 | 0.02
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00022 | 115.3 | P13:138-115:MP:TCH:TR4(1) | External | 112.8 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00024 | 115.3 | P13:138-115:MP:TCH:TR4(1) | External | 112.8 | 2.5
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.0024 | 133.58 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.07 | 3.51
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00234 | 133.58 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.07 | 3.51
Thermal | 00NR | S2 | 20SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01735 | 105.57 | Base Case | External | 103.59 | 1.98
Thermal | 00NR | S2 | 20SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01812 | 105.57 | Base Case | External | 103.59 | 1.98
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00093 | 152.93 | P23:500:EES-EAI:WH_BLF:B7914 | External | 152.73 | 0.2
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00096 | 152.93 | P23:500:EES-EAI:WH_BLF:B7914 | External | 152.73 | 0.2
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00028 | 102.2 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 102.16 | 0.04
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00027 | 102.2 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 102.16 | 0.04
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00345 | 108.65 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1: 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | External | 107.19 | 1.46
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00359 | 108.65 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1: 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | External | 107.19 | 1.46
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00102 | 139.57 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.41 | 0.16
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00103 | 139.57 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.41 | 0.16
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.0017 | 107.67 | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 107.11 | 0.56
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00172 | 107.67 | 67882: 334383 4PETRYWDS% 138 334384 4CHEEK! 138 1 334211 4BDAYTON! 138 334383 4PETRYWDS% 138 1 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 107.11 | 0.56
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00157 | 113.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.53 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0016 | 113.9 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.53 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00186 | 107.34 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 106.83 | 0.51
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0018 | 107.34 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 106.83 | 0.51
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00134 | 108.07 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 107.19 | 0.88
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00131 | 108.07 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 107.19 | 0.88
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997045 GLENHAM TR1 115 1 | 25 | 31 | 0.00017 | 115.88 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 115.86 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997045 GLENHAM TR1 115 1 | 25 | 31 | 0.00017 | 115.88 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 115.86 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0011 | 136.68 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 135.39 | 1.29
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00115 | 136.68 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 135.39 | 1.29
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00157 | 105.48 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.1 | 0.38
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0016 | 105.48 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.1 | 0.38
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00117 | 102.1 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 101.73 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00115 | 102.1 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 101.73 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 166.76 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 166 | 0.76
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 166.76 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 166 | 0.76
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.54 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 109.54 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.54 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 109.54 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 106.81 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 106.1 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 106.81 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 106.1 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00135 | 124.17 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.66 | 1.51
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00133 | 124.17 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.66 | 1.51
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 128.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.4 | 0.19
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00038 | 128.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.4 | 0.19
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 5e-05 | 100.46 | P12:HV-EHV:EES::8ANO%:5ANO%:1 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 9e-05 | 100.46 | P12:HV-EHV:EES::8ANO%:5ANO%:1 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00495 | 112.5 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 112.26 | 0.24
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00508 | 112.5 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 112.26 | 0.24
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00262 | 107.27 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 106.48 | 0.79
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00265 | 107.27 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 106.48 | 0.79
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00135 | 124.17 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.66 | 1.51
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00133 | 124.17 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 122.66 | 1.51
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.04 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.04 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | P13:161-69:EES-EAI:HERGET:AT1 | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | P13:161-69:EES-EAI:HERGET:AT1 | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00313 | 210.5 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 204.45 | 6.05
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00322 | 210.5 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 204.45 | 6.05
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00012 | 124.18 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.16 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00012 | 124.18 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 124.16 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 102.95 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00554 | 102.95 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00083 | 123.84 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 122.48 | 1.36
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00085 | 123.84 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 122.48 | 1.36
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00347 | 102.42 | 85218: 505460 BULL SH5 161 505466 BSH3&4 1 13.8 1 505460 BULL SH5 161 505464 BSH #2 1 13.8 1 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 505460 BULL SH5 161 505462 BSH #1 1 13.8 1 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | External | 101.26 | 1.16
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00358 | 102.42 | 85218: 505460 BULL SH5 161 505466 BSH3&4 1 13.8 1 505460 BULL SH5 161 505464 BSH #2 1 13.8 1 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 505460 BULL SH5 161 505462 BSH #1 1 13.8 1 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | External | 101.26 | 1.16
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | P13:161-69:EES-EAI:HERGET:AT2 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | P13:161-69:EES-EAI:HERGET:AT2 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 102.99 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 102.99 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00037 | 109.93 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.76 | 0.17
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00038 | 109.93 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.76 | 0.17
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00157 | 115.08 | P23:500:EES-EAI:WH_BLF:B7914 | External | 114.71 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0016 | 115.08 | P23:500:EES-EAI:WH_BLF:B7914 | External | 114.71 | 0.37
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00014 | 108.98 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 108.69 | 0.29
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00013 | 108.98 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External | 108.69 | 0.29
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00159 | 100.59 | P12:HV:EES::6CHPTSR1:6CHINA%:1 | External | 100.01 | 0.58
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00161 | 100.59 | P12:HV:EES::6CHPTSR1:6CHINA%:1 | External | 100.01 | 0.58
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00159 | 100.59 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1: 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 100.01 | 0.58
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | 206 | 206 | 0.00161 | 100.59 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1: 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | External | 100.01 | 0.58
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 7e-05 | 107.08 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 107.1 | -0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 5e-05 | 107.08 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 107.1 | -0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 102.95 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00554 | 102.95 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 107.51 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 106.8 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 107.51 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 106.8 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00031 | 104.3 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 103.89 | 0.41
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00033 | 104.3 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 103.89 | 0.41
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00015 | 109.52 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 109.23 | 0.29
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00013 | 109.52 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 109.23 | 0.29
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00034 | 105.63 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00042 | 105.63 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 70 | 70 | 0.00034 | 111.54 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 111.1 | 0.44
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 70 | 70 | 0.00035 | 111.54 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 111.1 | 0.44
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 5e-05 | 100.46 | 337909 8ANO% 500 3WXFMR ANO 1: 337909 8ANO% 500 998897 ANO 161 1 337912 5ANO% 161 998897 ANO 161 1 337913 1ANO AUX 22.0 998897 ANO 161 1 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 9e-05 | 100.46 | 337909 8ANO% 500 3WXFMR ANO 1: 337909 8ANO% 500 998897 ANO 161 1 337912 5ANO% 161 998897 ANO 161 1 337913 1ANO AUX 22.0 998897 ANO 161 1 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | 106 | 106 | 0.0037 | 103.09 | 92681: 515300 FTSMTHE5 161 515301 FTSMTHW5 161 1 515300 FTSMTHE5 161 515301 FTSMTHW5 161 2 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 515301 FTSMTHW5 161 998255 FTSMITH4 161 4 515301 FTSMTHW5 161 998254 FTSMITH5 161 5 515299 BEVYTAP5 161 515300 FTSMTHE5 161 1 515300 FTSMTHE5 161 515310 QUANXTP5 161 1 515300 FTSMTHE5 161 515345 COLONY 5 161 1 515300 FTSMTHE5 161 998257 FTSMITH3 161 3 515300 FTSMTHE5 161 998256 FTSMTH6 161 6 | External | 101.01 | 2.08
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | 106 | 106 | 0.00377 | 103.09 | 92681: 515300 FTSMTHE5 161 515301 FTSMTHW5 161 1 515300 FTSMTHE5 161 515301 FTSMTHW5 161 2 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 515301 FTSMTHW5 161 998255 FTSMITH4 161 4 515301 FTSMTHW5 161 998254 FTSMITH5 161 5 515299 BEVYTAP5 161 515300 FTSMTHE5 161 1 515300 FTSMTHE5 161 515310 QUANXTP5 161 1 515300 FTSMTHE5 161 515345 COLONY 5 161 1 515300 FTSMTHE5 161 998257 FTSMITH3 161 3 515300 FTSMTHE5 161 998256 FTSMTH6 161 6 | External | 101.01 | 2.08
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00057 | 155.51 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 155.13 | 0.38
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00056 | 155.51 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 155.13 | 0.38
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00495 | 131.46 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 131.26 | 0.2
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00508 | 131.46 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 131.26 | 0.2
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 102.99 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 102.99 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 102.99 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 126.75 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 126.75 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 5e-05 | 100.46 | P13:500-161:EES-EAI:ARK_NU:AT3 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | 600 | 600 | 9e-05 | 100.46 | P13:500-161:EES-EAI:ARK_NU:AT3 | External | 100.51 | -0.05
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00092 | 141.51 | P12:161:DPC:RCE-HAR5 | External | 140.39 | 1.12
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00097 | 141.51 | P12:161:DPC:RCE-HAR5 | External | 140.39 | 1.12
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00034 | 105.63 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00042 | 105.63 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00262 | 101.17 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 100.37 | 0.8
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00265 | 101.17 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 100.37 | 0.8
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 126.38 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 126.38 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00355 | 111.32 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 110.17 | 1.15
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0037 | 111.32 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 110.17 | 1.15
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00171 | 154.45 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 151.34 | 3.11
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00174 | 154.45 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 151.34 | 3.11
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 166.76 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 166 | 0.76
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 166.76 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 166 | 0.76
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00024 | 117.6 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 117 | 0.6
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00022 | 117.6 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 117 | 0.6
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00034 | 105.63 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00042 | 105.63 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 105.71 | -0.08
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 107.43 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 106.72 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 107.43 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 106.72 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 103.12 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 102.86 | 0.26
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 103.12 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 102.86 | 0.26
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 70 | 70 | 0.00034 | 113.8 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 113.35 | 0.45
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 70 | 70 | 0.00036 | 113.8 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 113.35 | 0.45
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00104 | 142.24 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.07 | 0.17
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00105 | 142.24 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.07 | 0.17
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82892 | 121.56 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0003 | 112.54 | P13:161-69:ALTW:AUTO-SINGLE:RICE5:RICE8:1 | External | 112.12 | 0.42
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00032 | 112.54 | P13:161-69:ALTW:AUTO-SINGLE:RICE5:RICE8:1 | External | 112.12 | 0.42
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.54 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 109.54 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 109.54 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 109.54 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00345 | 108.92 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | External | 107.42 | 1.5
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00359 | 108.92 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | External | 107.42 | 1.5
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00313 | 210.5 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 204.45 | 6.05
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00322 | 210.5 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 204.45 | 6.05
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00092 | 135.05 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 133.79 | 1.26
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00097 | 135.05 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 133.79 | 1.26
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00194 | 105.79 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.6 | 0.19
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00196 | 105.79 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 105.6 | 0.19
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 104.69 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 104.44 | 0.25
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 104.69 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 104.44 | 0.25
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00012 | 122.88 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 123.06 | -0.18
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00012 | 122.88 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 123.06 | -0.18
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00345 | 108.92 | 338108 5ST JOE 161 338110 5HILLTOP% 161 1: 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | External | 107.42 | 1.5
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338125 5MT HOME 161 338814 5SOUTHLAND# 161 1 | 162 | 162 | 0.00359 | 108.92 | 338108 5ST JOE 161 338110 5HILLTOP% 161 1: 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | External | 107.42 | 1.5
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00355 | 114.31 | P11:024:DPC:ALMA2:6 | External | 113.13 | 1.18
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0037 | 114.31 | P11:024:DPC:ALMA2:6 | External | 113.13 | 1.18
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00012 | 124 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 123.99 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00012 | 124 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 123.99 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 70 | 70 | 0.00034 | 111.54 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 111.1 | 0.44
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997534 161/69 69.0 2 | 70 | 70 | 0.00035 | 111.54 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 111.1 | 0.44
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 110.13 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 110.13 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 110.13 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 110.13 | 0
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 112.36 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 112.35 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 112.36 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 112.35 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 102.95 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00554 | 102.95 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 101.13 | 1.82
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 108.13 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 107.42 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 108.13 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 107.42 | 0.71
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00028 | 108.72 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 108.7 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00025 | 108.72 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 108.7 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 103.12 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 102.86 | 0.26
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00044 | 103.12 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 102.86 | 0.26
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00355 | 114.31 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 113.13 | 1.18
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0037 | 114.31 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 113.13 | 1.18
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00037 | 104.39 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.21 | 0.18
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00038 | 104.39 | P23:500:EES-EAI:WH_BLF:B7914 | External | 104.21 | 0.18
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00083 | 116.33 | Base Case | External | 114.9 | 1.43
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00085 | 116.33 | Base Case | External | 114.9 | 1.43
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00083 | 124.04 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 122.69 | 1.35
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00085 | 124.04 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 122.69 | 1.35
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00031 | 103.66 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.25 | 0.41
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00033 | 103.66 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.25 | 0.41
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 70 | 70 | 0.00034 | 113.8 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 113.35 | 0.45
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997535 161/69 69.0 1 | 70 | 70 | 0.00036 | 113.8 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 113.35 | 0.45
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 122.02 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.01 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00012 | 122.02 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.01 | 0.01
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.04 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.04 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 115.64 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 115.62 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 115.64 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 115.62 | 0.02
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00083 | 123.84 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 122.48 | 1.36
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00085 | 123.84 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 122.48 | 1.36
Thermal | 00LVER | S1 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00024 | 117.68 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 117.08 | 0.6
Thermal | 00LVER | S1 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00022 | 117.68 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 117.08 | 0.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00512 | 121.22 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 118.79 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00537 | 121.22 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 118.79 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08894 | 124.14 | Base Case | External | 119.37 | 4.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09073 | 124.14 | Base Case | External | 119.37 | 4.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03872 | 120.94 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 117.88 | 3.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03818 | 120.94 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 117.88 | 3.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00827 | 118.18 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00841 | 118.18 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00099 | 133.7 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.52 | 0.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.001 | 133.7 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.52 | 0.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07377 | 113.72 | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 107.79 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07216 | 113.72 | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 107.79 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01299 | 108.09 | P23:345:MEC:GDMEC 901 | External | 106.74 | 1.35
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01334 | 108.09 | P23:345:MEC:GDMEC 901 | External | 106.74 | 1.35
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00364 | 107.29 | P23:345:ALTW:MITCHLCO:1140 | External | 105.32 | 1.97
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00386 | 107.29 | P23:345:ALTW:MITCHLCO:1140 | External | 105.32 | 1.97
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00145 | 111.06 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00146 | 111.06 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00614 | 122.39 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 122.53 | -0.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00623 | 122.39 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 122.53 | -0.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00364 | 108.06 | P23:345:ALTW:MITCHLCO:1160 | External | 106.38 | 1.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00386 | 108.06 | P23:345:ALTW:MITCHLCO:1160 | External | 106.38 | 1.68
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 128.9 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 128.08 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00015 | 128.9 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 128.08 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01294 | 109.63 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 109.81 | -0.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01328 | 109.63 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 109.81 | -0.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 7e-05 | 112.68 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 111.77 | 0.91
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 8e-05 | 112.68 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 111.77 | 0.91
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.0002 | 120.46 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 119.58 | 0.88
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00021 | 120.46 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 119.58 | 0.88
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.24358 | 108.6 | P12:161:OPPD:S1209-S1231 CKT 2 | Internal | 107.45 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00553 | 107.38 | P23:345:XEL:8S51 HMP | External | 106.1 | 1.28
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00583 | 107.38 | P23:345:XEL:8S51 HMP | External | 106.1 | 1.28
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00032 | 143.05 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 142.03 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00034 | 143.05 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 142.03 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00426 | 112.04 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 110.73 | 1.31
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00407 | 112.04 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 110.73 | 1.31
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00285 | 111.53 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 110.89 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00301 | 111.53 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 110.89 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03559 | 101.95 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03531 | 101.95 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.0026 | 102.55 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00267 | 102.55 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03602 | 101.94 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03575 | 101.94 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03873 | 121.6 | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 118.11 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03818 | 121.6 | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 118.11 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05493 | 105.02 | P12:345:WERE:ROSE-WOLF_345:: | Internal | 100.8 | 4.22
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05433 | 105.02 | P12:345:WERE:ROSE-WOLF_345:: | Internal | 100.8 | 4.22
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00054 | 115.64 | Base Case | External | 115.07 | 0.57
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00056 | 115.64 | Base Case | External | 115.07 | 0.57
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00467 | 152.56 | P23:345:MEC:GDMEC 901 | External | 143.97 | 8.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00479 | 152.56 | P23:345:MEC:GDMEC 901 | External | 143.97 | 8.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00402 | 122.56 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 117.23 | 5.33
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00412 | 122.56 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 117.23 | 5.33
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.0033 | 106.12 | Base Case | External | 104.45 | 1.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00349 | 106.12 | Base Case | External | 104.45 | 1.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01132 | 172.33 | P23:345:ITCM:HCKRYCK:FUT2 | External | 172.16 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01177 | 172.33 | P23:345:ITCM:HCKRYCK:FUT2 | External | 172.16 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00048 | 113.38 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 109.09 | 4.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.0005 | 113.38 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 109.09 | 4.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00103 | 132.44 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 127.77 | 4.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00112 | 132.44 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 127.77 | 4.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 3e-05 | 105.6 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1 | External | 105.59 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 4e-05 | 105.6 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1 | External | 105.59 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01299 | 113.04 | P23:345:MEC:GDMEC 901 | External | 111.13 | 1.91
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01334 | 113.04 | P23:345:MEC:GDMEC 901 | External | 111.13 | 1.91
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01402 | 106.93 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01485 | 106.93 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 997475 DGG9T1 161 1 | 560 | 700 | 0.02877 | 105.36 | P23:345:MEC:SYCAMORE 905 | External | 103.12 | 2.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 997475 DGG9T1 161 1 | 560 | 700 | 0.02942 | 105.36 | P23:345:MEC:SYCAMORE 905 | External | 103.12 | 2.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00023 | 104.17 | 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1: 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00024 | 104.17 | 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1: 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01178 | 120.54 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 116.85 | 3.69
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01227 | 120.54 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 116.85 | 3.69
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.1851 | 102.49 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18393 | 102.49 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00283 | 110.55 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 109.91 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00298 | 110.55 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 109.91 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00974 | 107.08 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 105.12 | 1.96
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00995 | 107.08 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 105.12 | 1.96
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02446 | 123.44 | P23:345:MEC:SYCAMORE 905 | External | 120.09 | 3.35
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02489 | 123.44 | P23:345:MEC:SYCAMORE 905 | External | 120.09 | 3.35
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00533 | 104.84 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00562 | 104.84 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00125 | 103.18 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 102.11 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00126 | 103.18 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 102.11 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00613 | 151.87 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 144.32 | 7.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00634 | 151.87 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 144.32 | 7.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00026 | 103.11 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 102.35 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00029 | 103.11 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 102.35 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00026 | 102.27 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 101.55 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00029 | 102.27 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 101.55 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.0002 | 101.43 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00018 | 101.43 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00838 | 121.6 | P23:345:ITCM:HCKRYCK:FUT2 | External | 121.2 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00875 | 121.6 | P23:345:ITCM:HCKRYCK:FUT2 | External | 121.2 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 0.00027 | 102.39 | P13:161-69:XEL:AUTO-SINGLE:GRAVLISLE5:GRAVLISLE8:5 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 0.00028 | 102.39 | P13:161-69:XEL:AUTO-SINGLE:GRAVLISLE5:GRAVLISLE8:5 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.0002 | 101.54 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00018 | 101.54 | P22:345:AMMO::LABADIE:3 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00199 | 103.76 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 103.38 | 0.38
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00202 | 103.76 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 103.38 | 0.38
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01002 | 141.96 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 137.17 | 4.79
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01052 | 141.96 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 137.17 | 4.79
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00778 | 125.08 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 122.98 | 2.1
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0075 | 125.08 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 122.98 | 2.1
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00038 | 145.15 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 144.94 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00039 | 145.15 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 144.94 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 9e-05 | 106.88 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 106.4 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00022 | 106.88 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 106.4 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.0026 | 112.35 | P23:345:MEC:HILLS 934 | External | 111.03 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00267 | 112.35 | P23:345:MEC:HILLS 934 | External | 111.03 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00053 | 123.38 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 121.23 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00056 | 123.38 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 121.23 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 560 | 560 | 0.01948 | 112.21 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 108.8 | 3.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 560 | 560 | 0.02026 | 112.21 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 108.8 | 3.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00077 | 114.04 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 111.37 | 2.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00081 | 114.04 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 111.37 | 2.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.0116 | 107.53 | P23:345:MEC:GDMEC 902 | External | 105.95 | 1.58
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01179 | 107.53 | P23:345:MEC:GDMEC 902 | External | 105.95 | 1.58
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 129 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 128.21 | 0.79
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00015 | 129 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 128.21 | 0.79
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00782 | 115.85 | P23:345:AMMO::ZACHARY:2 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00788 | 115.85 | P23:345:AMMO::ZACHARY:2 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00249 | 122.31 | 631083 TRAER 5 161 631086 DYSART 5 161 1: 631083 TRAER 5 161 631086 DYSART 5 161 1 | External | 117.58 | 4.73
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00251 | 122.31 | 631083 TRAER 5 161 631086 DYSART 5 161 1: 631083 TRAER 5 161 631086 DYSART 5 161 1 | External | 117.58 | 4.73
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00172 | 220.02 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 216.32 | 3.7
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00175 | 220.02 | 631009 NEWHAL5 161 631080 STON PT5 161 1: 631009 NEWHAL5 161 631080 STON PT5 161 1 | External | 216.32 | 3.7
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 187 | 233.8 | 0.00019 | 110.13 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 109.27 | 0.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 187 | 233.8 | 0.00022 | 110.13 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 109.27 | 0.86
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00145 | 102.22 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00146 | 102.22 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00044 | 143.36 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 142.9 | 0.46
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00047 | 143.36 | 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 142.9 | 0.46
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 344535 7ENON 345 345230 7MONTGMRY 345 1 | 956 | 956 | 0.01604 | 100.78 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 344535 7ENON 345 345230 7MONTGMRY 345 1 | 956 | 956 | 0.01582 | 100.78 | 63178: 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 344154 7BLAND 345 344224 7CALAWY 1 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00029 | 116.51 | Base Case | External | 115.73 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00031 | 116.51 | Base Case | External | 115.73 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00024 | 137.81 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 137.45 | 0.36
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00022 | 137.81 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 137.45 | 0.36
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.1851 | 102.49 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18393 | 102.49 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01264 | 133.44 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 133.44 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00054 | 123.02 | P23:345:XEL:8N22 SHC | External | 122.23 | 0.79
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00056 | 123.02 | P23:345:XEL:8N22 SHC | External | 122.23 | 0.79
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 100.97 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 100.97 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.03004 | 104.17 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 103.04 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.03058 | 104.17 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External | 103.04 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00152 | 132.83 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 130.15 | 2.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00163 | 132.83 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 130.15 | 2.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21505 | 102.33 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal | 101.11 | 1.22
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.00048 | 113.38 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 109.09 | 4.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 301422 2LEE 69.0 631216 WEVER5 161 1 | 84 | 84 | 0.0005 | 113.38 | 347840 5NIOTA 161 631216 WEVER5 161 1: 347840 5NIOTA 161 631216 WEVER5 161 1 | External | 109.09 | 4.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00782 | 115.85 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00788 | 115.85 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 120.54 | P22:345:MEC:SUB 92 | External | 119.14 | 1.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00267 | 120.54 | P22:345:MEC:SUB 92 | External | 119.14 | 1.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.001 | 136.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.08 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00102 | 136.25 | P23:500:EES-EAI:WH_BLF:B7914 | External | 136.08 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 106.16 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.99 | 2.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01078 | 106.16 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.99 | 2.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00133 | 105.23 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 103.82 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.0014 | 105.23 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 103.82 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00145 | 102.22 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00146 | 102.22 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00193 | 125.12 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 124.47 | 0.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00201 | 125.12 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 124.47 | 0.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01611 | 102.32 | Base Case | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01617 | 102.32 | Base Case | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00133 | 105.98 | P11:024:DPC:ALMA2:6 | External | 104.55 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.0014 | 105.98 | P11:024:DPC:ALMA2:6 | External | 104.55 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.8292 | 112.16 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 229.9 | 252.8 | 0.00066 | 101.11 | P23:345:XEL:8P4 ASK | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 229.9 | 252.8 | 0.00071 | 101.11 | P23:345:XEL:8P4 ASK | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02777 | 122.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 119.72 | 2.31
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02844 | 122.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 119.72 | 2.31
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00159 | 112.34 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 111 | 1.34
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00167 | 112.34 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 111 | 1.34
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04904 | 112.73 | P23:345:ALTW:MITCHLCO:1150 | External | 110.99 | 1.74
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04968 | 112.73 | P23:345:ALTW:MITCHLCO:1150 | External | 110.99 | 1.74
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00625 | 106.31 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 104.08 | 2.23
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00638 | 106.31 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 104.08 | 2.23
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.0101 | 107.21 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.19 | 4.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.01029 | 107.21 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.19 | 4.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00216 | 101.28 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00216 | 101.28 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 100.97 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 100.97 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00834 | 107.5 | Base Case | External | 103.53 | 3.97
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00874 | 107.5 | Base Case | External | 103.53 | 3.97
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04846 | 105.17 | Base Case | External | 103.56 | 1.61
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04904 | 105.17 | Base Case | External | 103.56 | 1.61
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01135 | 112.83 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 111.71 | 1.12
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01167 | 112.83 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 111.71 | 1.12
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11197 | 104.82 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11167 | 104.82 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997049 GLENHAM TR1 115 1 | 25 | 31 | 0.00019 | 113.07 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.78 | 0.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997049 GLENHAM TR1 115 1 | 25 | 31 | 0.00019 | 113.07 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.78 | 0.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00353 | 146.71 | Base Case | External | 145.17 | 1.54
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00368 | 146.71 | Base Case | External | 145.17 | 1.54
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.0001 | 102.8 | 601001 FORBES 2 500 601013 ROSEAUS2 500 1: 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | External | 102.2 | 0.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00014 | 102.8 | 601001 FORBES 2 500 601013 ROSEAUS2 500 1: 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | External | 102.2 | 0.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.0013 | 101.9 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 100.87 | 1.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.00124 | 101.9 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 100.87 | 1.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03093 | 106.19 | P55:161-345:KCPL:HAWTHORN_BUS_25:: | Internal | 103.11 | 3.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03068 | 106.19 | P55:161-345:KCPL:HAWTHORN_BUS_25:: | Internal | 103.11 | 3.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 107.9 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 107.69 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 107.9 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 107.69 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00285 | 111.53 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 110.89 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00301 | 111.53 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 110.89 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.00984 | 103.06 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.01002 | 103.06 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00614 | 122.39 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 122.53 | -0.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00623 | 122.39 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 122.53 | -0.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 120.98 | P13:161-69:EES-EAI:HERGET:AT1 | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 120.98 | P13:161-69:EES-EAI:HERGET:AT1 | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02526 | 104.97 | Base Case | External | 104.03 | 0.94
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02628 | 104.97 | Base Case | External | 104.03 | 0.94
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03074 | 112.91 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 109.55 | 3.36
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03042 | 112.91 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 109.55 | 3.36
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 125.07 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 124.02 | 1.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 125.07 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 124.02 | 1.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00074 | 110.95 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 108.73 | 2.22
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00078 | 110.95 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 108.73 | 2.22
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 560 | 560 | 0.00593 | 118.27 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 116.95 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 560 | 560 | 0.0071 | 118.27 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 116.95 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00212 | 114.4 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 115.05 | -0.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00219 | 114.4 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 115.05 | -0.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 127.76 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 126.69 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 127.76 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 126.69 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.00984 | 103.06 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631081 M-TOWN 5 161 1 | 299 | 299 | 0.01002 | 103.06 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00054 | 108.13 | Base Case | External | 107.52 | 0.61
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00056 | 108.13 | Base Case | External | 107.52 | 0.61
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00248 | 142.36 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 139.05 | 3.31
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00241 | 142.36 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 139.05 | 3.31
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00369 | 118.11 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 117.16 | 0.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00393 | 118.11 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 117.16 | 0.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00369 | 118.11 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 117.16 | 0.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00393 | 118.11 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 117.16 | 0.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00083 | 142.71 | Base Case | External | 140.56 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00085 | 142.71 | Base Case | External | 140.56 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00388 | 158.85 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 153.46 | 5.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00399 | 158.85 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 153.46 | 5.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00553 | 107.04 | P23:345:XEL:8S51 HMP | External | 105.78 | 1.26
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00583 | 107.04 | P23:345:XEL:8S51 HMP | External | 105.78 | 1.26
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00395 | 173.9 | P23:345:ALTW:MITCHLCO:1150 | External | 170.71 | 3.19
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00418 | 173.9 | P23:345:ALTW:MITCHLCO:1150 | External | 170.71 | 3.19
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.0017 | 104 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 103.36 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.0018 | 104 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 103.36 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.033 | 116.2 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03365 | 116.2 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03559 | 104.22 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03531 | 104.22 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0113 | 126.29 | P23:345:MEC:GDMEC 902 | External | 120.92 | 5.37
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01177 | 126.29 | P23:345:MEC:GDMEC 902 | External | 120.92 | 5.37
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00351 | 110.78 | P23:345:ALTW:MITCHLCO:1150 | External | 108.92 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00374 | 110.78 | P23:345:ALTW:MITCHLCO:1150 | External | 108.92 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21557 | 101.57 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | Internal | 100.33 | 1.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.17054 | 104.71 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16897 | 104.71 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 100.97 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 100.97 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 101.03 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00216 | 101.28 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00216 | 101.28 | P21:345:MEC:AUTO-SINGLE:OAKGROV3:LOUISA3:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 106.39 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 106.18 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 106.39 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 106.18 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00016 | 106.64 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 106.45 | 0.19
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00018 | 106.64 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 106.45 | 0.19
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00505 | 113.42 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00541 | 113.42 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00033 | 145.93 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 144.89 | 1.04
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00035 | 145.93 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 144.89 | 1.04
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 111.5 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 109.79 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00034 | 111.5 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 109.79 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.12497 | 116.95 | 82353: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 646221 S1221 5 161 646255 S1255 5 161 1 646233 S1233 5 161 646255 S1255 5 161 1 646255 S1255 5 161 646259 S1259 5 161 1 646255 S1255 5 161 646260 S1260 5 161 1 646255 S1255 5 161 997272 S3455 T1 161 1 646255 S1255 5 161 997271 S3455 T3 161 1 | Internal | 125.55 | -8.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.07559 | 120.06 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 156.04 | -35.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00053 | 100.03 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00056 | 100.03 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00218 | 116.87 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 113.59 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00228 | 116.87 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 113.59 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 100.89 | Base Case | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01078 | 100.89 | Base Case | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00315 | 135.59 | Base Case | External | 134.29 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00324 | 135.59 | Base Case | External | 134.29 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.72 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 111.97 | 0.75
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.72 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 111.97 | 0.75
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00065 | 101.89 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 101.38 | 0.51
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00066 | 101.89 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 101.38 | 0.51
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00247 | 110.69 | P23:345:GRE:PVS 19JB1 | External | 108.81 | 1.88
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00275 | 110.69 | P23:345:GRE:PVS 19JB1 | External | 108.81 | 1.88
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01184 | 118.14 | P23:345:MEC:GDMEC 901 | External | 112.5 | 5.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01233 | 118.14 | P23:345:MEC:GDMEC 901 | External | 112.5 | 5.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00286 | 219.74 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 212.15 | 7.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00313 | 219.74 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 212.15 | 7.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 222.7 | 222.7 | 0.00194 | 109.39 | P23:345:XEL:8P33 KOL | External | 107.83 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 222.7 | 222.7 | 0.00204 | 109.39 | P23:345:XEL:8P33 KOL | External | 107.83 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00709 | 106.09 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 101.84 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00752 | 106.09 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 101.84 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 185.81 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 185.87 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00103 | 185.81 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 185.87 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00613 | 151.87 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 144.32 | 7.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00634 | 151.87 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 144.32 | 7.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00043 | 127.56 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 126.36 | 1.2
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 127.56 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 126.36 | 1.2
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00744 | 124.27 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 122.23 | 2.04
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0072 | 124.27 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External | 122.23 | 2.04
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01248 | 148.15 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 144.31 | 3.84
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01299 | 148.15 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 144.31 | 3.84
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11197 | 104.82 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11167 | 104.82 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00724 | 111.84 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 107.48 | 4.36
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00768 | 111.84 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 107.48 | 4.36
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00568 | 142.96 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 139.93 | 3.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00602 | 142.96 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 139.93 | 3.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.00017 | 100.95 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.19 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.00018 | 100.95 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.19 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00402 | 122.48 | P11:345:AMMO::CALLAWAY:1 | External | 116.81 | 5.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00413 | 122.48 | P11:345:AMMO::CALLAWAY:1 | External | 116.81 | 5.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 110.74 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.5 | 0.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00038 | 110.74 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.5 | 0.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 7e-05 | 126.31 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 125.3 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 8e-05 | 126.31 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 125.3 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00397 | 163.44 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 157.71 | 5.73
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00408 | 163.44 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 157.71 | 5.73
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 123.59 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 123.59 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00757 | 117.68 | P23:345:XEL:8S25 WLM AS | External | 114.86 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00793 | 117.68 | P23:345:XEL:8S25 WLM AS | External | 114.86 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00539 | 107.64 | P23:345:AMIL::HERLEMAN:1 | External | 108.23 | -0.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00551 | 107.64 | P23:345:AMIL::HERLEMAN:1 | External | 108.23 | -0.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07287 | 112.22 | P23:345:MEC:GRIMES 901 | External | 109.1 | 3.12
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07483 | 112.22 | P23:345:MEC:GRIMES 901 | External | 109.1 | 3.12
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00449 | 120.06 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 119.67 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00441 | 120.06 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 119.67 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01061 | 134.97 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 130.14 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01115 | 134.97 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 130.14 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00037 | 104.21 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 103.71 | 0.5
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00038 | 104.21 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 103.71 | 0.5
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01254 | 145.45 | P23:345:MEC:GDMEC 901 | External | 138.98 | 6.47
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01306 | 145.45 | P23:345:MEC:GDMEC 901 | External | 138.98 | 6.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 123.59 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 123.59 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00361 | 118.5 | P23:345:XEL:8M38 CNC | External | 117.67 | 0.83
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00383 | 118.5 | P23:345:XEL:8M38 CNC | External | 117.67 | 0.83
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 111.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.82 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 111.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.82 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04904 | 112.9 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 111.05 | 1.85
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04968 | 112.9 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 111.05 | 1.85
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.72 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.72 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01623 | 112.23 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 107.28 | 4.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01788 | 112.23 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 107.28 | 4.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.0026 | 102.55 | P22:345:MEC:SUB 92 | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00267 | 102.55 | P22:345:MEC:SUB 92 | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 106.36 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.19 | 2.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01078 | 106.36 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.19 | 2.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00102 | 102.13 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 102.16 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00103 | 102.13 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 102.16 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00121 | 151.66 | P23:345:MEC:GDMEC 901 | External | 150.6 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00123 | 151.66 | P23:345:MEC:GDMEC 901 | External | 150.6 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 106.39 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 106.18 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00042 | 106.39 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 106.18 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00441 | 129.04 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 123.5 | 5.54
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00452 | 129.04 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 123.5 | 5.54
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01023 | 100.16 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01079 | 100.16 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00122 | 146.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 142.04 | 4.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00131 | 146.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 142.04 | 4.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00627 | 111 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 108.37 | 2.63
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.0064 | 111 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 108.37 | 2.63
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608616 HILLTOP4 230 997592 HIL1 115 1 | 187 | 233 | 0.00019 | 110.15 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 109.29 | 0.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608616 HILLTOP4 230 997592 HIL1 115 1 | 187 | 233 | 0.00022 | 110.15 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 109.29 | 0.86
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00827 | 118.18 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00841 | 118.18 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03559 | 104.22 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03531 | 104.22 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00121 | 154.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 153.06 | 1.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00123 | 154.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 153.06 | 1.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00662 | 122 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 119.3 | 2.7
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00693 | 122 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 119.3 | 2.7
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 127.07 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 126.01 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 127.07 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 126.01 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 120.62 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 120.62 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00402 | 118.53 | Base Case | External | 113.51 | 5.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00413 | 118.53 | Base Case | External | 113.51 | 5.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 227 | 227 | 0.00151 | 104.61 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 104.21 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300059 5BIG CK 161 345941 5WARENTN 161 1 | 227 | 227 | 0.00141 | 104.61 | 344535 7ENON 345 345230 7MONTGMRY 345 1: 344535 7ENON 345 345230 7MONTGMRY 345 1 | External | 104.21 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.0002 | 120.67 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 119.77 | 0.9
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00021 | 120.67 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 119.77 | 0.9
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00435 | 116.88 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00475 | 116.88 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00103 | 131.62 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 127.07 | 4.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00112 | 131.62 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 127.07 | 4.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01138 | 114.98 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 113.84 | 1.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0117 | 114.98 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 113.84 | 1.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 121.26 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 121.26 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00249 | 106.26 | P23:345:GRE:PVS 19JB4 | External | 105.01 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00276 | 106.26 | P23:345:GRE:PVS 19JB4 | External | 105.01 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00071 | 108.63 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 106.95 | 1.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.0007 | 108.63 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 106.95 | 1.68
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00315 | 126.79 | Base Case | External | 123.61 | 3.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00324 | 126.79 | Base Case | External | 123.61 | 3.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00037 | 105.69 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 105.26 | 0.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00038 | 105.69 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 105.26 | 0.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00105 | 138.47 | Base Case | External | 135.7 | 2.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00113 | 138.47 | Base Case | External | 135.7 | 2.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 141 | 141 | 0.00035 | 126.54 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 124.91 | 1.63
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 141 | 141 | 0.00037 | 126.54 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 124.91 | 1.63
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 257 | 257 | 0.00472 | 105.38 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 103.87 | 1.51
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337374 3DOWNSVILLE 115 337414 3STERL2% 115 1 | 257 | 257 | 0.00477 | 105.38 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 103.87 | 1.51
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 281.6 | 281.6 | 1e-05 | 120.4 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 119.76 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 281.6 | 281.6 | 2e-05 | 120.4 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 119.76 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16983 | 102.76 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16843 | 102.76 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00364 | 107.55 | P23:345:ALTW:MITCHLCO:1150 | External | 105.86 | 1.69
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00386 | 107.55 | P23:345:ALTW:MITCHLCO:1150 | External | 105.86 | 1.69
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 9e-05 | 108.35 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 107.58 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.0001 | 108.35 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 107.58 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00803 | 115.93 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | External | 113.13 | 2.8
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00783 | 115.93 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | External | 113.13 | 2.8
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00605 | 121.28 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 119.67 | 1.61
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00638 | 121.28 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 119.67 | 1.61
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 112.93 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 109.44 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 112.93 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 109.44 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00819 | 108.66 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 106.01 | 2.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00833 | 108.66 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 106.01 | 2.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00071 | 130.83 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 129.56 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00075 | 130.83 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 129.56 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00435 | 116.88 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00475 | 116.88 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03014 | 115.03 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal | 108.49 | 6.54
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.0044 | 129.42 | P23:345:XEL:8S22 WLM | External | 125.34 | 4.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.0047 | 129.42 | P23:345:XEL:8S22 WLM | External | 125.34 | 4.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03093 | 106.19 | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.11 | 3.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03068 | 106.19 | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.11 | 3.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 0.00167 | 114.79 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 113.6 | 1.19
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 0.00178 | 114.79 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 113.6 | 1.19
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01203 | 133.08 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 127.45 | 5.63
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01261 | 133.08 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 127.45 | 5.63
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18509 | 102.47 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18392 | 102.47 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 102.95 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 102.78 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 102.95 | 672696 BRADA 4 230 672699 NBEC 4 230 1: 672696 BRADA 4 230 672699 NBEC 4 230 1 | External | 102.78 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08894 | 123.21 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 118.61 | 4.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09073 | 123.21 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 118.61 | 4.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00312 | 120.74 | P12:230:OTP::HANKSON4:OAKES 4 | External | 119.72 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00323 | 120.74 | P12:230:OTP::HANKSON4:OAKES 4 | External | 119.72 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00536 | 103.2 | P23:345:XEL:8S50 HMP | External | 102.03 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00565 | 103.2 | P23:345:XEL:8S50 HMP | External | 102.03 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00019 | 104.77 | 608666 FONDULAC 115 608676 HIBBARD7 115 1: 608666 FONDULAC 115 608676 HIBBARD7 115 1 | External | 104.22 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.0002 | 104.77 | 608666 FONDULAC 115 608676 HIBBARD7 115 1: 608666 FONDULAC 115 608676 HIBBARD7 115 1 | External | 104.22 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 995 | 995 | 0.01195 | 105.28 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 103.3 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 995 | 995 | 0.01294 | 105.28 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 103.3 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04846 | 129.23 | Base Case | External | 127.78 | 1.45
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04904 | 129.23 | Base Case | External | 127.78 | 1.45
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 120.98 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 120.98 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00125 | 103.18 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 102.11 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00126 | 103.18 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 102.11 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 213.59 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 210.44 | 3.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 213.59 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 210.44 | 3.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.0189 | 105.4 | P23:345:MEC:SYCAMORE 905 | External | 102.89 | 2.51
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.01961 | 105.4 | P23:345:MEC:SYCAMORE 905 | External | 102.89 | 2.51
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05732 | 111.32 | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.0564 | 111.32 | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00226 | 103.76 | P23:345:MEC:LOUISA 964 | External | 103.32 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00232 | 103.76 | P23:345:MEC:LOUISA 964 | External | 103.32 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 123.59 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 123.59 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 122.74 | 0.85
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04904 | 112.85 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 111.01 | 1.84
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04968 | 112.85 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 111.01 | 1.84
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00291 | 108.01 | 681521 SENECA 5 161 681526 BELLCTR5 161 1: 681521 SENECA 5 161 681526 BELLCTR5 161 1 | External | 106.03 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00308 | 108.01 | 681521 SENECA 5 161 681526 BELLCTR5 161 1: 681521 SENECA 5 161 681526 BELLCTR5 161 1 | External | 106.03 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00291 | 108.01 | P12:161:DPC:AUTO-SINGLE:SENECA5:BELLCTR5:1 | External | 106.03 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00308 | 108.01 | P12:161:DPC:AUTO-SINGLE:SENECA5:BELLCTR5:1 | External | 106.03 | 1.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 470 | 517 | 0.00111 | 103.28 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 102.51 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 470 | 517 | 0.0012 | 103.28 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 102.51 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03559 | 101.95 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03531 | 101.95 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02524 | 106.56 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 105.55 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02627 | 106.56 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External | 105.55 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.1851 | 104.29 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18393 | 104.29 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00467 | 152.55 | P23:345:MEC:GDMEC 902 | External | 143.98 | 8.57
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00479 | 152.55 | P23:345:MEC:GDMEC 902 | External | 143.98 | 8.57
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.63 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 111.92 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.63 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 111.92 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 0.00027 | 102.39 | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 5: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | 70 | 80.5 | 0.00028 | 102.39 | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 5: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00022 | 104.21 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 103.5 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00023 | 104.21 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 103.5 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01155 | 109.52 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 110.02 | -0.5
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01173 | 109.52 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 110.02 | -0.5
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 122.84 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 119.47 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 122.84 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 119.47 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00782 | 115.85 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00788 | 115.85 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 109.95 | 5.9
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 0.00091 | 100.59 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External | 100.11 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 0.00095 | 100.59 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External | 100.11 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00154 | 124.39 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 121.93 | 2.46
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.0016 | 124.39 | 631100 LIBERTY5 161 631159 HCKRYCK5 161 1: 631100 LIBERTY5 161 631159 HCKRYCK5 161 1 | External | 121.93 | 2.46
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01453 | 135.01 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 131.64 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01415 | 135.01 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 131.64 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608672 HILLTOP7 115 997592 HIL1 115 1 | 187 | 233 | 0.00019 | 112.08 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 111.14 | 0.94
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608672 HILLTOP7 115 997592 HIL1 115 1 | 187 | 233 | 0.00022 | 112.08 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 111.14 | 0.94
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00533 | 104.84 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00562 | 104.84 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.63 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 111.92 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 112.63 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 111.92 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00054 | 114.81 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 113.94 | 0.87
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00056 | 114.81 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 113.94 | 0.87
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01053 | 192.42 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 189.23 | 3.19
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01163 | 192.42 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 189.23 | 3.19
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01053 | 107.83 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 105.19 | 2.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01163 | 107.83 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 105.19 | 2.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 111.5 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 109.79 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00034 | 111.5 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 109.79 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01402 | 106.93 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01485 | 106.93 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.0002 | 135 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 133.93 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00021 | 135 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 133.93 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 111.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.66 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 111.68 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 111.66 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00024 | 137.9 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 137.54 | 0.36
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00022 | 137.9 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 137.54 | 0.36
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 120.62 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 120.62 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 4e-05 | 101.12 | P12:HV:EES::6WILLOW_GL%:6PECUE:1 | External | 101.11 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 4e-05 | 101.12 | P12:HV:EES::6WILLOW_GL%:6PECUE:1 | External | 101.11 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00026 | 101.6 | 602014 BLUE LK4 230 619940 HUC-MCLEOD 4 230 1: 602014 BLUE LK4 230 619940 HUC-MCLEOD 4 230 1 | External | 100.88 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00029 | 101.6 | 602014 BLUE LK4 230 619940 HUC-MCLEOD 4 230 1: 602014 BLUE LK4 230 619940 HUC-MCLEOD 4 230 1 | External | 100.88 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00354 | 119.57 | P11:024:DPC:ALMA2:6 | External | 118.01 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00369 | 119.57 | P11:024:DPC:ALMA2:6 | External | 118.01 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00013 | 144.04 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 143.06 | 0.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00015 | 144.04 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 143.06 | 0.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00439 | 128.99 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.1 | 3.89
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00469 | 128.99 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.1 | 3.89
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00285 | 109.73 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.18 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00301 | 109.73 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 109.18 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03293 | 105.49 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 100.77 | 4.72
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03249 | 105.49 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 100.77 | 4.72
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00355 | 120.95 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 119.87 | 1.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00368 | 120.95 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 119.87 | 1.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00599 | 145.83 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 138.77 | 7.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00617 | 145.83 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 138.77 | 7.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00758 | 120.14 | P23:345:XEL:SPS 8S72 HNA | External | 117.13 | 3.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00794 | 120.14 | P23:345:XEL:SPS 8S72 HNA | External | 117.13 | 3.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03872 | 121.61 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 118.14 | 3.47
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03818 | 121.61 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 118.14 | 3.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.0116 | 107.52 | P23:345:MEC:GDMEC 901 | External | 105.94 | 1.58
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01179 | 107.52 | P23:345:MEC:GDMEC 901 | External | 105.94 | 1.58
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00388 | 158.85 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 153.46 | 5.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00399 | 158.85 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 153.46 | 5.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03293 | 105.49 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 100.77 | 4.72
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03249 | 105.49 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 100.77 | 4.72
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00102 | 102.13 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 102.16 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00103 | 102.13 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 102.16 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 123.51 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 123.5 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 123.51 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 123.5 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 956 | 1152 | 0.03911 | 106.06 | P23:345:MEC:LOUISA 924 | External | 104.18 | 1.88
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | 956 | 1152 | 0.04003 | 106.06 | P23:345:MEC:LOUISA 924 | External | 104.18 | 1.88
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01288 | 161.41 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 155.48 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0135 | 161.41 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 155.48 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02215 | 181.73 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 176.24 | 5.49
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02432 | 181.73 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 176.24 | 5.49
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01128 | 163.2 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 157.96 | 5.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01185 | 163.2 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 157.96 | 5.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00599 | 145.83 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 138.77 | 7.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00617 | 145.83 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External | 138.77 | 7.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00037 | 114.6 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 114.16 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00038 | 114.6 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 114.16 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00283 | 110.55 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 109.91 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997571 345-161 161 1 | 500 | 500 | 0.00298 | 110.55 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 109.91 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00704 | 117.1 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 115.39 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00686 | 117.1 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 115.39 | 1.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 121.26 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 121.26 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00033 | 145.93 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 144.89 | 1.04
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00035 | 145.93 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 144.89 | 1.04
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00627 | 110.5 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 107.54 | 2.96
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.0064 | 110.5 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 107.54 | 2.96
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00157 | 108.99 | P23:345:XEL:8M54 SCO | External | 107.72 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00167 | 108.99 | P23:345:XEL:8M54 SCO | External | 107.72 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00984 | 117.99 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 114.31 | 3.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01002 | 117.99 | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1: 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | External | 114.31 | 3.68
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02892 | 117.35 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 116.16 | 1.19
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.03031 | 117.35 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA | External | 116.16 | 1.19
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07039 | 125.75 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 123.1 | 2.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07163 | 125.75 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 123.1 | 2.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00153 | 105.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.26 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00156 | 105.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.26 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 120.54 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 119.14 | 1.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00267 | 120.54 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 119.14 | 1.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04904 | 112.78 | P23:345:ALTW:MITCHLCO:1150 | External | 111.03 | 1.75
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04968 | 112.78 | P23:345:ALTW:MITCHLCO:1150 | External | 111.03 | 1.75
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00023 | 104.17 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00024 | 104.17 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00641 | 117.62 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 115.24 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00654 | 117.62 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 115.24 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00105 | 222.83 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 219.59 | 3.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00111 | 222.83 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 219.59 | 3.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00953 | 103.98 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 101.91 | 2.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.00973 | 103.98 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 101.91 | 2.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 106.12 | Base Case | External | 106.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00059 | 106.12 | Base Case | External | 106.13 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00136 | 128.05 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 124.46 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.0014 | 128.05 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 124.46 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03293 | 108.56 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 103.44 | 5.12
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03249 | 108.56 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 103.44 | 5.12
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608672 HILLTOP7 115 608686 15TH AV7 115 1 | 80 | 80 | 0.00011 | 108.56 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 107.8 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608672 HILLTOP7 115 608686 15TH AV7 115 1 | 80 | 80 | 0.00012 | 108.56 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 107.8 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 0.00016 | 101.19 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 101.01 | 0.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 0.00018 | 101.19 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 101.01 | 0.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601055 SCOTTCO3 345 997635 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01068 | 111.96 | P23:345:XEL:8M57 SCO | External | 110.5 | 1.46
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601055 SCOTTCO3 345 997635 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.0112 | 111.96 | P23:345:XEL:8M57 SCO | External | 110.5 | 1.46
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 560 | 560 | 0.00593 | 118.68 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 117.4 | 1.28
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997471 WEB AB 161 1 | 560 | 560 | 0.0071 | 118.68 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 117.4 | 1.28
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00157 | 108.99 | P23:345:XEL:8M53 SCO | External | 107.72 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00167 | 108.99 | P23:345:XEL:8M53 SCO | External | 107.72 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 104.18 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 104.02 | 0.16
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 104.18 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 104.02 | 0.16
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00497 | 101.2 | P12:500:EES:ND:8MT_OLIVE%:LAYFLD8:1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00499 | 101.2 | P12:500:EES:ND:8MT_OLIVE%:LAYFLD8:1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00054 | 123 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 122.23 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00056 | 123 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 122.23 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 126.25 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 125.19 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 126.25 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 125.19 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01063 | 135.98 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 131.33 | 4.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01117 | 135.98 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 131.33 | 4.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00439 | 128.99 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.1 | 3.89
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00469 | 128.99 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | External | 125.1 | 3.89
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00286 | 221.1 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 213.32 | 7.78
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00313 | 221.1 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 213.32 | 7.78
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06094 | 108.48 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 104.99 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06017 | 108.48 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 104.99 | 3.49
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00105 | 146.37 | 104731: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00113 | 146.37 | 104731: 533249 LEC U4 3 115 532662 LEC U4 14.4 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00208 | 102.12 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 100.6 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00214 | 102.12 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 100.6 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00052 | 156.69 | P23:345:ALTW:MITCHLCO:1150 | External | 153.87 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00056 | 156.69 | P23:345:ALTW:MITCHLCO:1150 | External | 153.87 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01623 | 151.38 | Base Case | External | 145.88 | 5.5
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01788 | 151.38 | Base Case | External | 145.88 | 5.5
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00101 | 113.92 | P23:345:ITCM:HCKRYCK:FUT2 | External | 111.35 | 2.57
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00106 | 113.92 | P23:345:ITCM:HCKRYCK:FUT2 | External | 111.35 | 2.57
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03093 | 110.3 | P55:161-345:KCPL:HAWTHORN_BUS_25:: | Internal | 107.09 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03068 | 110.3 | P55:161-345:KCPL:HAWTHORN_BUS_25:: | Internal | 107.09 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00253 | 118.5 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 117.8 | 0.7
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00257 | 118.5 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 117.8 | 0.7
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.0002 | 135.95 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 134.89 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00021 | 135.95 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 134.89 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01294 | 115.53 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.05 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01328 | 115.53 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.05 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0034 | 141.18 | Base Case | External | 139.8 | 1.38
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00357 | 141.18 | Base Case | External | 139.8 | 1.38
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00044 | 147.65 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 147.13 | 0.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00047 | 147.65 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 147.13 | 0.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00312 | 363.07 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 354.6 | 8.47
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00321 | 363.07 | P12:161:ALTW:AUTO-SINGLE:NEWHAL5:BL.PLN.5:1 | External | 354.6 | 8.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00497 | 101.2 | P12:EHV:EES::8MT_OLIVE%:LAYFLD8%:1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00499 | 101.2 | P12:EHV:EES::8MT_OLIVE%:LAYFLD8%:1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.0002 | 100.79 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 100.57 | 0.22
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.79 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 100.57 | 0.22
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00146 | 108.05 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 105 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00139 | 108.05 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 105 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00423 | 111.73 | P23:345:XEL:8M36 CNC | External | 110.92 | 0.81
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00448 | 111.73 | P23:345:XEL:8M36 CNC | External | 110.92 | 0.81
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 2e-05 | 100.17 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.2 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 1e-05 | 100.17 | 103829: 300146 4SKIAETP 138 512705 COLLINS4 138 1 300146 4SKIAETP 138 512649 SKIAEAS4 138 1 300146 4SKIAETP 138 301339 4SFORKKTP 138 1 300138 4CLEVLND 138 300996 4JAVINE 138 1 300996 4JAVINE 138 301339 4SFORKKTP 138 1 | External | 100.2 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01009 | 113.31 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 109.73 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01037 | 113.31 | P12:161:ALTW:AUTO-SINGLE:ABBOTT5:TRAER5:1 | External | 109.73 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00153 | 106.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.43 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00156 | 106.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.43 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00625 | 106.31 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 104.08 | 2.23
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00638 | 106.31 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 104.08 | 2.23
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 112 | 140 | 0.00043 | 107.56 | P12:161:DPC:AUTO-SINGLE:APLRVR5:POPLK_5:1 | External | 106.04 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 112 | 140 | 0.00046 | 107.56 | P12:161:DPC:AUTO-SINGLE:APLRVR5:POPLK_5:1 | External | 106.04 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00533 | 104.84 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00562 | 104.84 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 103.57 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.0045 | 109.04 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 106.78 | 2.26
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00475 | 109.04 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 106.78 | 2.26
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.0026 | 102.55 | P23:345:MEC:HILLS 934 | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631024 E CALMS7 115 631095 E CALMS5 161 1 | 84 | 84 | 0.00267 | 102.55 | P23:345:MEC:HILLS 934 | External | 100.41 | 2.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00497 | 101.2 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337368 8MT_OLIVE% 500 337369 6MT_OLIVE% 230 1 | 560 | 560 | 0.00499 | 101.2 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1: 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | External | 100.42 | 0.78
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00253 | 106.07 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 105.38 | 0.69
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00257 | 106.07 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 105.38 | 0.69
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 239 | 239 | 8e-05 | 111.52 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 110.7 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 239 | 239 | 0.0001 | 111.52 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 110.7 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 4e-05 | 101.12 | 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1: 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1 | External | 101.11 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 4e-05 | 101.12 | 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1: 335568 6WILLOW_GL% 230 335659 6PECUE! 230 1 | External | 101.11 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02757 | 120.96 | P23:345:MEC:GDMEC 902 | External | 117.03 | 3.93
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02819 | 120.96 | P23:345:MEC:GDMEC 902 | External | 117.03 | 3.93
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00061 | 104.21 | P23:345:ALTW:MITCHLCO:1160 | External | 102.92 | 1.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00064 | 104.21 | P23:345:ALTW:MITCHLCO:1160 | External | 102.92 | 1.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00465 | 162.12 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 154.29 | 7.83
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00476 | 162.12 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 154.29 | 7.83
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00704 | 110.93 | Base Case | External | 108.37 | 2.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00686 | 110.93 | Base Case | External | 108.37 | 2.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00351 | 110.98 | P23:345:ALTW:MITCHLCO:1160 | External | 109.25 | 1.73
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00374 | 110.98 | P23:345:ALTW:MITCHLCO:1160 | External | 109.25 | 1.73
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00132 | 127.41 | 105809: 658082 MPSSE 7 115 658084 MPSCENT7 115 1 658084 MPSCENT7 115 658086 MPSNE 7 115 1 652203 FARGO 8 69.0 657802 DELVO 8 69.0 1 652203 FARGO 8 69.0 652436 FARGO 7 115 2 652430 EGF IND7 115 657707 CALEDON7 115 1 652436 FARGO 7 115 657707 CALEDON7 115 1 657707 CALEDON7 115 997127 CALEDONIA 69.0 1 652430 EGF IND7 115 652443 GRNDFKS7 115 1 652436 FARGO 7 115 658080 MPSBROOK 115 1 652323 FARGO 9 41.8 652436 FARGO 7 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 652553 MOORHED4 230 1 652435 FARGO 4 230 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 658343 MPS NE 9 12.5 658019 MPS WIND G 0.60 1 | External | 126.65 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00139 | 127.41 | 105809: 658082 MPSSE 7 115 658084 MPSCENT7 115 1 658084 MPSCENT7 115 658086 MPSNE 7 115 1 652203 FARGO 8 69.0 657802 DELVO 8 69.0 1 652203 FARGO 8 69.0 652436 FARGO 7 115 2 652430 EGF IND7 115 657707 CALEDON7 115 1 652436 FARGO 7 115 657707 CALEDON7 115 1 657707 CALEDON7 115 997127 CALEDONIA 69.0 1 652430 EGF IND7 115 652443 GRNDFKS7 115 1 652436 FARGO 7 115 658080 MPSBROOK 115 1 652323 FARGO 9 41.8 652436 FARGO 7 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 652553 MOORHED4 230 1 652435 FARGO 4 230 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 658343 MPS NE 9 12.5 658019 MPS WIND G 0.60 1 | External | 126.65 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00023 | 104.17 | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997508 115/69 69.0 1 | 95.6 | 95.6 | 0.00024 | 104.17 | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | External | 103.78 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0113 | 164.2 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 159.37 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01187 | 164.2 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 159.37 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02757 | 120.92 | P23:345:MEC:GDMEC 901 | External | 117 | 3.92
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02819 | 120.92 | P23:345:MEC:GDMEC 901 | External | 117 | 3.92
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04846 | 108.89 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 107.07 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04904 | 108.89 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 107.07 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00467 | 160.55 | P23:345:MEC:GDMEC 902 | External | 156.32 | 4.23
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00479 | 160.55 | P23:345:MEC:GDMEC 902 | External | 156.32 | 4.23
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00136 | 128.05 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 124.46 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.0014 | 128.05 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 124.46 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.03004 | 104.17 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 103.04 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.03058 | 104.17 | P12:345:MEC:OAK GROVE-LOUISA + REACTOR | External | 103.04 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00193 | 102.21 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00186 | 102.21 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01138 | 114.98 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 113.84 | 1.14
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0117 | 114.98 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 113.84 | 1.14
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00758 | 117.71 | P23:345:XEL:8S27 WLM AS | External | 114.89 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00793 | 117.71 | P23:345:XEL:8S27 WLM AS | External | 114.89 | 2.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 218.35 | P12:161:DPC:RCE-HAR5 | External | 215.14 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 218.35 | P12:161:DPC:RCE-HAR5 | External | 215.14 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00026 | 103.11 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 102.35 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00029 | 103.11 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 102.35 | 0.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 125.89 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 124.83 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 125.89 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 124.83 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01182 | 109.51 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.4 | 1.11
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01216 | 109.51 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.4 | 1.11
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00158 | 108.64 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 107.51 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00168 | 108.64 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1 | External | 107.51 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.02215 | 106.31 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.02432 | 106.31 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00435 | 116.88 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00475 | 116.88 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 116.87 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01496 | 137.64 | P24:345:AMMO::MCCREDIE:1 | External | 135.27 | 2.37
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01428 | 137.64 | P24:345:AMMO::MCCREDIE:1 | External | 135.27 | 2.37
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00353 | 178.78 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 176.38 | 2.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00368 | 178.78 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 176.38 | 2.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00283 | 108.74 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 108.2 | 0.54
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00298 | 108.74 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 108.2 | 0.54
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00037 | 105.69 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 105.26 | 0.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00038 | 105.69 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 105.26 | 0.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00102 | 185.81 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 185.87 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00103 | 185.81 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 185.87 | -0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603110 TERMINL7 115 997649 90198-B 115 10 | 672 | 734 | 0.00017 | 113.3 | P23:345:XEL:8P33 KOL | External | 112.73 | 0.57
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603110 TERMINL7 115 997649 90198-B 115 10 | 672 | 734 | 0.00021 | 113.3 | P23:345:XEL:8P33 KOL | External | 112.73 | 0.57
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00043 | 127.64 | P23:345:AMMO::MONTGOMERY:V43 | External | 126.39 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 127.64 | P23:345:AMMO::MONTGOMERY:V43 | External | 126.39 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.0026 | 112.35 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 111.03 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00267 | 112.35 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 111.03 | 1.32
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.05834 | 122.65 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 120.47 | 2.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.05915 | 122.65 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External | 120.47 | 2.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00125 | 100.49 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External | 100.32 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00123 | 100.49 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External | 100.32 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.1675 | 113.49 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | Internal | 100.08 | 13.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.1663 | 113.49 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | Internal | 100.08 | 13.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01299 | 108.09 | P23:345:MEC:GDMEC 902 | External | 106.75 | 1.34
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631012 BL.PLN.5 161 1 | 327 | 327 | 0.01334 | 108.09 | P23:345:MEC:GDMEC 902 | External | 106.75 | 1.34
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345221 5MOBERLY 161 345409 5OVERTON 161 1 | 204 | 242 | 0.00644 | 100.95 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345221 5MOBERLY 161 345409 5OVERTON 161 1 | 204 | 242 | 0.00652 | 100.95 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 126.93 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 125.87 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 126.93 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 125.87 | 1.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00032 | 100.93 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 100.93 | 0
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00032 | 100.93 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 100.93 | 0
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00583 | 148.72 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 141.81 | 6.91
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00599 | 148.72 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External | 141.81 | 6.91
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00124 | 125.69 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 123.17 | 2.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00133 | 125.69 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 123.17 | 2.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00956 | 115.71 | P23:345:MEC:OAK GROVE 901 | External | 114.98 | 0.73
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00986 | 115.71 | P23:345:MEC:OAK GROVE 901 | External | 114.98 | 0.73
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00218 | 116.87 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 113.59 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00228 | 116.87 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 113.59 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.033 | 116.2 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03365 | 116.2 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00512 | 121.22 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 118.79 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00537 | 121.22 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 118.79 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.00092 | 103.83 | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | External | 103.62 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335642 6ESSO% 230 335664 6DELMONT 230 1 | 339 | 339 | 0.00093 | 103.83 | 67850: 335568 6WILLOW_GL% 230 335658 6WARD_CREEK 230 1 335657 6DAWSON! 230 335658 6WARD_CREEK 230 1 335618 8WILLOW_GL% 500 335837 8COLY% 500 1 | External | 103.62 | 0.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00032 | 143.05 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 142.03 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00034 | 143.05 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 142.03 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00152 | 132.83 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 130.15 | 2.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00163 | 132.83 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 130.15 | 2.68
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 104.18 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 104.02 | 0.16
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 104.18 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 104.02 | 0.16
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00145 | 111.06 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00146 | 111.06 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01124 | 138.65 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 133 | 5.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01178 | 138.65 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 133 | 5.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 112 | 140 | 0.00043 | 107.56 | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | External | 106.04 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681544 POPLK_5 161 680374 POPLK_8 69.0 1 | 112 | 140 | 0.00046 | 107.56 | 681534 APL RVR5 161 681544 POPLK_5 161 1: 681534 APL RVR5 161 681544 POPLK_5 161 1 | External | 106.04 | 1.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00401 | 122.39 | P24:345:AMMO::LABADIE:8H | External | 116.86 | 5.53
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00412 | 122.39 | P24:345:AMMO::LABADIE:8H | External | 116.86 | 5.53
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03093 | 110.3 | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 107.09 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03068 | 110.3 | 104246: 542951 HAW G5 1 22.0 541 1544 5 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 107.09 | 3.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00532 | 137.51 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 134.56 | 2.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00564 | 137.51 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External | 134.56 | 2.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01267 | 121.68 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 118.91 | 2.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01282 | 121.68 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 118.91 | 2.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00074 | 106.78 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 106.7 | 0.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00072 | 106.78 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 106.7 | 0.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00353 | 181.19 | P11:024:DPC:ALMA2:6 | External | 178.9 | 2.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00368 | 181.19 | P11:024:DPC:ALMA2:6 | External | 178.9 | 2.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00248 | 142.36 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 139.05 | 3.31
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00241 | 142.36 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 139.05 | 3.31
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00022 | 104.21 | P11:024:DPC:ALMA2:6 | External | 103.5 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00023 | 104.21 | P11:024:DPC:ALMA2:6 | External | 103.5 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07377 | 113.72 | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 107.79 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07216 | 113.72 | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 107.79 | 5.93
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603103 SCOTTCO7 115 997635 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01068 | 114.95 | P23:345:XEL:8M57 SCO | External | 113.35 | 1.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603103 SCOTTCO7 115 997635 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.0112 | 114.95 | P23:345:XEL:8M57 SCO | External | 113.35 | 1.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01053 | 184.96 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 183.01 | 1.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01163 | 184.96 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 183.01 | 1.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00449 | 120.06 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 119.67 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00441 | 120.06 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 119.67 | 0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05493 | 104.9 | P23:345:WERE:ROSE_345-50:: | Internal | 100.7 | 4.2
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05434 | 104.9 | P23:345:WERE:ROSE_345-50:: | Internal | 100.7 | 4.2
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00043 | 131.75 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 131.08 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00045 | 131.75 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 131.08 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 113.91 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 113.4 | 0.51
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 113.91 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 113.4 | 0.51
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01299 | 113.05 | P23:345:MEC:GDMEC 902 | External | 111.14 | 1.91
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01334 | 113.05 | P23:345:MEC:GDMEC 902 | External | 111.14 | 1.91
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00354 | 119.57 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 118.01 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00369 | 119.57 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 118.01 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00043 | 127.7 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 126.5 | 1.2
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 127.7 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 126.5 | 1.2
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.06832 | 114.55 | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal | 109.03 | 5.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.06701 | 114.55 | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal | 109.03 | 5.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 0.00027 | 102.39 | P13:161-69:XEL:AUTO-SINGLE:GRAVLISLE5:GRAVLISLE8:6 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 0.00028 | 102.39 | P13:161-69:XEL:AUTO-SINGLE:GRAVLISLE5:GRAVLISLE8:6 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05732 | 111.32 | 84581: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.0564 | 111.32 | 84581: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00353 | 181.19 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 178.9 | 2.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00368 | 181.19 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 178.9 | 2.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.00984 | 117.99 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 114.31 | 3.68
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01002 | 117.99 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:BL.PLN.5:1 | External | 114.31 | 3.68
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02694 | 106.91 | P23:345:MEC:LOUISA 964 | External | 106.57 | 0.34
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02802 | 106.91 | P23:345:MEC:LOUISA 964 | External | 106.57 | 0.34
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 185.8 | 220.9 | 0.00133 | 104.04 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.71 | 1.33
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 185.8 | 220.9 | 0.00141 | 104.04 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.71 | 1.33
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601024 TERMINL3 345 997649 90198-B 115 10 | 672 | 734 | 0.00017 | 111.11 | P23:345:XEL:8P33 KOL | External | 110.55 | 0.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601024 TERMINL3 345 997649 90198-B 115 10 | 672 | 734 | 0.00021 | 111.11 | P23:345:XEL:8P33 KOL | External | 110.55 | 0.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01182 | 109.51 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.4 | 1.11
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01216 | 109.51 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.4 | 1.11
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 7e-05 | 112.11 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 111.2 | 0.91
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 8e-05 | 112.11 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 111.2 | 0.91
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.1851 | 104.29 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18393 | 104.29 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01402 | 106.93 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01485 | 106.93 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 104.78 | 2.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00054 | 114.81 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 113.94 | 0.87
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00056 | 114.81 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 113.94 | 0.87
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01623 | 146.75 | Base Case | External | 142.24 | 4.51
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01788 | 146.75 | Base Case | External | 142.24 | 4.51
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 6e-05 | 111.74 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 111.34 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 6e-05 | 111.74 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 111.34 | 0.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00439 | 130.46 | P23:345:XEL:8S23 WLM | External | 126.75 | 3.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00469 | 130.46 | P23:345:XEL:8S23 WLM | External | 126.75 | 3.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.0013 | 104.23 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 103 | 1.23
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 84 | 84 | 0.00124 | 104.23 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 103 | 1.23
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00091 | 137.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.13 | 0.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00094 | 137.37 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.13 | 0.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.033 | 116.2 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03365 | 116.2 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 114.79 | 1.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.17054 | 104.71 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16897 | 104.71 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00803 | 115.93 | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External | 113.13 | 2.8
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00783 | 115.93 | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External | 113.13 | 2.8
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01623 | 112.36 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 107.37 | 4.99
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01788 | 112.36 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 107.37 | 4.99
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 9e-05 | 106.88 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 106.4 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00022 | 106.88 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 106.4 | 0.48
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00043 | 131.75 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 131.08 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00045 | 131.75 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 131.08 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.05834 | 126.12 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 124.53 | 1.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.05915 | 126.12 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External | 124.53 | 1.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 268.1 | 268.1 | 8e-05 | 105.26 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 104.55 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 268.1 | 268.1 | 9e-05 | 105.26 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 104.55 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 560 | 560 | 0.01948 | 113.27 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 109.84 | 3.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997471 WEB AB 161 1 | 560 | 560 | 0.02026 | 113.27 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 109.84 | 3.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 2e-05 | 100.17 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.2 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300929 2FAIRFAX 69.0 300139 4FAIRFAX 138 1 | 56 | 56 | 1e-05 | 100.17 | P12:138:GRDA:CLEVLND-COLLINS | External | 100.2 | -0.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 106.36 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.18 | 2.18
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01078 | 106.36 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 104.18 | 2.18
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 995 | 995 | 0.01184 | 104.6 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 102.78 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | 995 | 995 | 0.01281 | 104.6 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 102.78 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01453 | 135.01 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 131.64 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01415 | 135.01 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 131.64 | 3.37
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00043 | 127.5 | P23:345:AMMO::MONTGOMERY:V43 | External | 126.25 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 127.5 | P23:345:AMMO::MONTGOMERY:V43 | External | 126.25 | 1.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 3e-05 | 105.6 | 620327 HANKSON4 230 620363 FORMAN 4 230 1: 620327 HANKSON4 230 620363 FORMAN 4 230 1 | External | 105.59 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620263 FORMN 7 115 997492 230/115 115 1 | 112 | 132 | 4e-05 | 105.6 | 620327 HANKSON4 230 620363 FORMAN 4 230 1: 620327 HANKSON4 230 620363 FORMAN 4 230 1 | External | 105.59 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00213 | 114.64 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 115.23 | -0.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.0022 | 114.64 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 115.23 | -0.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00579 | 148.38 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 141.51 | 6.87
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00595 | 148.38 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External | 141.51 | 6.87
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.05218 | 110.14 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 107.07 | 3.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.05144 | 110.14 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 107.07 | 3.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00053 | 100.03 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00056 | 100.03 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01264 | 133.44 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 133.44 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 134.34 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 131.35 | 2.99
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00387 | 134.34 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 131.35 | 2.99
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01009 | 113.31 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 109.73 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01037 | 113.31 | 631000 ABBOTT 5 161 631083 TRAER 5 161 1: 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | External | 109.73 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00726 | 102.03 | P23:345:XEL:SPS 8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00768 | 102.03 | P23:345:XEL:SPS 8S72 HNA | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05732 | 111.32 | P23:345:WERE:STRA_345-99:: | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.0564 | 111.32 | P23:345:WERE:STRA_345-99:: | Internal | 106.24 | 5.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 6e-05 | 105.87 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 105.58 | 0.29
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 6e-05 | 105.87 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 105.58 | 0.29
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00022 | 103.76 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 103.05 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997539 161/69 69.0 1 | 70 | 70 | 0.00023 | 103.76 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 103.05 | 0.71
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.0013 | 146.59 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 143.54 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00128 | 146.59 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 143.54 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00247 | 105.49 | P23:345:GRE:PVS 19JB1 | External | 104.22 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00275 | 105.49 | P23:345:GRE:PVS 19JB1 | External | 104.22 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00037 | 113.05 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 112.53 | 0.52
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00038 | 113.05 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 112.53 | 0.52
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00536 | 103.63 | P23:345:XEL:8S50 HMP | External | 102.42 | 1.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00565 | 103.63 | P23:345:XEL:8S50 HMP | External | 102.42 | 1.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00397 | 173.77 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 171.56 | 2.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00408 | 173.77 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 171.56 | 2.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00034 | 130.93 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.76 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00034 | 130.93 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.76 | 0.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01126 | 128.8 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 125.21 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01171 | 128.8 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 125.21 | 3.59
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.0013 | 146.59 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 143.54 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00128 | 146.59 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 143.54 | 3.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00925 | 124.27 | Base Case | External | 120.12 | 4.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0097 | 124.27 | Base Case | External | 120.12 | 4.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15082 | 113.64 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 102.89 | 10.75
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14963 | 113.64 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 102.89 | 10.75
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00562 | 149.14 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 141.83 | 7.31
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00579 | 149.14 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 141.83 | 7.31
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00193 | 126.72 | Base Case | External | 125.9 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00201 | 126.72 | Base Case | External | 125.9 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 4e-05 | 100.78 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00145 | 102.22 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 | 120 | 120 | 0.00146 | 102.22 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 101.25 | 0.97
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00505 | 113.42 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00541 | 113.42 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00154 | 124.39 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 121.93 | 2.46
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.0016 | 124.39 | P12:161:ALTW:AUTO-SINGLE:LIBERTY5:HCKRYCK5:1 | External | 121.93 | 2.46
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00037 | 114.6 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 114.16 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00038 | 114.6 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 114.16 | 0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00285 | 109.73 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.18 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 2 | 500 | 500 | 0.00301 | 109.73 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 109.18 | 0.55
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00605 | 121.59 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 119.77 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997516 CHL345-115-1 115 1 | 448 | 448 | 0.00638 | 121.59 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 119.77 | 1.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.84176 | 121.59 | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03872 | 120.94 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 117.88 | 3.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997740 NASHUA11 161 11 | 650 | 715 | 0.03818 | 120.94 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 117.88 | 3.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00641 | 118.12 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 115.69 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00654 | 118.12 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 115.69 | 2.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01018 | 114 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 110.34 | 3.66
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01046 | 114 | P12:161:ITCM:ABBOTT5 - DYSART 5:IA-SW | External | 110.34 | 3.66
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 997475 DGG9T1 161 1 | 560 | 700 | 0.02877 | 108.41 | P23:345:MEC:SYCAMORE 905 | External | 105.65 | 2.76
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 997475 DGG9T1 161 1 | 560 | 700 | 0.02942 | 108.41 | P23:345:MEC:SYCAMORE 905 | External | 105.65 | 2.76
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17319 | 122.75 | P42:345:NPPD:BKR-C-3322-2 | Internal | 110.35 | 12.4
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16979 | 122.75 | P42:345:NPPD:BKR-C-3322-2 | Internal | 110.35 | 12.4
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00095 | 115.03 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 113.96 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00104 | 115.03 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 113.96 | 1.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00433 | 110.87 | P12:345:XEL:AUTO-SINGLE:COONCK3:TERMINL3:1 | External | 110.2 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00459 | 110.87 | P12:345:XEL:AUTO-SINGLE:COONCK3:TERMINL3:1 | External | 110.2 | 0.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00061 | 102.9 | P23:345:ALTW:MITCHLCO:1140 | External | 102.27 | 0.63
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00064 | 102.9 | P23:345:ALTW:MITCHLCO:1140 | External | 102.27 | 0.63
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337542 3ELD MONSNTO 115 337543 3ELDORADO.W 115 1 | 159 | 159 | 0.00042 | 100.11 | P12:115:EES-EAI:EL_EHV:ELDEST | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337542 3ELD MONSNTO 115 337543 3ELDORADO.W 115 1 | 159 | 159 | 0.00042 | 100.11 | P12:115:EES-EAI:EL_EHV:ELDEST | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.00062 | 100.1 | P23:500:EMI:ABF_MCKNT-C | External | 100.04 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 1200 | 1200 | 0.0006 | 100.1 | P23:500:EMI:ABF_MCKNT-C | External | 100.04 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00081 | 187.18 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 183.84 | 3.34
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00088 | 187.18 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 183.84 | 3.34
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00058 | 166.12 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 166.51 | -0.39
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00057 | 166.12 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 166.51 | -0.39
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00441 | 124.31 | Base Case | External | 118.96 | 5.35
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00452 | 124.31 | Base Case | External | 118.96 | 5.35
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.0017 | 104 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 103.36 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.0018 | 104 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 103.36 | 0.64
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02215 | 191.27 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 184.06 | 7.21
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02432 | 191.27 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 184.06 | 7.21
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00069 | 164.91 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 162.65 | 2.26
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00072 | 164.91 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 162.65 | 2.26
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.0013 | 106.99 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 105.86 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337338 3RIVERTON 115 337386 3RILLA! 115 1 | 106 | 106 | 0.00131 | 106.99 | 67796: 337373 3BERNICE 115 337549 3JNCTN CITY! 115 1 337371 3VIENNA_LA! 115 337373 3BERNICE 115 1 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 105.86 | 1.13
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00748 | 125 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 122.92 | 2.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00724 | 125 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 122.92 | 2.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03074 | 110.53 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 107.25 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03042 | 110.53 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 107.25 | 3.28
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.0101 | 122.18 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 118.2 | 3.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631000 ABBOTT 5 161 631083 TRAER 5 161 1 | 276 | 276 | 0.01029 | 122.18 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 118.2 | 3.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00024 | 131.97 | P13:115:XEL:COL TR5 AS- | External | 129.63 | 2.34
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997538 161/69 69.0 2 | 70 | 70 | 0.00025 | 131.97 | P13:115:XEL:COL TR5 AS- | External | 129.63 | 2.34
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00038 | 152.42 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 151.58 | 0.84
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00039 | 152.42 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 151.58 | 0.84
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00261 | 105.3 | P23:345:ITCM:HCKRYCK:FUT2 | External | 106.05 | -0.75
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00262 | 105.3 | P23:345:ITCM:HCKRYCK:FUT2 | External | 106.05 | -0.75
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00395 | 173.11 | P23:345:ALTW:MITCHLCO:1140 | External | 169.48 | 3.63
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00418 | 173.11 | P23:345:ALTW:MITCHLCO:1140 | External | 169.48 | 3.63
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00283 | 108.74 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 108.2 | 0.54
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997571 345-161 161 1 | 500 | 500 | 0.00298 | 108.74 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 108.2 | 0.54
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00395 | 176.88 | P23:345:ALTW:MITCHLCO:1160 | External | 173.3 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00418 | 176.88 | P23:345:ALTW:MITCHLCO:1160 | External | 173.3 | 3.58
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0113 | 126.31 | P23:345:MEC:GDMEC 901 | External | 120.9 | 5.41
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01177 | 126.31 | P23:345:MEC:GDMEC 901 | External | 120.9 | 5.41
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00253 | 112.16 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 111.47 | 0.69
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00257 | 112.16 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 111.47 | 0.69
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00827 | 118.18 | P23:345:AMMO::ZACHARY:2 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00841 | 118.18 | P23:345:AMMO::ZACHARY:2 | External | 113.93 | 4.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00569 | 121.26 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997676 ADAMS 3 161 9 | 300 | 334.6 | 0.00614 | 121.26 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 119.83 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00625 | 106.84 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 104.68 | 2.16
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631111 JEFF 5 161 1 | 197 | 197 | 0.00638 | 106.84 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 104.68 | 2.16
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15082 | 113.64 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 102.89 | 10.75
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14963 | 113.64 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 102.89 | 10.75
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300531 2GEORGE 69.0 300082 5GEORGE 161 1 | 56 | 56 | 0.00057 | 102.56 | 300541 2SEDALI 69 300117 5SEDALA 161 1: 300541 2SEDALI 69.0 300117 5SEDALA 161 1 | External | 102.46 | 0.1
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300531 2GEORGE 69.0 300082 5GEORGE 161 1 | 56 | 56 | 0.00054 | 102.56 | 300541 2SEDALI 69 300117 5SEDALA 161 1: 300541 2SEDALI 69.0 300117 5SEDALA 161 1 | External | 102.46 | 0.1
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.04996 | 102.78 | P23:345:MEC:LOUISA 964 | External | 101.77 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.05117 | 102.78 | P23:345:MEC:LOUISA 964 | External | 101.77 | 1.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00312 | 363.07 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 354.6 | 8.47
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00321 | 363.07 | 631009 NEWHAL5 161 631012 BL.PLN.5 161 1: 631009 NEWHAL5 161 631012 BL.PLN.5 161 1 | External | 354.6 | 8.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04846 | 129.02 | Base Case | External | 126.99 | 2.03
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04904 | 129.02 | Base Case | External | 126.99 | 2.03
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00388 | 168.96 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 167.1 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00399 | 168.96 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 167.1 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 7e-05 | 127.28 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 126.26 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 8e-05 | 127.28 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 126.26 | 1.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.0001 | 110.88 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 109.99 | 0.89
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00012 | 110.88 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 109.99 | 0.89
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00354 | 118.25 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 116.58 | 1.67
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00369 | 118.25 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 116.58 | 1.67
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00052 | 159.83 | P23:345:ALTW:MITCHLCO:1160 | External | 157.45 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00056 | 159.83 | P23:345:ALTW:MITCHLCO:1160 | External | 157.45 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01 | 140.74 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 135.91 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0105 | 140.74 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 135.91 | 4.83
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 112 | 112 | 0.00071 | 125.86 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 123.77 | 2.09
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 112 | 112 | 0.00075 | 125.86 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External | 123.77 | 2.09
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02859 | 116.48 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 115.31 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02996 | 116.48 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1 | External | 115.31 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01184 | 118.12 | P23:345:MEC:GDMEC 902 | External | 112.52 | 5.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01233 | 118.12 | P23:345:MEC:GDMEC 902 | External | 112.52 | 5.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.72 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.72 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00026 | 102.27 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 101.55 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997511 230/115 115 1 | 187 | 187 | 0.00029 | 102.27 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 101.55 | 0.72
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00465 | 167.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 162.98 | 4.26
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00476 | 167.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 162.98 | 4.26
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.0001 | 102.8 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1 | External | 102.2 | 0.6
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00014 | 102.8 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1 | External | 102.2 | 0.6
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01179 | 107.42 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.34 | 1.08
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01212 | 107.42 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.34 | 1.08
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.0001 | 111.85 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 110.95 | 0.9
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00012 | 111.85 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 110.95 | 0.9
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.0005 | 115.89 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 114.33 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00053 | 115.89 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 114.33 | 1.56
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00249 | 111.4 | P23:345:GRE:PVS 19JB4 | External | 109.55 | 1.85
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 2 | 500 | 500 | 0.00276 | 111.4 | P23:345:GRE:PVS 19JB4 | External | 109.55 | 1.85
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00423 | 111.44 | P23:345:XEL:8M35 CNC | External | 110.62 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00448 | 111.44 | P23:345:XEL:8M35 CNC | External | 110.62 | 0.82
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00388 | 168.96 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 167.1 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00399 | 168.96 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 167.1 | 1.86
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00212 | 114.4 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 115.05 | -0.65
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00219 | 114.4 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 115.05 | -0.65
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00766 | 103.73 | P24:345:AMMO::MCCREDIE:1 | External | 101.16 | 2.57
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00788 | 103.73 | P24:345:AMMO::MCCREDIE:1 | External | 101.16 | 2.57
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00554 | 151.13 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 144.13 | 7
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00569 | 151.13 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External | 144.13 | 7
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18509 | 104.27 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18392 | 104.27 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00271 | 111.58 | P23:345:MEC:OAK GROVE 901 | External | 109.33 | 2.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 633261 KPECKTP5 161 636673 SB 112 5 161 1 | 180 | 180 | 0.00273 | 111.58 | P23:345:MEC:OAK GROVE 901 | External | 109.33 | 2.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.00627 | 110.5 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 107.54 | 2.96
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631106 HENRYCO5 161 631108 DENMARK5 161 1 | 169 | 169 | 0.0064 | 110.5 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 107.54 | 2.96
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 120.98 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 120.98 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 120.91 | 0.07
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00066 | 119.86 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 119.09 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.0007 | 119.86 | P12:161:ALTW-DPC:AUTO-SINGLE:LANSINGL15:GENOA5:1 | External | 119.09 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 263.7 | 263.7 | 0.00104 | 103.36 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.36 | 1
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 263.7 | 263.7 | 0.0011 | 103.36 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.36 | 1
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17191 | 123.68 | P42:345:NPPD:BKR-CPR-3322 | Internal | 111.51 | 12.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16808 | 123.68 | P42:345:NPPD:BKR-CPR-3322 | Internal | 111.51 | 12.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00505 | 113.42 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00541 | 113.42 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 112.12 | 1.3
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00611 | 135.19 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 128.15 | 7.04
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00632 | 135.19 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 128.15 | 7.04
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03872 | 121.61 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 118.14 | 3.47
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997740 NASHUA11 161 11 | 650 | 715 | 0.03818 | 121.61 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 118.14 | 3.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03029 | 116.64 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal | 110.17 | 6.47
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01254 | 145.44 | P23:345:MEC:GDMEC 902 | External | 138.99 | 6.45
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01306 | 145.44 | P23:345:MEC:GDMEC 902 | External | 138.99 | 6.45
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.0115 | 100.82 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01171 | 100.82 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17193 | 123.32 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 111.15 | 12.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16812 | 123.32 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 111.15 | 12.17
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 120.62 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 120.62 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.56 | 0.06
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00641 | 117.62 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 115.24 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00654 | 117.62 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 115.24 | 2.38
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 128.03 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 128.02 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 128.03 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 128.02 | 0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00061 | 103.69 | P23:345:ALTW:MITCHLCO:1150 | External | 102.24 | 1.45
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00064 | 103.69 | P23:345:ALTW:MITCHLCO:1150 | External | 102.24 | 1.45
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00145 | 111.06 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00146 | 111.06 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 110.29 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00121 | 151.67 | P23:345:MEC:GDMEC 902 | External | 150.62 | 1.05
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631012 BL.PLN.5 161 629102 BELLE PLN 8 69.0 1 | 36 | 36 | 0.00123 | 151.67 | P23:345:MEC:GDMEC 902 | External | 150.62 | 1.05
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00246 | 141.98 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 138.73 | 3.25
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00239 | 141.98 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 138.73 | 3.25
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00731 | 111.14 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 108.19 | 2.95
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00763 | 111.14 | 631199 KILLDEER3 345 631206 QUINN3 345 1: 631199 KILLDEER3 345 631206 QUINN3 345 1 | External | 108.19 | 2.95
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00071 | 130.83 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 129.56 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00075 | 130.83 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 129.56 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00467 | 160.56 | P23:345:MEC:GDMEC 901 | External | 156.32 | 4.24
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00479 | 160.56 | P23:345:MEC:GDMEC 901 | External | 156.32 | 4.24
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00013 | 144.99 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 144.01 | 0.98
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00015 | 144.99 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 144.01 | 0.98
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01229 | 108.24 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 102.88 | 5.36
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01272 | 108.24 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 102.88 | 5.36
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03602 | 104.22 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN20 161 20 | 500 | 550 | 0.03575 | 104.22 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03293 | 108.56 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.44 | 5.12
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997745 HAWTHORN22 161 22 | 550 | 605 | 0.03249 | 108.56 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.44 | 5.12
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 0.00027 | 102.39 | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 6: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 5 | 70 | 80.5 | 0.00028 | 102.39 | 605603 GRAVL ISLE 8 69 602044 GRAVL ISLE 5 161 6: 605603 GRAVL ISLE 8 69.0 602044 GRAVL ISLE 5 161 6 | External | 101.24 | 1.15
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.72 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.72 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 104.73 | -0.01
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00255 | 100.1 | P23:345:ITCM:HCKRYCK:FUT2 | External | 100.98 | -0.88
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00255 | 100.1 | P23:345:ITCM:HCKRYCK:FUT2 | External | 100.98 | -0.88
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02859 | 116.48 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 115.31 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 1195 | 1195 | 0.02996 | 116.48 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1: 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | External | 115.31 | 1.17
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14487 | 137.47 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 157.21 | -19.74
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01264 | 133.44 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 133.44 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 133.88 | -0.44
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00249 | 122.31 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 117.58 | 4.73
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 630027 TRAER 8 69.0 1 | 84 | 84 | 0.00251 | 122.31 | P12:161:ALTW:AUTO-SINGLE:TRAER5:DYSART5:1 | External | 117.58 | 4.73
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.0002 | 100.79 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 100.57 | 0.22
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00021 | 100.79 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 100.57 | 0.22
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 114.9 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 114.88 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 114.9 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 114.88 | 0.02
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00426 | 117.91 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 116.64 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00407 | 117.91 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 116.64 | 1.27
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00133 | 105.98 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 104.55 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.0014 | 105.98 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 104.55 | 1.43
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.03911 | 113.93 | P23:345:MEC:LOUISA 924 | External | 112.58 | 1.35
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 1189 | 1189 | 0.04003 | 113.93 | P23:345:MEC:LOUISA 924 | External | 112.58 | 1.35
Thermal | 00NR | S2 | 29SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00026 | 102.78 | P12:230:XEL:AUTO-SINGLE:BLUELK4:HUC-MCLEOD4:1 | External | 102.01 | 0.77
Thermal | 00NR | S2 | 29SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997511 230/115 115 1 | 187 | 187 | 0.00029 | 102.78 | P12:230:XEL:AUTO-SINGLE:BLUELK4:HUC-MCLEOD4:1 | External | 102.01 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00518 | 119.91 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 116.89 | 3.02
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00544 | 119.91 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 116.89 | 3.02
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08772 | 111.77 | Base Case | External | 108.16 | 3.61
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08953 | 111.77 | Base Case | External | 108.16 | 3.61
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06555 | 103.4 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 100.91 | 2.49
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06746 | 103.4 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External | 100.91 | 2.49
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00093 | 137.17 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.16 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00094 | 137.17 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.16 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 103.13 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 103.13 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04975 | 103.03 | 104268: 532780 CANEYRV7 345 532781 CANEYWF7 345 1 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | Internal | 100.13 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04902 | 103.03 | 104268: 532780 CANEYRV7 345 532781 CANEYWF7 345 1 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | Internal | 100.13 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01044 | 162.61 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01089 | 162.61 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16146 | 122.28 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.41 | 12.87
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16026 | 122.28 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.41 | 12.87
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1195 | 1195 | 0.16417 | 108.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1195 | 1195 | 0.16279 | 108.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 345408 7OVERTON 345 345409 5OVERTON 161 1 | 560 | 560 | 0.01168 | 103.89 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 105.73 | -1.84
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345408 7OVERTON 345 345409 5OVERTON 161 1 | 560 | 560 | 0.01032 | 103.89 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1: 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | External | 105.73 | -1.84
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00023 | 120.98 | P13:115:XEL:COL TR5 AS- | External | 119.77 | 1.21
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00024 | 120.98 | P13:115:XEL:COL TR5 AS- | External | 119.77 | 1.21
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.10022 | 102.38 | P12:345:WERE:STRA-IATAN_345_1:: | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09998 | 102.38 | P12:345:WERE:STRA-IATAN_345_1:: | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.0015 | 113.73 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 111.89 | 1.84
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00158 | 113.73 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 111.89 | 1.84
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10154 | 103.48 | P12:345:WERE:STRA-IATAN_345_2::FUTURE | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10129 | 103.48 | P12:345:WERE:STRA-IATAN_345_2::FUTURE | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 1e-05 | 237.09 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 237.25 | -0.16
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00053 | 105.06 | Base Case | External | 104.42 | 0.64
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00055 | 105.06 | Base Case | External | 104.42 | 0.64
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01313 | 103.58 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01395 | 103.58 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08331 | 104.05 | P23:345:MEC:NORWALK 901 | External | 101.25 | 2.8
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08498 | 104.05 | P23:345:MEC:NORWALK 901 | External | 101.25 | 2.8
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00516 | 102.2 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00545 | 102.2 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00582 | 119.72 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 112.91 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00603 | 119.72 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 112.91 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00056 | 101.35 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 101.19 | 0.16
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00057 | 101.35 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 101.19 | 0.16
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00773 | 103 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00809 | 103 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00967 | 106.36 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 100.33 | 6.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01017 | 106.36 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 100.33 | 6.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00766 | 126.87 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 125.56 | 1.31
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00738 | 126.87 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 125.56 | 1.31
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.0003 | 108.75 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 108.1 | 0.65
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.00031 | 108.75 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 108.1 | 0.65
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 4e-05 | 107.19 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 106.44 | 0.75
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00017 | 107.19 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 106.44 | 0.75
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00518 | 119.91 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 116.89 | 3.02
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00544 | 119.91 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 116.89 | 3.02
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00337 | 119.65 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 112.84 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00342 | 119.65 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 112.84 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00076 | 116.86 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 114.23 | 2.63
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.0008 | 116.86 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 114.23 | 2.63
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00026 | 114.24 | Base Case | External | 112.04 | 2.2
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00028 | 114.24 | Base Case | External | 112.04 | 2.2
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00889 | 101.44 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00944 | 101.44 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01155 | 137.46 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01224 | 137.46 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00053 | 101.33 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00055 | 101.33 | P23:345:XEL:8N22 SHC | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00345 | 117.32 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 118.2 | -0.88
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00353 | 117.32 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 118.2 | -0.88
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00137 | 121.77 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 118.33 | 3.44
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00148 | 121.77 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 118.33 | 3.44
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09969 | 100.97 | P23:345:WERE:STRA_345-98:: | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09944 | 100.97 | P23:345:WERE:STRA_345-98:: | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21417 | 105.24 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal | 103.33 | 1.91
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05718 | 112.46 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 108.84 | 3.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.0564 | 112.46 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 108.84 | 3.62
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.17897 | 101.85 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.17781 | 101.85 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00094 | 139.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.78 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00096 | 139.79 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.78 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00094 | 117.28 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 112.42 | 4.86
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00098 | 117.28 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 112.42 | 4.86
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82943 | 111.93 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16142 | 122.31 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.45 | 12.86
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16022 | 122.31 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.45 | 12.86
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01039 | 112.63 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 112.01 | 0.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01038 | 112.63 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 112.01 | 0.62
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01167 | 108.62 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 107.85 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01202 | 108.62 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 107.85 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10209 | 110.25 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal | 103.22 | 7.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.1018 | 110.25 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal | 103.22 | 7.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00755 | 126.16 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 124.36 | 1.8
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00728 | 126.16 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | External | 124.36 | 1.8
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00373 | 118.49 | Base Case | External | 116.74 | 1.75
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00389 | 118.49 | Base Case | External | 116.74 | 1.75
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00137 | 102.6 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 102.12 | 0.48
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.0013 | 102.6 | 300034 5EDMONS 161 300555 5GRAVOI 161 1: 300034 5EDMONS 161 300555 5GRAVOI 161 1 | External | 102.12 | 0.48
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00064 | 105.45 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 102.22 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00068 | 105.45 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 102.22 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 0.00012 | 103.14 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 103.48 | -0.34
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 96 | 96 | 6e-05 | 103.14 | 300045 7MORGAN 345 300949 7JASPER 345 1: 300045 7MORGAN 345 300949 7JASPER 345 1 | External | 103.48 | -0.34
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 1e-05 | 237.09 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 237.25 | -0.16
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00029 | 108.67 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 110.07 | -1.4
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00028 | 108.67 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 110.07 | -1.4
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620263 FORMN 7 115 997493 230/115 115 1 | 112 | 140 | 0.00098 | 110.62 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620263 FORMN 7 115 997493 230/115 115 1 | 112 | 140 | 0.00102 | 110.62 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00031 | 141.32 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 139.85 | 1.47
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00033 | 141.32 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 139.85 | 1.47
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00784 | 117.05 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | External | 115.95 | 1.1
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00765 | 117.05 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | External | 115.95 | 1.1
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00035 | 108.24 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 105.83 | 2.41
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00037 | 108.24 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 105.83 | 2.41
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00352 | 106.86 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 107.61 | -0.75
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.0036 | 106.86 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 107.61 | -0.75
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06555 | 103.4 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 100.91 | 2.49
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06746 | 103.4 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External | 100.91 | 2.49
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21466 | 105.17 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | Internal | 102.99 | 2.18
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00094 | 117.28 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 112.42 | 4.86
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00098 | 117.28 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 112.42 | 4.86
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0323 | 108.16 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 105.32 | 2.84
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03202 | 108.16 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 105.32 | 2.84
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05981 | 106.9 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 103.55 | 3.35
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05914 | 106.9 | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | Internal | 103.55 | 3.35
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01036 | 128.98 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01088 | 128.98 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.07517 | 111.02 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 146.16 | -35.14
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00114 | 102.13 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | External | 101.58 | 0.55
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.0012 | 102.13 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | External | 101.58 | 0.55
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00337 | 119.65 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 112.84 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00342 | 119.65 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 112.84 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01039 | 108.46 | Base Case | External | 107.42 | 1.04
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01038 | 108.46 | Base Case | External | 107.42 | 1.04
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 239 | 239 | 0.00303 | 100.14 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603067 CHEMOLT7 115 603069 COTTAGE7 115 1 | 239 | 239 | 0.00315 | 100.14 | 601023 REDROCK3 345 601075 BAILEY RD3 345 1: 601023 REDROCK3 345 601075 BAILEY RD3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06595 | 104.02 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06787 | 104.02 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00278 | 168.29 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 163.05 | 5.24
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00306 | 168.29 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 163.05 | 5.24
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 292.2 | 292.2 | 0.00184 | 102.17 | P23:345:XEL:8P33 KOL | External | 100.62 | 1.55
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 292.2 | 292.2 | 0.00194 | 102.17 | P23:345:XEL:8P33 KOL | External | 100.62 | 1.55
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00044 | 102.22 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 100.26 | 1.96
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00048 | 102.22 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 100.26 | 1.96
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 179.63 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 175.06 | 4.57
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 179.63 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 175.06 | 4.57
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00582 | 119.72 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 112.91 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00603 | 119.72 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 112.91 | 6.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10209 | 110.25 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal | 103.22 | 7.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.1018 | 110.25 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal | 103.22 | 7.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00583 | 103.93 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.2 | 2.73
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00617 | 103.93 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.2 | 2.73
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.04826 | 101.37 | Base Case | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.04731 | 101.37 | Base Case | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00398 | 115.39 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 110.36 | 5.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.0041 | 115.39 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 110.36 | 5.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07113 | 119.24 | P23:345:MEC:GRIMES 901 | External | 116.52 | 2.72
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.0731 | 119.24 | P23:345:MEC:GRIMES 901 | External | 116.52 | 2.72
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05282 | 100.21 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05202 | 100.21 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0323 | 105.59 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 102.42 | 3.17
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03202 | 105.59 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 102.42 | 3.17
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.01584 | 108.66 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 103.89 | 4.77
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.0175 | 108.66 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 103.89 | 4.77
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02164 | 160.25 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 156.31 | 3.94
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02381 | 160.25 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 156.31 | 3.94
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00243 | 130.02 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 127.48 | 2.54
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00237 | 130.02 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 127.48 | 2.54
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01044 | 162.61 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01089 | 162.61 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00186 | 130.44 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 130.09 | 0.35
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00195 | 130.44 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 130.09 | 0.35
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 640066 AXTELL 7 115 997459 AXTELL T1 115 1 | 336 | 336 | 0.03992 | 102.87 | P42:345:NPPD:BKR-AXT-3308 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 640066 AXTELL 7 115 997459 AXTELL T1 115 1 | 336 | 336 | 0.03891 | 102.87 | P42:345:NPPD:BKR-AXT-3308 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01036 | 128.98 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01088 | 128.98 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 335 | 335 | 0.00678 | 100.08 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 335 | 335 | 0.0071 | 100.08 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00029 | 107.95 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 109.36 | -1.41
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00028 | 107.95 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 109.36 | -1.41
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01036 | 128.98 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 335 | 335 | 0.01088 | 128.98 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 123.17 | 5.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.001 | 101.4 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.0011 | 101.4 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01172 | 110.17 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 109.38 | 0.79
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01207 | 110.17 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 109.38 | 0.79
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.001 | 104.31 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 100.84 | 3.47
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.0011 | 104.31 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 100.84 | 3.47
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00914 | 102.75 | P12:161:XEL:ECL-WHT | External | 101.33 | 1.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00969 | 102.75 | P12:161:XEL:ECL-WHT | External | 101.33 | 1.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00875 | 110.86 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00938 | 110.86 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00101 | 101.93 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.0011 | 101.93 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00458 | 110.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 109.71 | 1.18
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00574 | 110.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 109.71 | 1.18
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.0301 | 141.41 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.46 | 6.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.03113 | 141.41 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 134.46 | 6.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.0003 | 138.52 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 137.08 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00032 | 138.52 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 137.08 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00398 | 115.85 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 110.68 | 5.17
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.0041 | 115.85 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 110.68 | 5.17
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.0187 | 103.17 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.01947 | 103.17 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00369 | 105.77 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 103.18 | 2.59
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00368 | 105.77 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 103.18 | 2.59
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00875 | 110.86 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00938 | 110.86 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00066 | 138.5 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 136.53 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00069 | 138.5 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 136.53 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00029 | 116.65 | 71561: 615477 GRE-SPRGCK15 161 615478 GRE-SPRGCK25 161 Z 615478 GRE-SPRGCK25 161 616900 GRE-RAVENNA5 161 1 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 602001 PR ISLD5 161 616900 GRE-RAVENNA5 161 1 | External | 115.7 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00031 | 116.65 | 71561: 615477 GRE-SPRGCK15 161 615478 GRE-SPRGCK25 161 Z 615478 GRE-SPRGCK25 161 616900 GRE-RAVENNA5 161 1 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 602001 PR ISLD5 161 616900 GRE-RAVENNA5 161 1 | External | 115.7 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04975 | 103.19 | P23:345:WERE:LATH_BKRS:: | Internal | 100.29 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04902 | 103.19 | P23:345:WERE:LATH_BKRS:: | Internal | 100.29 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08772 | 103.32 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 100.58 | 2.74
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08953 | 103.32 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 100.58 | 2.74
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00031 | 141.32 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 139.85 | 1.47
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00033 | 141.32 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 139.85 | 1.47
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00583 | 103.82 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.23 | 2.59
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00617 | 103.82 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External | 101.23 | 2.59
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0482 | 123.3 | Base Case | External | 121.29 | 2.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04878 | 123.3 | Base Case | External | 121.29 | 2.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00083 | 205.38 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 199.97 | 5.41
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 205.38 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 199.97 | 5.41
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03299 | 126.69 | 104144: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03244 | 126.69 | 104144: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00369 | 115.14 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 112.93 | 2.21
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00368 | 115.14 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 112.93 | 2.21
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00067 | 130.77 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 128.35 | 2.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00069 | 130.77 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 128.35 | 2.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01044 | 162.61 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01089 | 162.61 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 157.19 | 5.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01313 | 103.58 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01395 | 103.58 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.0001 | 114.32 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.31 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.0001 | 114.32 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.31 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00378 | 104.58 | P11:024:DPC:ALMA2:6 | External | 103.22 | 1.36
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00394 | 104.58 | P11:024:DPC:ALMA2:6 | External | 103.22 | 1.36
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00574 | 100.25 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00592 | 100.25 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03299 | 126.69 | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03244 | 126.69 | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00398 | 115.85 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 110.68 | 5.17
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.0041 | 115.85 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 110.68 | 5.17
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04975 | 103.19 | 104278: 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532800 LATHAMS7 345 532801 ELKRVR17 345 1 | Internal | 100.29 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.04902 | 103.19 | 104278: 532780 CANEYRV7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532800 LATHAMS7 345 532801 ELKRVR17 345 1 | Internal | 100.29 | 2.9
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 25 | 31 | 0.00026 | 113.11 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.75 | 0.36
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 25 | 31 | 0.00026 | 113.11 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 112.75 | 0.36
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 117.33 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.34 | -0.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 117.33 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.34 | -0.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02164 | 160.25 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 156.31 | 3.94
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02381 | 160.25 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 156.31 | 3.94
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00188 | 105.98 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00193 | 105.98 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00574 | 100.25 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00592 | 100.25 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00689 | 114.78 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 114.73 | 0.05
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0067 | 114.78 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 114.73 | 0.05
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.00068 | 107.66 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 120 | 120 | 0.0007 | 107.66 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00032 | 107.77 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 106.82 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00033 | 107.77 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 106.82 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.0301 | 137.74 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 129.38 | 8.36
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.03113 | 137.74 | 92723: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645011 NEBCTY1G 18.0 1 645458 S3458 3 345 645012 NEBCTY2G 23.0 1 | External | 129.38 | 8.36
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00145 | 105.47 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.22 | 0.25
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00147 | 105.47 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.22 | 0.25
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00068 | 121.96 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.0007 | 121.96 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00063 | 100.47 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00068 | 100.47 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00101 | 221.32 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 215.5 | 5.82
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00107 | 221.32 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 215.5 | 5.82
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00088 | 100.99 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0009 | 100.99 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00132 | 121.16 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 116.81 | 4.35
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00136 | 121.16 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External | 116.81 | 4.35
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00021 | 101.62 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 100.72 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00022 | 101.62 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 100.72 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00035 | 108.24 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 105.83 | 2.41
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00037 | 108.24 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 105.83 | 2.41
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00059 | 103.91 | P23:345:MEC:LOUISA 954 | External | 102.51 | 1.4
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00061 | 103.91 | P23:345:MEC:LOUISA 954 | External | 102.51 | 1.4
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00053 | 101.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00055 | 101.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00029 | 107.24 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 108.64 | -1.4
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00028 | 107.24 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 108.64 | -1.4
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00101 | 105.03 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.0011 | 105.03 | 300002 1THLG2 22 300132 5THMHLB2 161 1: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00278 | 173.12 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 167.36 | 5.76
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00306 | 173.12 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 167.36 | 5.76
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05417 | 117.96 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 114.82 | 3.14
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.0534 | 117.96 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 114.82 | 3.14
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00889 | 101.44 | P11:024:DPC:ALMA2:6 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00944 | 101.44 | P11:024:DPC:ALMA2:6 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.01584 | 125.62 | Base Case | External | 121.15 | 4.47
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.0175 | 125.62 | Base Case | External | 121.15 | 4.47
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00208 | 106.33 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 103.44 | 2.89
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00219 | 106.33 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 103.44 | 2.89
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.16141 | 101.32 | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | Internal | 107.29 | -5.97
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00332 | 144.67 | Base Case | External | 141.05 | 3.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.0035 | 144.67 | Base Case | External | 141.05 | 3.62
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00035 | 106.42 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 104.08 | 2.34
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620233 EDGETAP7 115 620234 PEL RPD7 115 1 | 80 | 88 | 0.00037 | 106.42 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 104.08 | 2.34
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00083 | 101.15 | 344004 5ADAIR1 161 346005 2ADAIR 1 69 1: 344004 5ADAIR1 161 346005 2ADAIR 1 69.0 1 | External | 100.68 | 0.47
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00088 | 101.15 | 344004 5ADAIR1 161 346005 2ADAIR 1 69 1: 344004 5ADAIR1 161 346005 2ADAIR 1 69.0 1 | External | 100.68 | 0.47
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00755 | 126.16 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 124.36 | 1.8
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00728 | 126.16 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External | 124.36 | 1.8
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.0003 | 138.52 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 137.08 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00032 | 138.52 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 137.08 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 92 | 92 | 0.0003 | 101.67 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.49 | 1.18
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 92 | 92 | 0.00032 | 101.67 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.49 | 1.18
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00145 | 107.6 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.34 | 0.26
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00147 | 107.6 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.34 | 0.26
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00516 | 102.2 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00545 | 102.2 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00516 | 102.2 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00545 | 102.2 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00352 | 106.86 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 107.61 | -0.75
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.0036 | 106.86 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 107.61 | -0.75
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00438 | 106.94 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 104.32 | 2.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00463 | 106.94 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 104.32 | 2.62
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08357 | 105.43 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 102.48 | 2.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08528 | 105.43 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 102.48 | 2.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00689 | 111.69 | Base Case | External | 110.8 | 0.89
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.0067 | 111.69 | Base Case | External | 110.8 | 0.89
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03261 | 109.54 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 106.63 | 2.91
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03234 | 109.54 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 106.63 | 2.91
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.22215 | 106.57 | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | Internal | 104.22 | 2.35
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01084 | 121.89 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 115.2 | 6.69
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.0114 | 121.89 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 115.2 | 6.69
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00806 | 122.34 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 121 | 1.34
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00818 | 122.34 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 121 | 1.34
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0482 | 101.55 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 100.64 | 0.91
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04878 | 101.55 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 100.64 | 0.91
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03261 | 109.54 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 106.63 | 2.91
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03234 | 109.54 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 106.63 | 2.91
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00132 | 121.16 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 116.81 | 4.35
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00136 | 121.16 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External | 116.81 | 4.35
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01172 | 110.17 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 109.38 | 0.79
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01207 | 110.17 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 109.38 | 0.79
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00083 | 219.26 | P12:161:DPC:RCE-HAR5 | External | 212.31 | 6.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 219.26 | P12:161:DPC:RCE-HAR5 | External | 212.31 | 6.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02164 | 124.21 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 117.75 | 6.46
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02381 | 124.21 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 117.75 | 6.46
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05021 | 105.55 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 102.76 | 2.79
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04964 | 105.55 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 102.76 | 2.79
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00458 | 110.75 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 109.72 | 1.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00574 | 110.75 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 109.72 | 1.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 179.63 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 175.06 | 4.57
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 179.63 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 175.06 | 4.57
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00278 | 153.28 | 300097 5MARYVL 161 300104 5NODWAY 161 1: 300097 5MARYVL 161 300104 5NODWAY 161 1 | External | 147.01 | 6.27
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00306 | 153.28 | 300097 5MARYVL 161 300104 5NODWAY 161 1: 300097 5MARYVL 161 300104 5NODWAY 161 1 | External | 147.01 | 6.27
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00029 | 107.96 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.35 | -1.39
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00028 | 107.96 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.35 | -1.39
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00398 | 108.28 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 106.1 | 2.18
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.0041 | 108.28 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 106.1 | 2.18
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 640065 AXTELL 3 345 997459 AXTELL T1 115 1 | 336 | 336 | 0.03992 | 107.02 | P42:345:NPPD:BKR-AXT-3308 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 640065 AXTELL 3 345 997459 AXTELL T1 115 1 | 336 | 336 | 0.03891 | 107.02 | P42:345:NPPD:BKR-AXT-3308 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00345 | 117.32 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 118.2 | -0.88
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00353 | 117.32 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 118.2 | -0.88
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00112 | 115.08 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 111.76 | 3.32
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00121 | 115.08 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 111.76 | 3.32
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00208 | 106.33 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 103.44 | 2.89
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00219 | 106.33 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 103.44 | 2.89
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00737 | 123.79 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 120.83 | 2.96
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00804 | 123.79 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 120.83 | 2.96
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00326 | 103.91 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 104.43 | -0.52
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00333 | 103.91 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 104.43 | -0.52
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03261 | 106.94 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 103.71 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03234 | 106.94 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 103.71 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00137 | 121.77 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 118.33 | 3.44
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00148 | 121.77 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 118.33 | 3.44
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 143 | 157.3 | 0.0003 | 100.18 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 143 | 157.3 | 0.00032 | 100.18 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.0042 | 115.33 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 115.67 | -0.34
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00402 | 115.33 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 115.67 | -0.34
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 103.13 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 103.13 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01097 | 104.49 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01151 | 104.49 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.01584 | 108.76 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.97 | 4.79
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.0175 | 108.76 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.97 | 4.79
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.04425 | 101.05 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.04348 | 101.05 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00049 | 115.22 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 112.96 | 2.26
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00052 | 115.22 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 112.96 | 2.26
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16142 | 122.31 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.45 | 12.86
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.16022 | 122.31 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 109.45 | 12.86
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00373 | 143.81 | P11:024:DPC:ALMA2:6 | External | 141.52 | 2.29
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00389 | 143.81 | P11:024:DPC:ALMA2:6 | External | 141.52 | 2.29
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00243 | 130.02 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 127.48 | 2.54
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00237 | 130.02 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 127.48 | 2.54
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.0004 | 125.05 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 124.28 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00043 | 125.05 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 124.28 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00378 | 104.58 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 103.22 | 1.36
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00394 | 104.58 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 103.22 | 1.36
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00373 | 143.81 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 141.52 | 2.29
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00389 | 143.81 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 141.52 | 2.29
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06595 | 104.02 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06787 | 104.02 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 189 | 220.9 | 0.00119 | 110.68 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 108.87 | 1.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 189 | 220.9 | 0.00126 | 110.68 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 108.87 | 1.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 109.26 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 109.09 | 0.17
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 109.26 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 109.09 | 0.17
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01216 | 114.37 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 113.14 | 1.23
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01253 | 114.37 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 113.14 | 1.23
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00458 | 129.76 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 127.67 | 2.09
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00574 | 129.76 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 127.67 | 2.09
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01313 | 103.58 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01395 | 103.58 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.01584 | 128.66 | Base Case | External | 125.52 | 3.14
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.0175 | 128.66 | Base Case | External | 125.52 | 3.14
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.00137 | 105.48 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 104.85 | 0.63
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 301401 2TURKEYCRK 69.0 301370 5TURKEYCRK 161 1 | 96 | 96 | 0.0013 | 105.48 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1: 300034 5EDMONS 161 301402 5LOSTVALY 161 1 | External | 104.85 | 0.63
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00088 | 143.45 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.37 | 0.08
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00091 | 143.45 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.37 | 0.08
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00784 | 117.05 | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External | 115.95 | 1.1
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00765 | 117.05 | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External | 115.95 | 1.1
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 4e-05 | 107.19 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 106.44 | 0.75
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00017 | 107.19 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 106.44 | 0.75
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.0004 | 125.05 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 124.28 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00043 | 125.05 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 124.28 | 0.77
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06595 | 104.02 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06787 | 104.02 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External | 101.52 | 2.5
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00773 | 103 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00809 | 103 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.8395 | 101.58 | 82345: 646298 S1298 5 161 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00145 | 100.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.4 | 0.26
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00147 | 100.66 | P23:500:EES-EAI:WH_BLF:B7914 | External | 100.4 | 0.26
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04531 | 119.23 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 116.42 | 2.81
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04458 | 119.23 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 116.42 | 2.81
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00044 | 102.22 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 100.26 | 1.96
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630189 RICE 8 69.0 613330 RICE 5 161 1 | 96 | 106 | 0.00048 | 102.22 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 100.26 | 1.96
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01155 | 137.46 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01224 | 137.46 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00369 | 121.89 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 119.85 | 2.04
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00368 | 121.89 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 119.85 | 2.04
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00458 | 129.84 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 127.87 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00574 | 129.84 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 127.87 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00373 | 141.95 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 139.58 | 2.37
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00389 | 141.95 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 139.58 | 2.37
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00126 | 143.31 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.91 | 2.4
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00124 | 143.31 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.91 | 2.4
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00032 | 107.77 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 106.82 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00033 | 107.77 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 106.82 | 0.95
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00398 | 108.18 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 105.94 | 2.24
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.0041 | 108.18 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 105.94 | 2.24
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00029 | 130.27 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.06 | 0.21
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00029 | 130.27 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.06 | 0.21
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00806 | 105.08 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 104.97 | 0.11
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00818 | 105.08 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 104.97 | 0.11
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08493 | 104.74 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 101.82 | 2.92
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08668 | 104.74 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 101.82 | 2.92
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00126 | 143.31 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.91 | 2.4
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00124 | 143.31 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.91 | 2.4
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00893 | 102.2 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00937 | 102.2 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.0009 | 117.07 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 112.2 | 4.87
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00095 | 117.07 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 112.2 | 4.87
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00538 | 101.96 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 335 | 335 | 0.00555 | 101.96 | P12:161:ITCM:DENMARK5-VIELE5:IA-SE | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00186 | 133.76 | Base Case | External | 131.74 | 2.02
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00195 | 133.76 | Base Case | External | 131.74 | 2.02
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02164 | 162.14 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 155.52 | 6.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02381 | 162.14 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 155.52 | 6.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.84127 | 128.97 | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 107.68 | Base Case | External | 107.72 | -0.04
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 107.68 | Base Case | External | 107.72 | -0.04
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00053 | 100.11 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00056 | 100.11 | Base Case | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.0001 | 114.48 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.47 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 114.48 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 114.47 | 0.01
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01216 | 114.37 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 113.14 | 1.23
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01253 | 114.37 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 113.14 | 1.23
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00021 | 101.2 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 100.3 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00022 | 101.2 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 100.3 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03261 | 106.94 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 103.71 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03234 | 106.94 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 103.71 | 3.23
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 1e-05 | 237.09 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 237.25 | -0.16
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.00079 | 139.51 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 136.58 | 2.93
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.00085 | 139.51 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 136.58 | 2.93
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00115 | 161.52 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 157.63 | 3.89
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00118 | 161.52 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 157.63 | 3.89
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02164 | 162.14 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 155.52 | 6.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02381 | 162.14 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 155.52 | 6.62
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00066 | 166.85 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 162.57 | 4.28
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0007 | 166.85 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 162.57 | 4.28
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00053 | 102.53 | P11:24:CLEC::G1DOLHIL:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00056 | 102.53 | P11:24:CLEC::G1DOLHIL:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.0003 | 122.65 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 121.5 | 1.15
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 120 | 132 | 0.00031 | 122.65 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 121.5 | 1.15
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00875 | 110.86 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636199 BLACKHAWK 3 345 636200 BLACKHAWK 5 161 1 | 560 | 669 | 0.00938 | 110.86 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External | 105.03 | 5.83
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00068 | 108.01 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 106.57 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00068 | 108.01 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 106.57 | 1.44
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0482 | 123.34 | Base Case | External | 121.32 | 2.02
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04878 | 123.34 | Base Case | External | 121.32 | 2.02
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00773 | 103 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 395 | 498 | 0.00809 | 103 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00378 | 103.37 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 102.16 | 1.21
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 337 | 348 | 0.00394 | 103.37 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 102.16 | 1.21
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00965 | 105.33 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01015 | 105.33 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01211 | 112.71 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 111.49 | 1.22
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01247 | 112.71 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 111.49 | 1.22
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00053 | 102.48 | P11:22:CLEC::G3MADISN:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00056 | 102.48 | P11:22:CLEC::G3MADISN:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03295 | 126.67 | 104071: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.0324 | 126.67 | 104071: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00398 | 108.28 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 106.1 | 2.18
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.0041 | 108.28 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 106.1 | 2.18
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02164 | 124.21 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 117.75 | 6.46
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02381 | 124.21 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 117.75 | 6.46
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 0.0001 | 121.9 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.78 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.17897 | 102.45 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.17781 | 102.45 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | Internal
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00581 | 108.32 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 102.06 | 6.26
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 223 | 223 | 0.00601 | 108.32 | P12:161:AMIL-ALTW::NIOTA:WEVER:1 | External | 102.06 | 6.26
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00179 | 102.32 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00186 | 102.32 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 0.0001 | 121.55 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.43 | 0.12
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 117.94 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.96 | -0.02
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 117.94 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.96 | -0.02
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 103.13 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 103.13 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 102.45 | 0.68
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01082 | 120.99 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 114.3 | 6.69
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01138 | 120.99 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 114.3 | 6.69
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00241 | 129.76 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 127.19 | 2.57
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00235 | 129.76 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 127.19 | 2.57
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.0187 | 104.75 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.01947 | 104.75 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00066 | 138.5 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 136.53 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00069 | 138.5 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 136.53 | 1.97
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 109.26 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 109.09 | 0.17
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00019 | 109.26 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 109.09 | 0.17
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00021 | 101.62 | P11:024:DPC:ALMA2:6 | External | 100.72 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00022 | 101.62 | P11:024:DPC:ALMA2:6 | External | 100.72 | 0.9
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14445 | 114.42 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 133.79 | -19.37
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01155 | 137.46 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01224 | 137.46 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 132.61 | 4.85
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 103.72 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.69 | 0.03
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 103.72 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.69 | 0.03
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.0042 | 119.8 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 120.22 | -0.42
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00402 | 119.8 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 120.22 | -0.42
Thermal | 00NR | S2 | 24WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05718 | 112.46 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 108.84 | 3.62
Thermal | 00NR | S2 | 24WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.0564 | 112.46 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 108.84 | 3.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00032 | 101.46 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 103.41 | -1.95
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00035 | 101.46 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 103.41 | -1.95
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00523 | 114.22 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 113.02 | 1.2
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00548 | 114.22 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 113.02 | 1.2
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 78 | 114 | 0.00017 | 102.34 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 78 | 114 | 0.00018 | 102.34 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08931 | 118.37 | Base Case | External | 116.46 | 1.91
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09112 | 118.37 | Base Case | External | 116.46 | 1.91
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03048 | 105.78 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal | 101.13 | 4.65
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00834 | 112.32 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00848 | 112.32 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00098 | 129.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 129.72 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.001 | 129.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 129.72 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07431 | 104.67 | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 101.18 | 3.49
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.0727 | 104.67 | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 101.18 | 3.49
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03165 | 116.66 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 112.58 | 4.08
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.0314 | 116.66 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 112.58 | 4.08
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.0014 | 100.68 | P12:500:EES:MOLIVE:EL_EHV:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00141 | 100.68 | P12:500:EES:MOLIVE:EL_EHV:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00633 | 125.16 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 127.48 | -2.32
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00642 | 125.16 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 127.48 | -2.32
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01109 | 160.58 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01154 | 160.58 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 117.69 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 117.23 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 117.69 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 117.23 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00015 | 139.39 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 134.48 | 4.91
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00016 | 139.39 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 134.48 | 4.91
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 8e-05 | 123.62 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 117.97 | 5.65
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 9e-05 | 123.62 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 117.97 | 5.65
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00794 | 106.59 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00801 | 106.59 | P12:345:AMMO::ZACHARY:MAYWOOD:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608672 HILLTOP7 115 997593 HIL1 115 1 | 187 | 233 | 0.00022 | 124.7 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 116.64 | 8.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608672 HILLTOP7 115 997593 HIL1 115 1 | 187 | 233 | 0.00024 | 124.7 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 116.64 | 8.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.24336 | 111.31 | P12:161:OPPD:S1209-S1231 CKT 2 | Internal | 111.69 | -0.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 118.11 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 117.61 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 118.11 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 117.61 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04914 | 100.25 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04979 | 100.25 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03165 | 111.84 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 108.31 | 3.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.0314 | 111.84 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 108.31 | 3.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00051 | 119.09 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 108.9 | 10.19
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00053 | 119.09 | P12:069-161:DPC:HLSBORO:BELLCTR | External | 108.9 | 10.19
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00257 | 101.5 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 102.95 | -1.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00265 | 101.5 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 102.95 | -1.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00016 | 101.85 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00018 | 101.85 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00265 | 115.43 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00272 | 115.43 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03266 | 107.91 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 106.38 | 1.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03222 | 107.91 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 106.38 | 1.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 690 | 690 | 1e-05 | 178.94 | Base Case | External | 179.47 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 690 | 690 | 1e-05 | 178.94 | Base Case | External | 179.47 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03123 | 111.27 | P55:161-345:KCPL:HAWTHORN_BUS_20_161:: | Internal | 107.8 | 3.47
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03097 | 111.27 | P55:161-345:KCPL:HAWTHORN_BUS_20_161:: | Internal | 107.8 | 3.47
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.0188 | 113.2 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.51 | 0.69
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.01956 | 113.2 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.51 | 0.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00059 | 110.38 | Base Case | External | 111.51 | -1.13
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00061 | 110.38 | Base Case | External | 111.51 | -1.13
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00048 | 142.5 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 144.94 | -2.44
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00051 | 142.5 | 106178: 620314 BIGSTON4 230 655465 BLAIR-ER4 230 1 | External | 144.94 | -2.44
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00482 | 116.15 | P23:345:MEC:GDMEC 901 | External | 117.36 | -1.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00494 | 116.15 | P23:345:MEC:GDMEC 901 | External | 117.36 | -1.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00385 | 173.23 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 175.5 | -2.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00401 | 173.23 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 175.5 | -2.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 103.27 | P13:138-115:MP:TCH:TR4(1) | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 103.27 | P13:138-115:MP:TCH:TR4(1) | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00012 | 104.01 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 103.18 | 0.83
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00012 | 104.01 | 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1: 608713 MNTC C G 13.8 608711 MNTCPTC7 115 1 | External | 103.18 | 0.83
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01109 | 160.58 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01154 | 160.58 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00103 | 130.28 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 128.5 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00113 | 130.28 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 128.5 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01375 | 103.97 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01457 | 103.97 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.06873 | 107.58 | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.06742 | 107.58 | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 102.76 | P13:138-115:MP:TCH:TR4(1) | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 102.76 | P13:138-115:MP:TCH:TR4(1) | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00082 | 184.78 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 183.61 | 1.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00089 | 184.78 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 183.61 | 1.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01166 | 124.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01214 | 124.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00287 | 217.51 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 214.53 | 2.98
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00314 | 217.51 | 300073 5GENTRY 161 300076 5FAIRPT 161 1: 300073 5GENTRY 161 300076 5FAIRPT 161 1 | External | 214.53 | 2.98
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02408 | 120.93 | P23:345:MEC:SYCAMORE 905 | External | 118.73 | 2.2
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.0245 | 120.93 | P23:345:MEC:SYCAMORE 905 | External | 118.73 | 2.2
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 109.41 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 109.41 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00025 | 100.7 | 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1: 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00027 | 100.7 | 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1: 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 293 | 318 | 0.03123 | 100.3 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 293 | 318 | 0.03125 | 100.3 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00829 | 109.73 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00866 | 109.73 | P23:345:ITCM:HCKRYCK:FUT2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00209 | 107.16 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 107.12 | 0.04
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00213 | 107.16 | P13:161-69:ITCM-AECI:HENRYCO5 T1:IA-SE | External | 107.12 | 0.04
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00172 | 101.38 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 101.69 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00182 | 101.38 | P12:115:XEL:AUTO-SINGLE:WILMART7:SUMMIT:1 | External | 101.69 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0099 | 130.57 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 132.7 | -2.13
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0104 | 130.57 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 132.7 | -2.13
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00787 | 119.76 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00759 | 119.76 | 84326: 541229 ODESSA 5 161 541232 LEX161 5 161 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 115.56 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 115.56 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00116 | 102.52 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 102.41 | 0.11
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00115 | 102.52 | 92458: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 | External | 102.41 | 0.11
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00044 | 142.38 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 143.18 | -0.8
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00045 | 142.38 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 143.18 | -0.8
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.09458 | 135.39 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 132.23 | 3.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.09368 | 135.39 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 132.23 | 3.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01075 | 100.06 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01132 | 100.06 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00523 | 114.22 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 113.02 | 1.2
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00548 | 114.22 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 113.02 | 1.2
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00056 | 126.63 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 133.84 | -7.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00059 | 126.63 | P12:115:XEL:AUTO-SINGLE:RIVFLT7:RIVFLSN7:1 | External | 133.84 | -7.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00087 | 122.47 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 112.44 | 10.03
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00092 | 122.47 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 112.44 | 10.03
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00059 | 117.03 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 119.13 | -2.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00061 | 117.03 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 119.13 | -2.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.06927 | 122.39 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.07716 | 122.39 | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00015 | 139.68 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 134.63 | 5.05
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00016 | 139.68 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 134.63 | 5.05
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00794 | 106.59 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00801 | 106.59 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 187 | 233.8 | 0.00022 | 121.34 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 114.24 | 7.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608616 HILLTOP4 230 1 | 187 | 233.8 | 0.00024 | 121.34 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 114.24 | 7.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00032 | 125.82 | Base Case | External | 127.12 | -1.3
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00033 | 125.82 | Base Case | External | 127.12 | -1.3
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07054 | 120.92 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 118.68 | 2.24
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07178 | 120.92 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 118.68 | 2.24
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 103.27 | P13:138-115:MP:TCH:TR4 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 103.27 | P13:138-115:MP:TCH:TR4 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00447 | 118.28 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 118.84 | -0.56
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00476 | 118.28 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 118.84 | -0.56
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00023 | 132.94 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 133.48 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00022 | 132.94 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 133.48 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00411 | 102.46 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00424 | 102.46 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03266 | 105.47 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 103.69 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03222 | 105.47 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 103.69 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01225 | 118.09 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01293 | 118.09 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 101.93 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 101.93 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00148 | 117.94 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 120.15 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00158 | 117.94 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 120.15 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21472 | 106.61 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03003 | 111.98 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 109.97 | 2.01
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00635 | 106.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00647 | 106.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 5e-05 | 108.95 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 5e-05 | 108.95 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00368 | 114.29 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 112.8 | 1.49
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00382 | 114.29 | P12:230:OTP:AUTO-SINGLE:OAKES4:FORMAN4:1 | External | 112.8 | 1.49
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15024 | 110.95 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.44 | 6.51
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14906 | 110.95 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.44 | 6.51
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00778 | 119.47 | P22:345:AMMO::OVERTON:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00751 | 119.47 | P22:345:AMMO::OVERTON:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00011 | 103.71 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00012 | 103.71 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.001 | 132.32 | P23:500:EES-EAI:WH_BLF:B7914 | External | 132.2 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00102 | 132.32 | P23:500:EES-EAI:WH_BLF:B7914 | External | 132.2 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04068 | 108.95 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 105.11 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04044 | 108.95 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 105.11 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.001 | 123.88 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 128.28 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00105 | 123.88 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 128.28 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00216 | 120.44 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 120.98 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00224 | 120.44 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 120.98 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01605 | 101.46 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01611 | 101.46 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00141 | 107.58 | P11:024:DPC:ALMA2:6 | External | 112.06 | -4.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00149 | 107.58 | P11:024:DPC:ALMA2:6 | External | 112.06 | -4.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82913 | 111.43 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 229.9 | 252.8 | 0.00071 | 103.19 | P23:345:XEL:8P4 ASK | External | 107.94 | -4.75
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603048 BAYTOWN7 115 603086 LONG LK7 115 1 | 229.9 | 252.8 | 0.00076 | 103.19 | P23:345:XEL:8P4 ASK | External | 107.94 | -4.75
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02794 | 117.41 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02863 | 117.41 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00022 | 129.43 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 122.81 | 6.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00023 | 129.43 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 122.81 | 6.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00167 | 107.79 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 109.86 | -2.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00175 | 107.79 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 109.86 | -2.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00048 | 140.63 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 142.18 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00051 | 140.63 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 142.18 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00105 | 147.03 | 104728: 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00114 | 147.03 | 104728: 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00383 | 104.08 | P23:345-161:XEL:ADAMS_I:680_S | External | 105.62 | -1.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00407 | 104.08 | P23:345-161:XEL:ADAMS_I:680_S | External | 105.62 | -1.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00032 | 100.96 | P13:345:XEL:BLL TR 7 | External | 103.08 | -2.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00035 | 100.96 | P13:345:XEL:BLL TR 7 | External | 103.08 | -2.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.0004 | 102.03 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1 | External | 102.48 | -0.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00042 | 102.03 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1 | External | 102.48 | -0.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 101.93 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 101.93 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 3e-05 | 108 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 3e-05 | 108 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 109.41 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 109.41 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00026 | 130.46 | P13:115:XEL:COL TR5 AS- | External | 132.77 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00027 | 130.46 | P13:115:XEL:COL TR5 AS- | External | 132.77 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01082 | 105.12 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.68 | 1.44
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 105.12 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.68 | 1.44
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01194 | 116.47 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 115.74 | 0.73
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01229 | 116.47 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 115.74 | 0.73
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.1106 | 102.57 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11032 | 102.57 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00407 | 109.98 | P12:161:DPC:STO-AT15 | External | 107.34 | 2.64
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00426 | 109.98 | P12:161:DPC:STO-AT15 | External | 107.34 | 2.64
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00385 | 142.97 | Base Case | External | 143.82 | -0.85
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00401 | 142.97 | Base Case | External | 143.82 | -0.85
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00014 | 105.92 | 601001 FORBES 2 500 601013 ROSEAUS2 500 1: 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | External | 106.27 | -0.35
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00019 | 105.92 | 601001 FORBES 2 500 601013 ROSEAUS2 500 1: 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | External | 106.27 | -0.35
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.00277 | 108.24 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 108.77 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.00293 | 108.24 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 108.77 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00257 | 101.49 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 102.9 | -1.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00265 | 101.49 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 102.9 | -1.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 102.7 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 102.54 | 0.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 102.7 | P12:115:EES-EAI:EL_EHV:ELDEST | External | 102.54 | 0.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00633 | 125.16 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 127.48 | -2.32
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00642 | 125.16 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 127.48 | -2.32
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 101.93 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661020 DIXGREENRVR7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 101.93 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 103.56 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.55 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.55 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00075 | 110.64 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 104.56 | 6.08
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 67.2 | 71 | 0.00079 | 110.64 | P12:161:ATC-DPC:Q-2D:NED161:SENECA5 | External | 104.56 | 6.08
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01874 | 114.89 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.27 | 2.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01879 | 114.89 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.27 | 2.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00257 | 138.93 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 138.45 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00265 | 138.93 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:ALBANY5:1 | External | 138.45 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 116.82 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 117.04 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 116.82 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 117.04 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00059 | 104.26 | Base Case | External | 105.35 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00061 | 104.26 | Base Case | External | 105.35 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00251 | 130.87 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.64 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00244 | 130.87 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 130.64 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00392 | 115.17 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 117.77 | -2.6
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00416 | 115.17 | P12:345:XEL:AUTO-SINGLE:COONCK3:KOLMNLK3:1 | External | 117.77 | -2.6
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00392 | 115.17 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 117.77 | -2.6
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00416 | 115.17 | 601019 COON CK3 345 601021 KOLMNLK3 345 1: 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 117.77 | -2.6
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00035 | 144.89 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 147.48 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00037 | 144.89 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 147.48 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00399 | 163.92 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 163.92 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03349 | 109.28 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03416 | 109.28 | P12:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00351 | 161.55 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00359 | 161.55 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01125 | 115.36 | P23:345:MEC:GDMEC 902 | External | 115.06 | 0.3
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01171 | 115.36 | P23:345:MEC:GDMEC 902 | External | 115.06 | 0.3
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.17006 | 101.93 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16849 | 101.93 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.001 | 123.88 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 128.28 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00105 | 123.88 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 128.28 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04068 | 108.95 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 105.11 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04044 | 108.95 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 105.11 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0108 | 126.29 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01132 | 126.29 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.31 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 101.14 | 0.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.31 | 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1: 337539 3EL DORADO! 115 337553 3ELDORADO.E! 115 1 | External | 101.14 | 0.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00019 | 103.02 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 105.05 | -2.03
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00022 | 103.02 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT | External | 105.05 | -2.03
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00566 | 115.62 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00603 | 115.62 | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1: 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00031 | 117.43 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 101.77 | 15.66
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 117.43 | P13:69-161:DPC:AUTO-SINGLE:BELLCNTR:BELLCTR5:1 | External | 101.77 | 15.66
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.12506 | 115.82 | 82353: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 646221 S1221 5 161 646255 S1255 5 161 1 646233 S1233 5 161 646255 S1255 5 161 1 646255 S1255 5 161 646259 S1259 5 161 1 646255 S1255 5 161 646260 S1260 5 161 1 646255 S1255 5 161 997272 S3455 T1 161 1 646255 S1255 5 161 997271 S3455 T3 161 1 | Internal | 124.51 | -8.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03506 | 109.58 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal | 103.98 | 5.6
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03478 | 109.58 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal | 103.98 | 5.6
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 997476 DGG9T1 161 1 | 560 | 700 | 0.0284 | 101.88 | P23:345:MEC:SYCAMORE 905 | External | 100.61 | 1.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 997476 DGG9T1 161 1 | 560 | 700 | 0.02904 | 101.88 | P23:345:MEC:SYCAMORE 905 | External | 100.61 | 1.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.07545 | 123.78 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 159.45 | -35.67
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 109.41 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 109.41 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 115.12 | -5.71
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 293 | 334 | 0.03123 | 105.32 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 101.05 | 4.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 293 | 334 | 0.03125 | 105.32 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 101.05 | 4.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00012 | 115.66 | P13:138-115:MP:TCH:TR4 | External | 110.27 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00013 | 115.66 | P13:138-115:MP:TCH:TR4 | External | 110.27 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00322 | 103.93 | Base Case | External | 104.34 | -0.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00331 | 103.93 | Base Case | External | 104.34 | -0.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00087 | 121.47 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 121.48 | -0.01
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00089 | 121.47 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 121.48 | -0.01
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01172 | 119.87 | P23:345:MEC:GDMEC 901 | External | 119.46 | 0.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01221 | 119.87 | P23:345:MEC:GDMEC 901 | External | 119.46 | 0.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.038 | 121.95 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.18 | 1.77
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03746 | 121.95 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.18 | 1.77
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00287 | 215.78 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 213.57 | 2.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00314 | 215.78 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 213.57 | 2.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07431 | 106.81 | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal | 103.38 | 3.43
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.0727 | 106.81 | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal | 103.38 | 3.43
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 222.7 | 222.7 | 0.00204 | 106.68 | P23:345:XEL:8P33 KOL | External | 109.35 | -2.67
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603100 ROSE PL7 115 603110 TERMINL7 115 1 | 222.7 | 222.7 | 0.00215 | 106.68 | P23:345:XEL:8P33 KOL | External | 109.35 | -2.67
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618600 GRE-MCGREGR7 115 618601 GRE-KIMBRLY7 115 1 | 77 | 84.7 | 0.00011 | 102.01 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618600 GRE-MCGREGR7 115 618601 GRE-KIMBRLY7 115 1 | 77 | 84.7 | 0.00012 | 102.01 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00153 | 199.59 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 198.97 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00157 | 199.59 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 198.97 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00044 | 120.08 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 120.83 | -0.75
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 120.08 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 120.83 | -0.75
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00342 | 101.56 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 105.81 | -4.25
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00358 | 101.56 | P12:161:DPC-ALTE:AUTO-SINGLE:STONEMAN:NED161:1 | External | 105.81 | -4.25
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01231 | 151.25 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01282 | 151.25 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.1106 | 102.57 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1099 | 1195 | 0.11032 | 102.57 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00016 | 105.77 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 101.63 | 4.14
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00018 | 105.77 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 101.63 | 4.14
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.00019 | 108.6 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 106.31 | 2.29
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.0002 | 108.6 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 106.31 | 2.29
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.0004 | 103.48 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 103.94 | -0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00042 | 103.48 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 103.94 | -0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00623 | 117.17 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00657 | 117.17 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 107.15 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.67 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00038 | 107.15 | P23:500:EES-EAI:WH_BLF:B7914 | External | 106.67 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 106.56 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 102.05 | 4.51
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 106.56 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 102.05 | 4.51
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 8e-05 | 138.24 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 132.12 | 6.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 9e-05 | 138.24 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 132.12 | 6.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 500 | 500 | 0.00277 | 105.33 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 105.43 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 500 | 500 | 0.00293 | 105.33 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 105.43 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00406 | 124.75 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 125.67 | -0.92
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00418 | 124.75 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 125.67 | -0.92
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00776 | 108.59 | P23:345:XEL:8S25 WLM AS | External | 106.91 | 1.68
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00813 | 108.59 | P23:345:XEL:8S25 WLM AS | External | 106.91 | 1.68
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00553 | 112.61 | P23:345:AMIL::HERLEMAN:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 300050 7PALMYR_AI 345 1 | 336 | 336 | 0.00565 | 112.61 | P23:345:AMIL::HERLEMAN:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07232 | 108.03 | P23:345:MEC:GRIMES 901 | External | 106.48 | 1.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07429 | 108.03 | P23:345:MEC:GRIMES 901 | External | 106.48 | 1.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 126.32 | Base Case | External | 125.46 | 0.86
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 126.32 | Base Case | External | 125.46 | 0.86
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.0047 | 113 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 117 | -4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00462 | 113 | P12:345:AMMO-AMIL:HERLEMAN:MAYWOOD:49 | External | 117 | -4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00012 | 101.59 | Base Case | External | 100.58 | 1.01
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00012 | 101.59 | Base Case | External | 100.58 | 1.01
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00011 | 110.55 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External | 105.27 | 5.28
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00012 | 110.55 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External | 105.27 | 5.28
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01044 | 135.79 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 137.41 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01097 | 135.79 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 137.41 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01237 | 146.64 | P23:345:MEC:GDMEC 901 | External | 146.12 | 0.52
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01289 | 146.64 | P23:345:MEC:GDMEC 901 | External | 146.12 | 0.52
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 113.85 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.82 | 0.03
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 113.85 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.82 | 0.03
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0071 | 111.09 | P11:345:AMMO::CALLAWAY:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00692 | 111.09 | P11:345:AMMO::CALLAWAY:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 293 | 318 | 0.03123 | 100.3 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542991 TERRACE5 161 546651 BARBER 5 161 1 | 293 | 318 | 0.03125 | 100.3 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.76 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.76 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01625 | 111.77 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 109.08 | 2.69
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01791 | 111.77 | 92446: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 | External | 109.08 | 2.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01082 | 105.36 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.93 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 105.36 | 92445: 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 300021 1CHOTCT5 16.0 301348 5CHOTEAU2 161 22 300020 1CHOTCT4 16.0 301348 5CHOTEAU2 161 21 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.93 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00391 | 109.25 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00429 | 109.25 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00153 | 109.7 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 109.36 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00157 | 109.7 | 631110 WAPELLO5 161 630048 WAPELLO8 69 2: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | External | 109.36 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.31 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 101.14 | 0.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1 | 159 | 159 | 0.00041 | 101.31 | P12:HV:EES::3EL DORADO!:3ELDORADO.E!:1 | External | 101.14 | 0.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02218 | 181.18 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 178.04 | 3.14
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02436 | 181.18 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 178.04 | 3.14
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00441 | 106.2 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00452 | 106.2 | 80251: 500200 COLFAX 6 230 500770 RODEMR 6 230 1 500280 ELEESV 6 230 500770 RODEMR 6 230 1 500405 HINSTON 6 230 500770 RODEMR 6 230 1 500760 RAPIDES6 230 500770 RODEMR 6 230 1 500770 RODEMR 6 230 500790 SHERWD 6 230 1 501811 G1NESBIT 22.0 500770 RODEMR 6 230 1 501812 G2RODEMR 22.0 500770 RODEMR 6 230 1 501813 G3MADISN 22.0 500770 RODEMR 6 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07054 | 120.98 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 118.73 | 2.25
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07178 | 120.98 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 118.73 | 2.25
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18458 | 100.86 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18342 | 100.86 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00569 | 103.41 | P23:345:XEL:8S51 HMP | External | 103.63 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.006 | 103.41 | P23:345:XEL:8S51 HMP | External | 103.63 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 107.36 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 103.05 | 4.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 107.36 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 103.05 | 4.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01109 | 160.58 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 325 | 325 | 0.01154 | 160.58 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.038 | 121.72 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.13 | 1.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.03746 | 121.72 | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.13 | 1.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0108 | 126.29 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01132 | 126.29 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00677 | 114.21 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 112.43 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00709 | 114.21 | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1: 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | External | 112.43 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 116.2 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 116.41 | -0.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 116.2 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 116.41 | -0.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.21 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.21 | P13:161-69:EES-EAI:HERGET:AT2 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.0108 | 126.29 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01132 | 126.29 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00022 | 129.26 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 123.29 | 5.97
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00023 | 129.26 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 123.29 | 5.97
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.00277 | 108.24 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 108.77 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.00293 | 108.24 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 1: 615306 GRE-PL VLLY3 345 997578 345-161 161 1 615307 GRE-PL VLLY5 161 997578 345-161 161 1 615308 GRE-PL VLL1T 13.8 997578 345-161 161 1 | External | 108.77 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 114.35 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 114.57 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 114.35 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 114.57 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00391 | 109.25 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00429 | 109.25 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00034 | 142.02 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 144.57 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00036 | 142.02 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 144.57 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00103 | 129.25 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 127.92 | 1.33
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 30 | 30 | 0.00113 | 129.25 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 127.92 | 1.33
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 997476 DGG9T1 161 1 | 560 | 700 | 0.0284 | 104.27 | P23:345:MEC:SYCAMORE 905 | External | 102.87 | 1.4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 997476 DGG9T1 161 1 | 560 | 700 | 0.02904 | 104.27 | P23:345:MEC:SYCAMORE 905 | External | 102.87 | 1.4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01199 | 118.46 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 117.71 | 0.75
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01234 | 118.46 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 117.71 | 0.75
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01077 | 101.04 | P12:161:XEL:ECL-WHT | External | 105.14 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01132 | 101.04 | P12:161:XEL:ECL-WHT | External | 105.14 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00342 | 101.56 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 105.81 | -4.25
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00358 | 101.56 | 681519 STONEMAN 161 699010 NED 161 161 1: 681519 STONEMAN 161 699010 NED 161 161 1 | External | 105.81 | -4.25
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00012 | 116.55 | P13:138-115:MP:TCH:TR4(1) | External | 111.16 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00013 | 116.55 | P13:138-115:MP:TCH:TR4(1) | External | 111.16 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00032 | 101.24 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 102.79 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00035 | 101.24 | P13:230-115-13:XEL:AUTO-SINGLE:BLUELK4:BLUELK7:BLUELK9:7 | External | 102.79 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00072 | 104.22 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 103.72 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00072 | 104.22 | 300331 2PITTSV 69 300110 5PITTSV 161 1: 300331 2PITTSV 69.0 300110 5PITTSV 161 1 | External | 103.72 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.0004 | 103.48 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 103.94 | -0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618204 GRE-CMRTJCT7 115 618207 GRE-CORMRNT7 115 1 | 97.9 | 97.9 | 0.00042 | 103.48 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 103.94 | -0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00105 | 136.54 | Base Case | External | 135.09 | 1.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00114 | 136.54 | Base Case | External | 135.09 | 1.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 141 | 141 | 0.00024 | 127.11 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 602039 ROCK CO5 161 631038 MAGNLIA5 161 1 | 141 | 141 | 0.00026 | 127.11 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00533 | 119.5 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00649 | 119.5 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00011 | 106.48 | Base Case | External | 100.94 | 5.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608671 BURNETT7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 106.48 | Base Case | External | 100.94 | 5.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 281.6 | 281.6 | 2e-05 | 117.47 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 119.89 | -2.42
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603068 COON CK7 115 603111 TWIN LK7 115 1 | 281.6 | 281.6 | 3e-05 | 117.47 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 119.89 | -2.42
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04849 | 107.34 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04907 | 107.34 | 636640 SUB 93 3 345 636641 LOUISA G 24 1: 636640 SUB 93 3 345 636641 LOUISA G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00406 | 125.84 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 127.07 | -1.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00418 | 125.84 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 127.07 | -1.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.0001 | 117.59 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 115.31 | 2.28
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | 159 | 159 | 0.00012 | 117.59 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 115.31 | 2.28
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00737 | 136.56 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00799 | 136.56 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00441 | 105.15 | P11:HV:EES::1WAT U3!:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00452 | 105.15 | P11:HV:EES::1WAT U3!:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00032 | 101.24 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 102.79 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00035 | 101.24 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 102.79 | -1.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 112.38 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 110.31 | 2.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 112.38 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External | 110.31 | 2.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00821 | 109.69 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 108.9 | 0.79
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00836 | 109.69 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 108.9 | 0.79
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07431 | 107.37 | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 103.78 | 3.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.0727 | 107.37 | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 103.78 | 3.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.00179 | 100.78 | P23:345:GRE:PVS 19JB1 | External | 104.85 | -4.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.00204 | 100.78 | P23:345:GRE:PVS 19JB1 | External | 104.85 | -4.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00073 | 123.76 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00076 | 123.76 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00834 | 112.32 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00848 | 112.32 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 0.0018 | 122.35 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 120.32 | 2.03
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608615 ARROWHD4 230 608624 FORBES 4 230 1 | 470 | 517 | 0.00191 | 122.35 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 120.32 | 2.03
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00397 | 115.61 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00422 | 115.61 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00011 | 106.99 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External | 102.07 | 4.92
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00012 | 106.99 | 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1: 608663 FLDWDTP7 115 608739 BLCKBRY7 115 1 | External | 102.07 | 4.92
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00105 | 147.03 | 92347: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 50 | 50 | 0.00114 | 147.03 | 92347: 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00043 | 104.09 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00045 | 104.09 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08931 | 118.53 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 116.68 | 1.85
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09112 | 118.53 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 116.68 | 1.85
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00035 | 144.89 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 147.48 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00037 | 144.89 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 147.48 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.0002 | 108.63 | 608666 FONDULAC 115 608676 HIBBARD7 115 1: 608666 FONDULAC 115 608676 HIBBARD7 115 1 | External | 105.01 | 3.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00022 | 108.63 | 608666 FONDULAC 115 608676 HIBBARD7 115 1: 608666 FONDULAC 115 608676 HIBBARD7 115 1 | External | 105.01 | 3.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00623 | 117.09 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615649 GRE-CHUBLAK3 345 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00657 | 117.09 | 71602: 601015 BLUE LK3 345 601020 INVRHLS3 345 1 601020 INVRHLS3 345 601023 REDROCK3 345 1 601020 INVRHLS3 345 997664 IVH TR9 115 9 601003 PR ISLD3 345 601051 HMPT CNR3 345 1 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 601039 NROC 3 345 601051 HMPT CNR3 345 1 601051 HMPT CNR3 345 615649 GRE-CHUBLAK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00024 | 103.32 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.21 | -1.89
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00025 | 103.32 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 105.21 | -1.89
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04849 | 122.17 | Base Case | External | 121.12 | 1.05
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04907 | 122.17 | Base Case | External | 121.12 | 1.05
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.55 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.55 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 222.43 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 225.42 | -2.99
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00099 | 222.43 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 225.42 | -2.99
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00153 | 103.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.72 | 0.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00156 | 103.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.72 | 0.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.01893 | 100.76 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635605 GRNGRTP5 161 635614 100 54 5 161 1 | 373 | 395 | 0.01966 | 100.76 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0086 | 101.35 | Base Case | External | 100.73 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00902 | 101.35 | Base Case | External | 100.73 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00153 | 109.7 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 109.36 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | 131 | 131 | 0.00157 | 109.7 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:2 | External | 109.36 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.03799 | 121.69 | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 120.12 | 1.57
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.03745 | 121.69 | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 120.12 | 1.57
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05748 | 109.63 | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05657 | 109.63 | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 470 | 517 | 0.00121 | 107.69 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 106.13 | 1.56
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608615 ARROWHD4 230 1 | 470 | 517 | 0.00131 | 107.69 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 106.13 | 1.56
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601055 SCOTTCO3 345 997636 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01103 | 109.25 | P23:345:XEL:8M57 SCO | External | 107.52 | 1.73
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601055 SCOTTCO3 345 997636 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01156 | 109.25 | P23:345:XEL:8M57 SCO | External | 107.52 | 1.73
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00265 | 107.7 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00272 | 107.7 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 500 | 500 | 0.00277 | 105.33 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 105.43 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997573 345-161 161 2 | 500 | 500 | 0.00293 | 105.33 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL1T:1 | External | 105.43 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18459 | 100.89 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18343 | 100.89 | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00443 | 105.66 | P24:345:AMMO::LABADIE:15H | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00453 | 105.66 | P24:345:AMMO::LABADIE:15H | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00087 | 121.52 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 121.43 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00089 | 121.52 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 121.43 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21524 | 105.42 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04068 | 110.55 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 106.97 | 3.58
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.04044 | 110.55 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 106.97 | 3.58
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 122.28 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 120 | 2.28
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 122.28 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 120 | 2.28
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00794 | 106.59 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300694 5PALMYR_AI 161 1 | 172 | 172 | 0.00801 | 106.59 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01465 | 129.72 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 130.22 | -0.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01427 | 129.72 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 130.22 | -0.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 78 | 114 | 0.00028 | 102.86 | 608668 CLOQUET7 115 608916 CANOSIA7 115 1: 608668 CLOQUET7 115 608916 CANOSIA7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608666 FONDULAC 115 1 | 78 | 114 | 0.00031 | 102.86 | 608668 CLOQUET7 115 608916 CANOSIA7 115 1: 608668 CLOQUET7 115 608916 CANOSIA7 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.02 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 124.81 | 0.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.02 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 124.81 | 0.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00087 | 121.52 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 121.43 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00089 | 121.52 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 121.43 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00059 | 111.14 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 112.45 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00061 | 111.14 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 112.45 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00059 | 111.14 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 112.45 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00061 | 111.14 | 601011 SHERCO 3 345 600001 SHERC32G 24 1: 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | External | 112.45 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00241 | 101.67 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 101.44 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00246 | 101.67 | 631106 HENRYCO5 161 631111 JEFF 5 161 1: 631106 HENRYCO5 161 631111 JEFF 5 161 1 | External | 101.44 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01058 | 190.88 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 189.16 | 1.72
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01168 | 190.88 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 189.16 | 1.72
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.0007 | 130.8 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 130.98 | -0.18
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00073 | 130.8 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 130.98 | -0.18
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01058 | 109.13 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 107.7 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01168 | 109.13 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 107.7 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05187 | 100.5 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05128 | 100.5 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00031 | 117.43 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 101.77 | 15.66
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 2 | 33.6 | 41 | 0.00032 | 117.43 | 681526 BELLCTR5 161 680075 BELLCNTR 69 1: 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | External | 101.77 | 15.66
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01375 | 103.97 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01457 | 103.97 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00022 | 144.23 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 138.43 | 5.8
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00023 | 144.23 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 138.43 | 5.8
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 113.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.67 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 113.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 113.67 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00024 | 133.03 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 133.57 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00022 | 133.03 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 133.57 | -0.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.21 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.21 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00387 | 114.89 | P11:024:DPC:ALMA2:6 | External | 115.04 | -0.15
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00403 | 114.89 | P11:024:DPC:ALMA2:6 | External | 115.04 | -0.15
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00015 | 155.14 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 150.41 | 4.73
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00016 | 155.14 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 150.41 | 4.73
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01009 | 128.62 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00978 | 128.62 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00372 | 114.95 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 113.45 | 1.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620314 BIGSTON4 230 620325 BROWNSV4 230 1 | 259 | 285 | 0.00385 | 114.95 | 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1: 620362 OAKES 4 230 661098 ELLENDLMVP4 230 1 | External | 113.45 | 1.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00598 | 114.2 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00616 | 114.2 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00012 | 100.01 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618601 GRE-KIMBRLY7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00013 | 100.01 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00777 | 110.97 | P23:345:XEL:SPS 8S72 HNA | External | 109.48 | 1.49
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00813 | 110.97 | P23:345:XEL:SPS 8S72 HNA | External | 109.48 | 1.49
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00406 | 125.84 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 127.07 | -1.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00418 | 125.84 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 127.07 | -1.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03506 | 106.91 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal | 101.79 | 5.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03478 | 106.91 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal | 101.79 | 5.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 25 | 31 | 0.0002 | 105.22 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 104.98 | 0.24
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997050 GLENHAM TR1 115 1 | 25 | 31 | 0.0002 | 105.22 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 104.98 | 0.24
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 122.09 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.07 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 122.09 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 122.07 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00598 | 114.2 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631109 BRLGTN 5 161 631216 WEVER5 161 1 | 229 | 229 | 0.00616 | 114.2 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01096 | 102.44 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1188.5 | 1188.5 | 0.01155 | 102.44 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.0004 | 111.87 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 112.64 | -0.77
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00042 | 111.87 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1 | External | 112.64 | -0.77
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0071 | 111.56 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 111.62 | -0.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00692 | 111.56 | 85223: 505502 TRUMAN 5 161 505504 TRU123 1 13.8 1 505502 TRUMAN 5 161 505506 TRU456 1 13.8 1 | External | 111.62 | -0.06
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00011 | 109.21 | Base Case | External | 103.7 | 5.51
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00012 | 109.21 | Base Case | External | 103.7 | 5.51
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00074 | 175.72 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 177.6 | -1.88
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00078 | 175.72 | P12:161:DPC:AUTO-SINGLE:BVRCRK5:HARMONY5:1 | External | 177.6 | -1.88
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.0017 | 106.04 | P23:345:XEL:8M54 SCO | External | 107.66 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.0018 | 106.04 | P23:345:XEL:8M54 SCO | External | 107.66 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00032 | 105.52 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00032 | 105.52 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.00123 | 100.88 | 300113 5SRIVER 161 300339 5EMERSN 161 1: 300113 5SRIVER 161 300339 5EMERSN 161 1 | External | 100.61 | 0.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.0013 | 100.88 | 300113 5SRIVER 161 300339 5EMERSN 161 1: 300113 5SRIVER 161 300339 5EMERSN 161 1 | External | 100.61 | 0.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00032 | 108.75 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.53 | 0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00033 | 108.75 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.53 | 0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00153 | 102.01 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.48 | 0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00156 | 102.01 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.48 | 0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 104.05 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.05 | -10
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 104.05 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.05 | -10
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04897 | 107.28 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04962 | 107.28 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.00028 | 125.49 | 71569: 601019 COON CK3 345 997666 90199-A 115 10 603068 COON CK7 115 997666 90199-A 115 10 605017 CNCTER29 34.5 997666 90199-A 115 10 601011 SHERCO 3 345 601019 COON CK3 345 1 601011 SHERCO 3 345 615327 GRE-BUNKER 3 345 2 601019 COON CK3 345 615327 GRE-BUNKER 3 345 2 615327 GRE-BUNKER 3 345 997571 345/230 230 1 | External | 125.61 | -0.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.0003 | 125.49 | 71569: 601019 COON CK3 345 997666 90199-A 115 10 603068 COON CK7 115 997666 90199-A 115 10 605017 CNCTER29 34.5 997666 90199-A 115 10 601011 SHERCO 3 345 601019 COON CK3 345 1 601011 SHERCO 3 345 615327 GRE-BUNKER 3 345 2 601019 COON CK3 345 615327 GRE-BUNKER 3 345 2 615327 GRE-BUNKER 3 345 997571 345/230 230 1 | External | 125.61 | -0.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00653 | 114.58 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 114.78 | -0.2
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00667 | 114.58 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 114.78 | -0.2
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00012 | 116.55 | P13:138-115:MP:TCH:TR4 | External | 111.16 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00013 | 116.55 | P13:138-115:MP:TCH:TR4 | External | 111.16 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 110.49 | 608681 LSPI 7 115 608682 LSPI 9 14.3 1: 608681 LSPI 7 115 608682 LSPI 9 14.3 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 110.49 | 608681 LSPI 7 115 608682 LSPI 9 14.3 1: 608681 LSPI 7 115 608682 LSPI 9 14.3 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00112 | 233.27 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 236.69 | -3.42
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00118 | 233.27 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 236.69 | -3.42
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00087 | 112.77 | Base Case | External | 112.43 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00089 | 112.77 | Base Case | External | 112.43 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00024 | 103.79 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 105.73 | -1.94
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00025 | 103.79 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 105.73 | -1.94
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00047 | 137.72 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 141.82 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00049 | 137.72 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 141.82 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00116 | 103.57 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 103.46 | 0.11
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00114 | 103.57 | 87093: 547459 WWR477 161 547498 STL439 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547470 JOP145 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 1 547483 JOP389 5 161 547498 STL439 5 161 2 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547658 S4G439 1 18.0 1 | External | 103.46 | 0.11
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00342 | 100.97 | P12:161:DPC:STO-AT15 | External | 104.04 | -3.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681525 GRANGRAE 161 1 | 201 | 221 | 0.00357 | 100.97 | P12:161:DPC:STO-AT15 | External | 104.04 | -3.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.0017 | 106.04 | P23:345:XEL:8M53 SCO | External | 107.66 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.0018 | 106.04 | P23:345:XEL:8M53 SCO | External | 107.66 | -1.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00059 | 117.03 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 119.13 | -2.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00061 | 117.03 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | External | 119.13 | -2.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00272 | 106.37 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00275 | 106.37 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 115.44 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 115.65 | -0.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 115.44 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 115.65 | -0.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01046 | 136.69 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 138.26 | -1.57
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01099 | 136.69 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 138.26 | -1.57
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06175 | 105.99 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 104.51 | 1.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06098 | 105.99 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 104.51 | 1.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00399 | 163.28 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 163.28 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00049 | 159.55 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00053 | 159.55 | P23:345:ALTW:MITCHLCO:1150 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00025 | 100.7 | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00027 | 100.7 | P12:230:UMZW:# 139 #: GF IN MN. GF-WILLMAR LINE FAULT | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01625 | 149.82 | Base Case | External | 146.87 | 2.95
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.01791 | 149.82 | Base Case | External | 146.87 | 2.95
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00482 | 116.16 | P23:345:MEC:GDMEC 902 | External | 117.37 | -1.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00494 | 116.16 | P23:345:MEC:GDMEC 902 | External | 117.37 | -1.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00257 | 109.07 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 110.49 | -1.42
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00265 | 109.07 | P12:115:ALTW:AUTO-SINGLE:PRARCK7:BERTRAM7:1 | External | 110.49 | -1.42
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00212 | 117.04 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 116.58 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00222 | 117.04 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 116.58 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00383 | 104.08 | P23:345-161:XEL:ADAMS_I:681_S | External | 105.62 | -1.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00407 | 104.08 | P23:345-161:XEL:ADAMS_I:681_S | External | 105.62 | -1.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00022 | 145.11 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 139.32 | 5.79
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00023 | 145.11 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 139.32 | 5.79
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01253 | 100.97 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | 327 | 327 | 0.01287 | 100.97 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00357 | 139.98 | Base Case | External | 140.25 | -0.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00375 | 139.98 | Base Case | External | 140.25 | -0.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 105.27 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608676 HIBBARD7 115 608680 WNTR ST7 115 1 | 182 | 182 | 1e-05 | 105.27 | Base Case | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.038 | 121.95 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.18 | 1.77
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03746 | 121.95 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.18 | 1.77
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603150 HOLCOMB7 115 680245 HOLCOMBE 69.0 1 | 46.7 | 54 | 0.00027 | 103.71 | 71613: 605353 CADOTT 8 69.0 605354 BOYD 8 69.0 1 605354 BOYD 8 69.0 605420 DELMAR 8 69.0 1 605351 WISOTBC8 69.0 680482 DPC TAP8 69.0 1 605353 CADOTT 8 69.0 680482 DPC TAP8 69.0 1 605349 WISSOTAG 69.0 605523 LFY TAP8 69.0 1 605351 WISOTBC8 69.0 605523 LFY TAP8 69.0 1 605523 LFY TAP8 69.0 680511 LAFAYETE 69.0 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 605355 STANLEY8 69.0 605420 DELMAR 8 69.0 1 | External | 112.22 | -8.51
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603150 HOLCOMB7 115 680245 HOLCOMBE 69.0 1 | 46.7 | 54 | 0.00028 | 103.71 | 71613: 605353 CADOTT 8 69.0 605354 BOYD 8 69.0 1 605354 BOYD 8 69.0 605420 DELMAR 8 69.0 1 605351 WISOTBC8 69.0 680482 DPC TAP8 69.0 1 605353 CADOTT 8 69.0 680482 DPC TAP8 69.0 1 605349 WISSOTAG 69.0 605523 LFY TAP8 69.0 1 605351 WISOTBC8 69.0 605523 LFY TAP8 69.0 1 605523 LFY TAP8 69.0 680511 LAFAYETE 69.0 1 603152 T-CRNRS7 115 603273 PIP61 OWEN 8 115 1 603153 HYDROLN7 115 603273 PIP61 OWEN 8 115 1 603152 T-CRNRS7 115 603216 TCORNERSCAP7 115 Z 605028 T CORNE8 69.0 603152 T-CRNRS7 115 1 605355 STANLEY8 69.0 605420 DELMAR 8 69.0 1 | External | 112.22 | -8.51
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 102.76 | P13:138-115:MP:TCH:TR4 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00013 | 102.76 | P13:138-115:MP:TCH:TR4 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00023 | 100.27 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 100.65 | -0.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00024 | 100.27 | P12:161:ALTW:AUTO-SINGLE:BVRCHNL25:BVRCHNL15:1 | External | 100.65 | -0.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.00147 | 107.44 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 105.6 | 1.84
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300278 2LOCUST 69.0 300094 5LOCUST 161 1 | 56 | 56 | 0.0014 | 107.44 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 105.6 | 1.84
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00448 | 108.45 | P23:345:XEL:8M36 CNC | External | 110.9 | -2.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00474 | 108.45 | P23:345:XEL:8M36 CNC | External | 110.9 | -2.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 104.05 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.05 | -10
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 104.05 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.05 | -10
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00034 | 142.02 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 144.57 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00036 | 142.02 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 144.57 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.00123 | 101.32 | 300339 5EMERSN 161 300363 5NEWARK 161 1: 300339 5EMERSN 161 300363 5NEWARK 161 1 | External | 101.06 | 0.26
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.0013 | 101.32 | 300339 5EMERSN 161 300363 5NEWARK 161 1: 300339 5EMERSN 161 300363 5NEWARK 161 1 | External | 101.06 | 0.26
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00257 | 101.5 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 102.95 | -1.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631017 PRAR CK7 115 631022 SUTLIFF7 115 1 | 80 | 80 | 0.00265 | 101.5 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 102.95 | -1.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05748 | 109.63 | 84827: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05657 | 109.63 | 84827: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00351 | 161.55 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00359 | 161.55 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00454 | 104.04 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 103.98 | 0.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00479 | 104.04 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 103.98 | 0.06
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 115.56 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 115.56 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00011 | 108.33 | Base Case | External | 102.81 | 5.52
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00012 | 108.33 | Base Case | External | 102.81 | 5.52
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00251 | 100.4 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 335361 4CANKTON% 138 335454 4COLTON 138 1 | 225 | 225 | 0.00254 | 100.4 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 293 | 334 | 0.03123 | 105.32 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 101.05 | 4.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542989 NAVY 5 161 542991 TERRACE5 161 1 | 293 | 334 | 0.03125 | 105.32 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 101.05 | 4.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 239 | 239 | 9e-05 | 107.2 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 109.92 | -2.72
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603091 MOORELK7 115 603099 RIVRSID7 115 1 | 239 | 239 | 0.00011 | 107.2 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 109.92 | -2.72
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02773 | 113.01 | P23:345:MEC:GDMEC 902 | External | 113.08 | -0.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02837 | 113.01 | P23:345:MEC:GDMEC 902 | External | 113.08 | -0.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00829 | 109.73 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00866 | 109.73 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00479 | 124.01 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00491 | 124.01 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0071 | 105.4 | Base Case | External | 105.32 | 0.08
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00692 | 105.4 | Base Case | External | 105.32 | 0.08
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.00275 | 107.27 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 107.8 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.0029 | 107.27 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 107.8 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00718 | 128.81 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00775 | 128.81 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00569 | 103.59 | P23:345:XEL:8S51 HMP | External | 103.9 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.006 | 103.59 | P23:345:XEL:8S51 HMP | External | 103.9 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0354 | 110.06 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 104.4 | 5.66
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03513 | 110.06 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 104.4 | 5.66
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00153 | 120.8 | 105809: 658082 MPSSE 7 115 658084 MPSCENT7 115 1 658084 MPSCENT7 115 658086 MPSNE 7 115 1 652203 FARGO 8 69.0 657802 DELVO 8 69.0 1 652203 FARGO 8 69.0 652436 FARGO 7 115 2 652430 EGF IND7 115 657707 CALEDON7 115 1 652436 FARGO 7 115 657707 CALEDON7 115 1 657707 CALEDON7 115 997127 CALEDONIA 69.0 1 652430 EGF IND7 115 652443 GRNDFKS7 115 1 652436 FARGO 7 115 658080 MPSBROOK 115 1 652323 FARGO 9 41.8 652436 FARGO 7 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 652553 MOORHED4 230 1 652435 FARGO 4 230 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 658343 MPS NE 9 12.5 658019 MPS WIND G 0.60 1 | External | 122.11 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00159 | 120.8 | 105809: 658082 MPSSE 7 115 658084 MPSCENT7 115 1 658084 MPSCENT7 115 658086 MPSNE 7 115 1 652203 FARGO 8 69.0 657802 DELVO 8 69.0 1 652203 FARGO 8 69.0 652436 FARGO 7 115 2 652430 EGF IND7 115 657707 CALEDON7 115 1 652436 FARGO 7 115 657707 CALEDON7 115 1 657707 CALEDON7 115 997127 CALEDONIA 69.0 1 652430 EGF IND7 115 652443 GRNDFKS7 115 1 652436 FARGO 7 115 658080 MPSBROOK 115 1 652323 FARGO 9 41.8 652436 FARGO 7 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 652435 FARGO 4 230 652553 MOORHED4 230 1 652435 FARGO 4 230 997173 FA KV1A 115 1 652435 FARGO 4 230 997172 FA KV2A 115 2 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 658343 MPS NE 9 12.5 658019 MPS WIND G 0.60 1 | External | 122.11 | -1.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00241 | 101.67 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 101.44 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630036 JEFF 8 69.0 631111 JEFF 5 161 1 | 100 | 100 | 0.00246 | 101.67 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:JEFF5:1 | External | 101.44 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00307 | 105.05 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External | 103.13 | 1.92
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00316 | 105.05 | 681523 GENOA 5 161 681528 HARMONY5 161 1: 681523 GENOA 5 161 681528 HARMONY5 161 1 | External | 103.13 | 1.92
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00029 | 115.09 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 115.32 | -0.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 115.09 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 115.32 | -0.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00635 | 128.34 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 114.21 | 14.13
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00647 | 128.34 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 114.21 | 14.13
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02773 | 112.99 | P23:345:MEC:GDMEC 901 | External | 113.05 | -0.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02837 | 112.99 | P23:345:MEC:GDMEC 901 | External | 113.05 | -0.06
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04849 | 102.16 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 101.21 | 0.95
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04907 | 102.16 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 101.21 | 0.95
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00482 | 127.81 | P23:345:MEC:GDMEC 902 | External | 129.17 | -1.36
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00494 | 127.81 | P23:345:MEC:GDMEC 902 | External | 129.17 | -1.36
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0354 | 110.06 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 104.4 | 5.66
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03513 | 110.06 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 104.4 | 5.66
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03165 | 111.84 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 108.31 | 3.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.0314 | 111.84 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 108.31 | 3.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.00028 | 124.66 | P23:345:XEL:8M40 CNC | External | 124.68 | -0.02
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615328 GRE-BUNKER 4 230 615383 GRE-ELK RIV4 230 1 | 242.8 | 242.8 | 0.0003 | 124.66 | P23:345:XEL:8M40 CNC | External | 124.68 | -0.02
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00689 | 110.66 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00717 | 110.66 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00194 | 103.99 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 102.84 | 1.15
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300226 2HICKRY 69.0 300087 5HICKCK 161 1 | 56 | 56 | 0.00187 | 103.99 | 300068 5CHILLI 161 300087 5HICKCK 161 1: 300068 5CHILLI 161 300087 5HICKCK 161 1 | External | 102.84 | 1.15
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01199 | 118.46 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 117.71 | 0.75
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01234 | 118.46 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 117.71 | 0.75
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03266 | 107.91 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 106.38 | 1.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03222 | 107.91 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 106.38 | 1.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 500 | 500 | 0.00275 | 104.35 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 104.45 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 500 | 500 | 0.0029 | 104.35 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 104.45 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00777 | 108.61 | P23:345:XEL:8S27 WLM AS | External | 106.92 | 1.69
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00813 | 108.61 | P23:345:XEL:8S27 WLM AS | External | 106.92 | 1.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 226.76 | P12:161:DPC:RCE-HAR5 | External | 229.88 | -3.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00099 | 226.76 | P12:161:DPC:RCE-HAR5 | External | 229.88 | -3.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.00275 | 107.27 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 107.8 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997572 345-161 161 1 | 500 | 500 | 0.0029 | 107.27 | 615306 GRE-PL VLLY3 345 3WXFMR 345-161 2: 615306 GRE-PL VLLY3 345 997577 345-161 161 2 615307 GRE-PL VLLY5 161 997577 345-161 161 2 615309 GRE-PL VLL2T 13.8 997577 345-161 161 2 | External | 107.8 | -0.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00391 | 109.25 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 631202 COLBY5 161 1 | 327 | 327 | 0.00429 | 109.25 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 115.32 | -6.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01109 | 164.81 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 166.19 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01166 | 164.81 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 166.19 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00032 | 100.41 | P13:345:XEL:BLL TR 7 | External | 102.1 | -1.69
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619940 HUC-MCLEOD 4 230 997512 230/115 115 1 | 187 | 187 | 0.00035 | 100.41 | P13:345:XEL:BLL TR 7 | External | 102.1 | -1.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00533 | 119.74 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00649 | 119.74 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00248 | 101.72 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00258 | 101.72 | P23:345:MEC:LOUISA 954 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00153 | 199.59 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 198.97 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00157 | 199.59 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 198.97 | 0.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00043 | 120.2 | P23:345:AMMO::MONTGOMERY:V43 | External | 121 | -0.8
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 120.2 | P23:345:AMMO::MONTGOMERY:V43 | External | 121 | -0.8
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00121 | 100.07 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.0012 | 100.07 | 300802 2CLARK 69 300070 5CLARK 161 1: 300802 2CLARK 69.0 300070 5CLARK 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00029 | 116.06 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 116.28 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 116.06 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 116.28 | -0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00406 | 138.72 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 140.1 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00418 | 138.72 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 140.1 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00031 | 109.82 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 109.9 | -0.08
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | 386 | 416 | 0.00031 | 109.82 | 80245: 500230 COUGH 4 138 500295 EOLA 4 138 1 500230 COUGH 4 138 500540 MANUEL 4 138 1 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 500230 COUGH 4 138 500720 PLAISAN4 138 1 500230 COUGH 4 138 500780 SHOAKS 4 138 1 500230 COUGH 4 138 500190 COCODR 6 230 1 500230 COUGH 4 138 500190 COCODR 6 230 2 501960 G6COUGH 13.8 500230 COUGH 4 138 1 501970 G7COUGH 22.0 500230 COUGH 4 138 1 501971 G7-1COUGH 23.8 500190 COCODR 6 230 1 501961 G6-1COUGH 23.8 500190 COCODR 6 230 1 501972 G7-2COUGH 23.8 500190 COCODR 6 230 1 500190 COCODR 6 230 500340 FHILL 6 230 1 500190 COCODR 6 230 500405 HINSTON 6 230 1 500190 COCODR 6 230 500880 VILPLT 6 230 1 | External | 109.9 | -0.08
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.07054 | 114.89 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 112.57 | 2.32
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.07178 | 114.89 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 112.57 | 2.32
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00344 | 149.97 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00352 | 149.97 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00582 | 121.78 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00598 | 121.78 | P13:161-69:ITCM:VIELE 5 T1:IA-SE | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00121 | 113.41 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 115.25 | -1.84
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.0013 | 113.41 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 115.25 | -1.84
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.00996 | 124.01 | P23:345:MEC:OAK GROVE 901 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636670 SB 18 5 161 636675 SB 85 5 161 1 | 248 | 248 | 0.01027 | 124.01 | P23:345:MEC:OAK GROVE 901 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00212 | 117.04 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 116.58 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00222 | 117.04 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 116.58 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00533 | 137.36 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997472 WEB AB 161 1 | 560 | 560 | 0.00649 | 137.36 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601024 TERMINL3 345 997650 90198-B 115 10 | 672 | 734 | 0.0002 | 109.3 | P23:345:XEL:8P33 KOL | External | 111.6 | -2.3
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601024 TERMINL3 345 997650 90198-B 115 10 | 672 | 734 | 0.00024 | 109.3 | P23:345:XEL:8P33 KOL | External | 111.6 | -2.3
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18459 | 100.89 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.18343 | 100.89 | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03349 | 109.28 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03416 | 109.28 | P21:345:MEC:AUTO-SINGLE:WALCOTT3:SUB923:1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0354 | 107.37 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 102.21 | 5.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03513 | 107.37 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 102.21 | 5.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00344 | 149.97 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00352 | 149.97 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00579 | 122.36 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00594 | 122.36 | P12:161:ALTW:AUTO-SINGLE:VIELE5:DENMARK5:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00148 | 117.94 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 120.15 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 118.3 | 0.00158 | 117.94 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 120.15 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.35 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 125.23 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.35 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 125.23 | 0.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15024 | 111.35 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 105.5 | 5.85
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14906 | 111.35 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 105.5 | 5.85
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.0043 | 107.34 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 107.97 | -0.63
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 343004 5PERCHE 161 1 | 223 | 223 | 0.00411 | 107.34 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 107.97 | -0.63
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00012 | 107.29 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 103.45 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 608659 RVT2BUS7 115 1 | 77 | 84.7 | 0.00013 | 107.29 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 103.45 | 3.84
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.0014 | 100.68 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00141 | 100.68 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01625 | 111.86 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 109.29 | 2.57
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.01791 | 111.86 | 92451: 300025 1NDWYG1 13.8 300104 5NODWAY 161 1 300026 1NDWYG2 13.8 300104 5NODWAY 161 2 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 109.29 | 2.57
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.038 | 121.72 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.13 | 1.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.03746 | 121.72 | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 120.13 | 1.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00257 | 109.07 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 110.45 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00265 | 109.07 | 631092 BERTRAM5 161 631020 BERTRAM7 115 1: 631092 BERTRAM5 161 631020 BERTRAM7 115 1 | External | 110.45 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01874 | 114.89 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.27 | 2.62
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01879 | 114.89 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External | 112.27 | 2.62
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00519 | 121.98 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 272 | 272 | 0.00551 | 121.98 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.0008 | 103.56 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 103.99 | -0.43
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 301345 2CDRCRST 69.0 301344 5CDRCRST 161 1 | 84 | 84 | 0.00078 | 103.56 | 81792: 300766 5BRIGGSTP 161 512655 TAHLQH 5 161 1 301307 5PARK 161 512655 TAHLQH 5 161 1 301344 5CDRCRST 161 512655 TAHLQH 5 161 1 512655 TAHLQH 5 161 515252 ROSSLAK5 161 1 512655 TAHLQH 5 161 515527 HWY59TP5 161 1 512655 TAHLQH 5 161 998352 TAHAUTO1 69.0 1 512655 TAHLQH 5 161 998351 TAHAUTO2 69.0 2 | External | 103.99 | -0.43
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00385 | 175.73 | P11:024:DPC:ALMA2:6 | External | 177.9 | -2.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00401 | 175.73 | P11:024:DPC:ALMA2:6 | External | 177.9 | -2.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00251 | 130.87 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.64 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00244 | 130.87 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.64 | 0.23
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00717 | 105.26 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 109.91 | -4.65
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.0076 | 105.26 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 109.91 | -4.65
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07431 | 104.67 | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 101.18 | 3.49
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.0727 | 104.67 | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | Internal | 101.18 | 3.49
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01058 | 184.32 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 183.14 | 1.18
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01168 | 184.32 | 300097 5MARYVL 161 541251 MARYVLE5 161 1: 300097 5MARYVL 161 541251 MARYVLE5 161 1 | External | 183.14 | 1.18
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.0047 | 113 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 117 | -4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300694 5PALMYR_AI 161 347516 5MARBLE N 161 1 | 280 | 308 | 0.00462 | 113 | 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1: 345435 7MAYWOOD 345 347010 7HERLEMAN 345 1 | External | 117 | -4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00047 | 137.72 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 141.82 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00049 | 137.72 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 141.82 | -4.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.43 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.43 | 0
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.43 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.43 | 0
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 120.75 | Base Case | External | 119.46 | 1.29
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 120.75 | Base Case | External | 119.46 | 1.29
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.0014 | 100.68 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00141 | 100.68 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00387 | 114.89 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 115.04 | -0.15
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00403 | 114.89 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 115.04 | -0.15
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00044 | 120.21 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 120.97 | -0.76
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 120.21 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 120.97 | -0.76
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00385 | 175.73 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 177.9 | -2.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00401 | 175.73 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 177.9 | -2.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00012 | 103.38 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608654 AITKNMN7 115 618602 GRE-AITKIN 7 115 1 | 77 | 84.7 | 0.00013 | 103.38 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01245 | 112.67 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 111.93 | 0.74
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01281 | 112.67 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 111.93 | 0.74
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04914 | 108.49 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04979 | 108.49 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00217 | 107.83 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 106.77 | 1.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00225 | 107.83 | 631065 BVR CHN L1 5 161 629070 BVRCH52G 20 1: 631065 BVR CHN L1 5 161 629070 BVRCH52G 20.0 1 | External | 106.77 | 1.06
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 500 | 500 | 0.00275 | 104.35 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 104.45 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615306 GRE-PL VLLY3 345 997572 345-161 161 1 | 500 | 500 | 0.0029 | 104.35 | P13:345-161-13:XEL-GRE-GRE:AUTO-SINGLE:GRE-PLVLLY3:GRE-PLVLLY5:GRE-PLVLL2T:2 | External | 104.45 | -0.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 8e-05 | 123.37 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 117.5 | 5.87
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 9e-05 | 123.37 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 117.5 | 5.87
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00533 | 137.21 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.00649 | 137.21 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00411 | 109.54 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.0043 | 109.54 | P12:161:WAUW:# 3088 #: HV IN MT. HV-RY-TT LINE FAULT | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01375 | 103.97 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01457 | 103.97 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.28 | -2.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603103 SCOTTCO7 115 997636 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01103 | 111.95 | P23:345:XEL:8M57 SCO | External | 110.28 | 1.67
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603103 SCOTTCO7 115 997636 SCOTTCO3 115 9 | 648.9 | 648.9 | 0.01156 | 111.95 | P23:345:XEL:8M57 SCO | External | 110.28 | 1.67
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00406 | 109.15 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 106.59 | 2.56
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 302 | 332 | 0.00424 | 109.15 | P13:069-161:ITCM:LORE 5 T1:IA-NE | External | 106.59 | 2.56
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01625 | 145.71 | Base Case | External | 143.18 | 2.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01791 | 145.71 | Base Case | External | 143.18 | 2.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00099 | 143.52 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 652555 MORRIS 7 115 1 | 92 | 92 | 0.00102 | 143.52 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00012 | 107.11 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 108.85 | -1.74
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620214 BIGSTON7 115 620215 HIWY12 7 115 1 | 230 | 230 | 0.00012 | 107.11 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 108.85 | -1.74
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0071 | 111.16 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00692 | 111.16 | 92673: 515224 MUSKOGE7 345 515223 MUSKOG4G 18.0 1 515044 SEMINOL4 138 515040 SEMINL1G 20.9 1 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 515224 MUSKOGE7 345 515226 MUSKOG6G 24.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997741 NASHUA11 161 11 | 650 | 715 | 0.03003 | 114.75 | 104180: 542973 HAWTHS5 161 542997 LEEDS 5 161 1 542973 HAWTHS5 161 542997 LEEDS 5 161 2 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542973 HAWTHS5 161 543665 HAWTHN5 161 @1 542973 HAWTHS5 161 543665 HAWTHN5 161 @2 542973 HAWTHS5 161 548814 SUB M-161 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542973 HAWTHS5 161 543003 HAWTH_B2_1 13.2 1 542973 HAWTHS5 161 543005 HAWTH_B32_1 13.2 1 542973 HAWTHS5 161 543663 HAWT11_2 69.0 11 542973 HAWTHS5 161 543664 HAWT12_2 69.0 12 542976 LEVEE 5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 1 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 543665 HAWTHN5 161 997752 HAWTHORN20 161 20 543665 HAWTHN5 161 997751 HAWTHORN22 161 22 | Internal | 112.59 | 2.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00445 | 122.48 | P23:345:XEL:8S23 WLM | External | 123.04 | -0.56
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00475 | 122.48 | P23:345:XEL:8S23 WLM | External | 123.04 | -0.56
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00092 | 133.75 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.44 | 0.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00094 | 133.75 | P23:500:EES-EAI:WH_BLF:B7914 | External | 133.44 | 0.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03349 | 109.28 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636635 OAKGROV3 345 636640 SUB 93 3 345 1 | 1195 | 1209 | 0.03416 | 109.28 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1: 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | External | 110.55 | -1.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.17006 | 101.93 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.16849 | 101.93 | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 268.1 | 268.1 | 9e-05 | 101.57 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 103.95 | -2.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603099 RIVRSID7 115 603125 BRKLNPK7 115 1 | 268.1 | 268.1 | 0.00011 | 101.57 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 103.95 | -2.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01082 | 105.36 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.93 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.0108 | 105.36 | 92439: 300032 1CHOTCT1 16.0 300069 5CHOTEAU1 161 11 300033 1CHOTCT2 16.0 300069 5CHOTEAU1 161 12 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 103.93 | 1.43
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15039 | 122.56 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal | 117.31 | 5.25
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14922 | 122.56 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal | 117.31 | 5.25
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01465 | 129.72 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 130.22 | -0.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01427 | 129.72 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 130.22 | -0.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00043 | 120.07 | P23:345:AMMO::MONTGOMERY:V43 | External | 120.86 | -0.79
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 120.07 | P23:345:AMMO::MONTGOMERY:V43 | External | 120.86 | -0.79
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00257 | 139.14 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 138.65 | 0.49
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00265 | 139.14 | P13:161-69:ITCM:BVR CH5 T1:IA-EC | External | 138.65 | 0.49
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00579 | 122.36 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00594 | 122.36 | 631084 VIELE 5 161 631108 DENMARK5 161 1: 631084 VIELE 5 161 631108 DENMARK5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.05292 | 107.75 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 106.63 | 1.12
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.05219 | 107.75 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 106.63 | 1.12
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01225 | 118.09 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01293 | 118.09 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 133.63 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 131.82 | 1.81
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00386 | 133.63 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 131.82 | 1.81
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.02 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 124.81 | 0.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00221 | 125.02 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 124.81 | 0.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05748 | 109.63 | P23:345:WERE:STRA_345-99:: | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05657 | 109.63 | P23:345:WERE:STRA_345-99:: | Internal | 106.93 | 2.7
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 0.00012 | 102.1 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 103.66 | -1.56
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620215 HIWY12 7 115 620216 ORTONVL7 115 1 | 230 | 230 | 0.00012 | 102.1 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 103.66 | -1.56
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00251 | 111.64 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 110.47 | 1.17
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00254 | 111.64 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 110.47 | 1.17
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00132 | 140.81 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.36 | 0.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.0013 | 140.81 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.36 | 0.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.0004 | 110.34 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 111.1 | -0.76
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00042 | 110.34 | 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1: 615637 GRE-SILVRLK4 230 615902 GRE-HENNING4 230 1 | External | 111.1 | -0.76
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00032 | 108.75 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.53 | 0.22
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00033 | 108.75 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.53 | 0.22
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00406 | 137.49 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 138.52 | -1.03
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00418 | 137.49 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 138.52 | -1.03
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00033 | 130.87 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.73 | 0.14
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00033 | 130.87 | P23:500:EMI-EES:ABF_FRKLN-A | External | 130.73 | 0.14
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09 | 115.17 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09188 | 115.17 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.0112 | 119.74 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01165 | 119.74 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00132 | 140.81 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.36 | 0.45
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.0013 | 140.81 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 140.36 | 0.45
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00907 | 126.95 | Base Case | External | 126.23 | 0.72
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00951 | 126.95 | Base Case | External | 126.23 | 0.72
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00097 | 123.55 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 127.95 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00101 | 123.55 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 127.95 | -4.4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1099 | 1202 | 0.06356 | 110.56 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1099 | 1202 | 0.06266 | 110.56 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.15024 | 111.35 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 105.5 | 5.85
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.14906 | 111.35 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal | 105.5 | 5.85
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00216 | 120.82 | Base Case | External | 121.08 | -0.26
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00224 | 120.82 | Base Case | External | 121.08 | -0.26
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00566 | 115.62 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00603 | 115.62 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02385 | 100.16 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02411 | 100.16 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.0004 | 111.87 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 112.64 | -0.77
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 618203 GRE-TAMARAC7 115 618207 GRE-CORMRNT7 115 1 | 94.8 | 94.8 | 0.00042 | 111.87 | 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1: 615637 GRE-SILVRLK4 230 658109 FERGSFL4 230 1 | External | 112.64 | -0.77
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.0018 | 101.44 | P23:345:GRE:PVS 19JB4 | External | 105.51 | -4.07
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615307 GRE-PL VLLY5 161 997573 345-161 161 2 | 500 | 500 | 0.00206 | 101.44 | P23:345:GRE:PVS 19JB4 | External | 105.51 | -4.07
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00689 | 110.66 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.00717 | 110.66 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00829 | 109.73 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631159 HCKRYCK5 161 631191 HCKRYCK3 345 1 | 352 | 444 | 0.00866 | 109.73 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.84194 | 119.18 | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00653 | 114.84 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 115.16 | -0.32
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00667 | 114.84 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 115.16 | -0.32
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.09458 | 135.39 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 132.23 | 3.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.09368 | 135.39 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal | 132.23 | 3.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17264 | 120.69 | P42:345:NPPD:BKR-C-3322-2 | Internal | 113.04 | 7.65
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16925 | 120.69 | P42:345:NPPD:BKR-C-3322-2 | Internal | 113.04 | 7.65
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00105 | 121.94 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 120.44 | 1.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00113 | 121.94 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 120.44 | 1.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00383 | 115.4 | P23:345:XEL:8M38 CNC | External | 117.95 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601024 TERMINL3 345 1 | 1195.1 | 1195.1 | 0.00406 | 115.4 | P23:345:XEL:8M38 CNC | External | 117.95 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03165 | 116.66 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 112.58 | 4.08
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.0314 | 116.66 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 112.58 | 4.08
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603110 TERMINL7 115 997650 90198-B 115 10 | 672 | 734 | 0.0002 | 110.59 | P23:345:XEL:8P33 KOL | External | 112.8 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603110 TERMINL7 115 997650 90198-B 115 10 | 672 | 734 | 0.00024 | 110.59 | P23:345:XEL:8P33 KOL | External | 112.8 | -2.21
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04849 | 107.34 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04907 | 107.34 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00458 | 107.84 | P12:345:XEL:AUTO-SINGLE:COONCK3:TERMINL3:1 | External | 110.32 | -2.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00485 | 107.84 | P12:345:XEL:AUTO-SINGLE:COONCK3:TERMINL3:1 | External | 110.32 | -2.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01245 | 112.67 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 111.93 | 0.74
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01281 | 112.67 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 111.93 | 0.74
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0035 | 145.21 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 147.37 | -2.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00359 | 145.21 | 681521 SENECA 5 161 681525 GRANGRAE 161 1: 681521 SENECA 5 161 681525 GRANGRAE 161 1 | External | 147.37 | -2.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00116 | 102.41 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.35 | 0.06
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00115 | 102.41 | 92454: 547498 STL439 5 161 547658 S4G439 1 18.0 1 547498 STL439 5 161 547655 S1G439 1 13.2 1 547498 STL439 5 161 547657 S3G439 1 18.0 1 547498 STL439 5 161 547656 S2G439 1 18.0 1 300012 1HOLDNG1 13.8 300124 5HOLDEN 161 1 300013 1HOLDNG2 13.8 300124 5HOLDEN 161 2 300014 1HOLDNG3 13.8 300124 5HOLDEN 161 3 | External | 102.35 | 0.06
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.0354 | 107.37 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 102.21 | 5.16
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN20 161 20 | 500 | 550 | 0.03513 | 107.37 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 102.21 | 5.16
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00773 | 113.67 | P23:345:XEL:8S72 HNA | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | 276 | 276 | 0.00809 | 113.67 | P23:345:XEL:8S72 HNA | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00257 | 109.07 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 110.49 | -1.42
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00265 | 109.07 | 631017 PRAR CK7 115 631020 BERTRAM7 115 1: 631017 PRAR CK7 115 631020 BERTRAM7 115 1 | External | 110.49 | -1.42
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00032 | 101.46 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 103.41 | -1.95
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619941 HUC-MCLEOD 7 115 997512 230/115 115 1 | 187 | 187 | 0.00035 | 101.46 | 602014 BLUE LK4 230 3WXFMR BLUE LK4 7: 602014 BLUE LK4 230 997628 BLUE LK4 115 7 603062 BLUE LK7 115 997628 BLUE LK4 115 7 605721 BLUELK 9 13.8 997628 BLUE LK4 115 7 | External | 103.41 | -1.95
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00011 | 105.95 | Base Case | External | 100.35 | 5.6
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | 78 | 85.8 | 0.00012 | 105.95 | Base Case | External | 100.35 | 5.6
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00113 | 181.7 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 181.1 | 0.6
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00116 | 181.7 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 181.1 | 0.6
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00441 | 101.09 | Base Case | External | 103.68 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00452 | 101.09 | Base Case | External | 103.68 | -2.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02218 | 189.6 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 185.85 | 3.75
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02436 | 189.6 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 185.85 | 3.75
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00141 | 106.73 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 111.32 | -4.59
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00149 | 106.73 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 111.32 | -4.59
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00754 | 119.04 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 119.44 | -0.4
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.0073 | 119.04 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 119.44 | -0.4
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 117.69 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 117.23 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00212 | 117.69 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 117.23 | 0.46
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00044 | 145.92 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 147.78 | -1.86
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00045 | 145.92 | 93765: 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | External | 147.78 | -1.86
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00399 | 164.77 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 164.77 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00172 | 101.38 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 101.69 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603002 WILMART7 115 603188 EASTWD18 115 1 | 224.7 | 247.1 | 0.00182 | 101.38 | 603002 WILMART7 115 603186 SUMMIT 115 1: 603002 WILMART7 115 603186 SUMMIT 115 1 | External | 101.69 | -0.31
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04897 | 107.3 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04962 | 107.3 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01125 | 115.38 | P23:345:MEC:GDMEC 901 | External | 115.06 | 0.32
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01171 | 115.38 | P23:345:MEC:GDMEC 901 | External | 115.06 | 0.32
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00251 | 105.86 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 104.71 | 1.15
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | 225 | 225 | 0.00254 | 105.86 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 104.71 | 1.15
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02312 | 115.46 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | External | 111.55 | 3.91
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02314 | 115.46 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | External | 111.55 | 3.91
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00012 | 115.66 | P13:138-115:MP:TCH:TR4(1) | External | 110.27 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00013 | 115.66 | P13:138-115:MP:TCH:TR4(1) | External | 110.27 | 5.39
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04849 | 121.54 | Base Case | External | 120.28 | 1.26
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04907 | 121.54 | Base Case | External | 120.28 | 1.26
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00017 | 103.8 | P12:230:MP-XEL:BRC-RCR | External | 102.69 | 1.11
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 144 | 144 | 0.00018 | 103.8 | P12:230:MP-XEL:BRC-RCR | External | 102.69 | 1.11
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 8e-05 | 139.12 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 133.01 | 6.11
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 9e-05 | 139.12 | 608662 SAVANNA7 115 608663 FLDWDTP7 115 1: 608662 SAVANNA7 115 608663 FLDWDTP7 115 1 | External | 133.01 | 6.11
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00012 | 120.72 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 116.19 | 4.53
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | 78 | 78 | 0.00013 | 120.72 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 116.19 | 4.53
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608616 HILLTOP4 230 997593 HIL1 115 1 | 187 | 233 | 0.00022 | 121.39 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 114.25 | 7.14
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608616 HILLTOP4 230 997593 HIL1 115 1 | 187 | 233 | 0.00024 | 121.39 | 608614 98L TAP4 230 608615 ARROWHD4 230 1: 608614 98L TAP4 230 608615 ARROWHD4 230 1 | External | 114.25 | 7.14
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00049 | 160.29 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00053 | 160.29 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00988 | 129.68 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 131.6 | -1.92
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01038 | 129.68 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 131.6 | -1.92
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0288 | 107.02 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02927 | 107.02 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 112 | 112 | 0.00065 | 126.07 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631038 MAGNLIA5 161 631182 ELK L1 5 161 1 | 112 | 112 | 0.00069 | 126.07 | P24:345:ITCM:LAKEFLD 885 FUT:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01172 | 119.85 | P23:345:MEC:GDMEC 902 | External | 119.46 | 0.39
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01221 | 119.85 | P23:345:MEC:GDMEC 902 | External | 119.46 | 0.39
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.0007 | 130.8 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 130.98 | -0.18
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00073 | 130.8 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 130.98 | -0.18
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00326 | 131.69 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 132.79 | -1.1
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00333 | 131.69 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 132.79 | -1.1
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00171 | 105.67 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615529 GRE-PANTHER4 230 619940 HUC-MCLEOD 4 230 1 | 321.9 | 321.9 | 0.00181 | 105.67 | 601050 HELENA 3 345 601055 SCOTTCO3 345 1: 601050 HELENA 3 345 601055 SCOTTCO3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.76 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.76 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00479 | 136.65 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00491 | 136.65 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00014 | 105.92 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1 | External | 106.27 | -0.35
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608614 98L TAP4 230 608622 IRONRNG4 230 1 | 470.5 | 517.5 | 0.00019 | 105.92 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1 | External | 106.27 | -0.35
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01239 | 110.78 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 110.09 | 0.69
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01275 | 110.78 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 110.09 | 0.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00012 | 121.62 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 117.1 | 4.52
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00013 | 121.62 | 71586: 608695 NUGGET 7 115 608700 43L TAP7 115 1 608698 HOYT LK7 115 608700 43L TAP7 115 1 608700 43L TAP7 115 608702 LASKIN 7 115 1 603181 MNRIVER7 115 600019 MNRIVRG1 13.8 1 603103 SCOTTCO7 115 603181 MNRIVER7 115 1 603181 MNRIVER7 115 618700 GRE-CHANHAS7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 1 603114 WSTGATE7 115 603115 BLUFFCK7 115 2 603115 BLUFFCK7 115 603287 LK HAZLTNE7 115 1 603115 BLUFFCK7 115 618700 GRE-CHANHAS7 115 1 606059 BLFFCRK 8 69.0 603115 BLUFFCK7 115 1 | External | 117.1 | 4.52
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00448 | 108.16 | P23:345:XEL:8M35 CNC | External | 110.6 | -2.44
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601019 COON CK3 345 601021 KOLMNLK3 345 1 | 1195.1 | 1195.1 | 0.00474 | 108.16 | P23:345:XEL:8M35 CNC | External | 110.6 | -2.44
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00406 | 138.72 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 140.1 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00418 | 138.72 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 140.1 | -1.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00257 | 138.93 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 138.45 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00265 | 138.93 | 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1: 631064 BVR CHN L2 5 161 631067 ALBANY 5 161 1 | External | 138.45 | 0.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00272 | 106.37 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631060 TRK RIV5 161 1 | 330 | 330 | 0.00275 | 106.37 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00025 | 100.7 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 619982 WMU-PRIAM 7 115 997509 115/69 69.0 1 | 95.6 | 95.6 | 0.00027 | 100.7 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-WILLMAR4:GRANITF4:1 | External | 101.79 | -1.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.02218 | 107.5 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 104.2 | 3.3
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.02436 | 107.5 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 104.2 | 3.3
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03266 | 105.47 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.69 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03222 | 105.47 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 103.69 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01009 | 128.62 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00978 | 128.62 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.55 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998887 HGT X1 69.0 1 | 100 | 112 | 5e-05 | 121.55 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.22 | 0.33
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 263.7 | 263.7 | 0.0011 | 108.73 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 107.95 | 0.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615328 GRE-BUNKER 4 230 615377 GRE-BLAINE 4 230 1 | 263.7 | 263.7 | 0.00116 | 108.73 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 107.95 | 0.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17137 | 121.74 | P42:345:NPPD:BKR-CPR-3322 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16754 | 121.74 | P42:345:NPPD:BKR-CPR-3322 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00566 | 115.62 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631088 ARNOLD 5 161 631188 DWNTWN IND5 161 1 | 326 | 326 | 0.00603 | 115.62 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1 | External | 119.03 | -3.41
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00387 | 113.8 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 113.71 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 275 | 291 | 0.00403 | 113.8 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1 | External | 113.71 | 0.09
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03063 | 107.32 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal | 102.6 | 4.72
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01237 | 146.62 | P23:345:MEC:GDMEC 902 | External | 146.12 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01289 | 146.62 | P23:345:MEC:GDMEC 902 | External | 146.12 | 0.5
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00482 | 115.56 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997677 ADAMS 3 161 9 | 300 | 334.6 | 0.00525 | 115.56 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 121.1 | -5.54
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.00123 | 102.26 | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | External | 101.98 | 0.28
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300364 2NOVLTY_SW 69.0 300106 5NOVELY_SW 161 1 | 56 | 56 | 0.0013 | 102.26 | 300106 5NOVELY_SW 161 300363 5NEWARK 161 1: 300106 5NOVELY_SW 161 300363 5NEWARK 161 1 | External | 101.98 | 0.28
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00768 | 166.54 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00835 | 166.54 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.17139 | 121.4 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.16758 | 121.4 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.21 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998886 HGT X2 69.0 1 | 100 | 112 | 5e-05 | 121.21 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 120.87 | 0.34
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01009 | 127.04 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00978 | 127.04 | 104740: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 532854 LEC U5 6 230 532663 LEC U5 24.0 1 533249 LEC U4 3 115 532662 LEC U4 14.4 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00653 | 114.58 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 114.78 | -0.2
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00667 | 114.58 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 114.78 | -0.2
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 122.77 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 122.75 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 122.77 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 122.75 | 0.02
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300194 2CHILLI 69.0 300068 5CHILLI 161 2 | 56 | 56 | 0.00056 | 106.02 | 300194 2CHILLI 69 300068 5CHILLI 161 1: 300194 2CHILLI 69.0 300068 5CHILLI 161 1 | External | 105.76 | 0.26
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300194 2CHILLI 69.0 300068 5CHILLI 161 2 | 56 | 56 | 0.00057 | 106.02 | 300194 2CHILLI 69 300068 5CHILLI 161 1: 300194 2CHILLI 69.0 300068 5CHILLI 161 1 | External | 105.76 | 0.26
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01107 | 163.75 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 165.38 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01164 | 163.75 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 165.38 | -1.63
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00248 | 130.55 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.28 | 0.27
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 56 | 56 | 0.00242 | 130.55 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 130.28 | 0.27
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 314 | 314 | 0.00996 | 106.53 | P23:345:MEC:OAK GROVE 901 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636616 SB 56 5 161 636675 SB 85 5 161 1 | 314 | 314 | 0.01027 | 106.53 | P23:345:MEC:OAK GROVE 901 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.0188 | 114.02 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 113.41 | 0.61
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997472 WEB AB 161 1 | 560 | 560 | 0.01956 | 114.02 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 113.41 | 0.61
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00226 | 129.23 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00234 | 129.23 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04914 | 108.46 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04979 | 108.46 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00482 | 127.8 | P23:345:MEC:GDMEC 901 | External | 129.16 | -1.36
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00494 | 127.8 | P23:345:MEC:GDMEC 901 | External | 129.16 | -1.36
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06595 | 123.7 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.06508 | 123.7 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00015 | 156.01 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 151.29 | 4.72
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | 78 | 78 | 0.00016 | 156.01 | 608614 98L TAP4 230 608622 IRONRNG4 230 1: 608614 98L TAP4 230 608622 IRONRNG4 230 1 | External | 151.29 | 4.72
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 608700 43L TAP7 115 608702 LASKIN 7 115 1 | 144 | 158.4 | 0.00012 | 101.68 | Base Case | External | 100.66 | 1.02
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 608700 43L TAP7 115 608702 LASKIN 7 115 1 | 144 | 158.4 | 0.00012 | 101.68 | Base Case | External | 100.66 | 1.02
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.0123 | 103.78 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01274 | 103.78 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00307 | 105.05 | P12:161:DPC:AUTO-SINGLE:GENOA5:HARMONY5:1 | External | 103.13 | 1.92
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631052 LANSING L1 5 161 681523 GENOA 5 161 1 | 240 | 264 | 0.00316 | 105.05 | P12:161:DPC:AUTO-SINGLE:GENOA5:HARMONY5:1 | External | 103.13 | 1.92
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00553 | 100.16 | P23:345:XEL:8S50 HMP | External | 100.2 | -0.04
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615650 GRE-CHUBLAK7 115 997517 CHL345-115-1 115 1 | 448 | 448 | 0.00582 | 100.16 | P23:345:XEL:8S50 HMP | External | 100.2 | -0.04
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00024 | 103.79 | P11:024:DPC:ALMA2:6 | External | 105.73 | -1.94
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00025 | 103.79 | P11:024:DPC:ALMA2:6 | External | 105.73 | -1.94
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 3e-05 | 104.76 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661018 COYOTE 7 115 661021 WSTMD1 7 115 1 | 102 | 102 | 7e-05 | 104.76 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 105.37 | -0.61
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00834 | 112.32 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300113 5SRIVER 161 300339 5EMERSN 161 1 | 172 | 172 | 0.00848 | 112.32 | P23:345:AMMO::ZACHARY:2 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14492 | 137.48 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 157.17 | -19.69
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01225 | 118.09 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01293 | 118.09 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 120.64 | -2.55
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00023 | 100.27 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 100.65 | -0.38
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630004 BVR CHN J1 8 69.0 631065 BVR CHN L1 5 161 1 | 123 | 123 | 0.00024 | 100.27 | 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1: 631064 BVR CHN L2 5 161 631065 BVR CHN L1 5 161 1 | External | 100.65 | -0.38
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 101.06 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.7 | 0.36
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 101.06 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.7 | 0.36
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.0043 | 112.82 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 113.46 | -0.64
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | 223 | 223 | 0.00411 | 112.82 | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z: 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | External | 113.46 | -0.64
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00141 | 107.58 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 112.06 | -4.48
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603289 BAILEY RD7 115 680265 GLENMONT 115 1 | 214.1 | 214.1 | 0.00149 | 107.58 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 112.06 | -4.48
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.038 | 121.92 | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 120.14 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997741 NASHUA11 161 11 | 650 | 715 | 0.03746 | 121.92 | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 120.14 | 1.78
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03123 | 116.09 | 104247: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 112.08 | 4.01
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997746 HAWTHORN22 161 22 | 550 | 605 | 0.03097 | 116.09 | 104247: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542976 LEVEE 5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 112.08 | 4.01
Thermal | 00NR | S2 | 24SP0 | GEN_025_028 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00099 | 149.18 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 00NR | S2 | 24SP0 | GEN_043_044_045 | FROM -> TO | 616002 GRE-JOHNJCT7 115 620216 ORTONVL7 115 1 | 108 | 108 | 0.00102 | 149.18 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02763 | 121.52 | P23:345:MEC:GDMEC 902 | External | 116.1 | 5.42
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02806 | 121.52 | P23:345:MEC:GDMEC 902 | External | 116.1 | 5.42
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.0011 | 130.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.6 | -0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00112 | 130.5 | P23:500:EES-EAI:WH_BLF:B7914 | External | 130.6 | -0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06832 | 127.25 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 123.98 | 3.27
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06956 | 127.25 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 123.98 | 3.27
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08565 | 130.91 | Base Case | External | 124.75 | 6.16
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08746 | 130.91 | Base Case | External | 124.75 | 6.16
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02069 | 107.58 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 101.24 | 6.34
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02153 | 107.58 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 101.24 | 6.34
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01668 | 118.94 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 113.74 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01703 | 118.94 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 113.74 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00069 | 122.13 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0007 | 122.13 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07797 | 145.02 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 131 | 14.02
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07749 | 145.02 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 131 | 14.02
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00095 | 128.57 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.62 | -0.05
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00097 | 128.57 | P23:500:EES-EAI:WH_BLF:B7914 | External | 128.62 | -0.05
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02941 | 132.28 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 121.53 | 10.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.0293 | 132.28 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 121.53 | 10.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00252 | 102.67 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 102.67 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00078 | 141.08 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 140.92 | 0.16
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00079 | 141.08 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 140.92 | 0.16
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05381 | 108.22 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05672 | 108.22 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.0532 | 122.37 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 111.09 | 11.28
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.05286 | 122.37 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 111.09 | 11.28
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01127 | 118.37 | P23:345:MEC:GDMEC 901 | External | 114.2 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01176 | 118.37 | P23:345:MEC:GDMEC 901 | External | 114.2 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01017 | 165.91 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01062 | 165.91 | P21:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0119 | 100.48 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01165 | 100.48 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02753 | 116.04 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.44 | 9.6
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02745 | 116.04 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.44 | 9.6
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00042 | 105.42 | P12:230:EES:TEZCUC:WATERF:1 | External | 105.34 | 0.08
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00043 | 105.42 | P12:230:EES:TEZCUC:WATERF:1 | External | 105.34 | 0.08
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00096 | 145.23 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 143.6 | 1.63
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00102 | 145.23 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 143.6 | 1.63
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02989 | 130.81 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 125.46 | 5.35
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.03033 | 130.81 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 125.46 | 5.35
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02069 | 105.45 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02153 | 105.45 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 102.91 | Base Case | External | 102.41 | 0.5
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 4e-05 | 102.91 | Base Case | External | 102.41 | 0.5
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00397 | 115.24 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 110.37 | 4.87
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00407 | 115.24 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 110.37 | 4.87
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01711 | 103.95 | P24:345:AMMO::MCCREDIE:1 | External | 101.19 | 2.76
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01644 | 103.95 | P24:345:AMMO::MCCREDIE:1 | External | 101.19 | 2.76
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 2e-05 | 132.35 | 608614 98L TAP4 230 608616 HILLTOP4 230 1: 608614 98L TAP4 230 608616 HILLTOP4 230 1 | External | 131.92 | 0.43
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 132.35 | 608614 98L TAP4 230 608616 HILLTOP4 230 1: 608614 98L TAP4 230 608616 HILLTOP4 230 1 | External | 131.92 | 0.43
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00146 | 125.32 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 124.18 | 1.14
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00149 | 125.32 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 124.18 | 1.14
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 109.66 | P13:230:EES:WATERF:T6:T7 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 4e-05 | 109.66 | P13:230:EES:WATERF:T6:T7 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01717 | 118.42 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 111.33 | 7.09
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0168 | 118.42 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 111.33 | 7.09
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.02753 | 112.38 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 102.23 | 10.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.02745 | 112.38 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 102.23 | 10.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06439 | 127.81 | P23:345:AMMO::ZACHARY:1 | External | 124.88 | 2.93
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06549 | 127.81 | P23:345:AMMO::ZACHARY:1 | External | 124.88 | 2.93
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01187 | 140.47 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 136.13 | 4.34
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01237 | 140.47 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 136.13 | 4.34
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 523961 POTTER_CO 7 345 998118 WAUK 90343-A 230 1 | 516 | 559 | 0.03009 | 103.24 | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | Internal
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01672 | 119.24 | P23:345:MEC:GDMEC 901 | External | 114.01 | 5.23
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01707 | 119.24 | P23:345:MEC:GDMEC 901 | External | 114.01 | 5.23
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01189 | 100.06 | P23:345:MEC:GDMEC 902 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01163 | 100.06 | P23:345:MEC:GDMEC 902 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01672 | 119.24 | P23:345:MEC:GDMEC 902 | External | 114.01 | 5.23
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01707 | 119.24 | P23:345:MEC:GDMEC 902 | External | 114.01 | 5.23
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.02753 | 109.22 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.02745 | 109.22 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01677 | 102.26 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01645 | 102.26 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05381 | 108.22 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05672 | 108.22 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00656 | 107.12 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 103.74 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.007 | 107.12 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 103.74 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00997 | 127.05 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 123.03 | 4.02
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01051 | 127.05 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 123.03 | 4.02
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02428 | 106.86 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 102.47 | 4.39
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02445 | 106.86 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 102.47 | 4.39
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03769 | 139.91 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 132.96 | 6.95
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03892 | 139.91 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 132.96 | 6.95
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00067 | 107.22 | P12:230:EES:IRONMN:L_GPSY:1 | External | 107.07 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00068 | 107.22 | P12:230:EES:IRONMN:L_GPSY:1 | External | 107.07 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.02991 | 113.91 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 104.29 | 9.62
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.03125 | 113.91 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 104.29 | 9.62
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08297 | 111.26 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 106.44 | 4.82
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08473 | 111.26 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 106.44 | 4.82
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04796 | 109.49 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 107.28 | 2.21
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04854 | 109.49 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 107.28 | 2.21
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00252 | 102.67 | P23:345:MEC:HILLS 934 | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 102.67 | P23:345:MEC:HILLS 934 | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01207 | 122.2 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 118.82 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.0122 | 122.2 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 118.82 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08565 | 126.74 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 121.8 | 4.94
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08746 | 126.74 | 92467: 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | External | 121.8 | 4.94
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00875 | 114.43 | Base Case | External | 110.9 | 3.53
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00919 | 114.43 | Base Case | External | 110.9 | 3.53
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06979 | 102.47 | P23:345:MEC:GRIMES 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07175 | 102.47 | P23:345:MEC:GRIMES 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01851 | 100.7 | P42:345:NPPD:BKR-C-3322-2 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01941 | 100.7 | P42:345:NPPD:BKR-C-3322-2 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01663 | 120.36 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.53 | 4.83
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01696 | 120.36 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.53 | 4.83
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.0112 | 112.01 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 106.66 | 5.35
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01164 | 112.01 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 106.66 | 5.35
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00996 | 126.8 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 122.78 | 4.02
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01049 | 126.8 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 122.78 | 4.02
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01191 | 138.63 | P23:345:MEC:GDMEC 901 | External | 132.12 | 6.51
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01242 | 138.63 | P23:345:MEC:GDMEC 901 | External | 132.12 | 6.51
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00065 | 101.43 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 101.28 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336064 6ROMEVL! 230 336065 6CONVNT! 230 1 | 405 | 405 | 0.00066 | 101.43 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 101.28 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06439 | 125.98 | P23:345:AMMO::ZACHARY:1 | External | 122.6 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06549 | 125.98 | P23:345:AMMO::ZACHARY:1 | External | 122.6 | 3.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 9e-05 | 120.8 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.78 | 0.02
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 9e-05 | 120.8 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.78 | 0.02
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.03422 | 126.34 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 110.85 | 15.49
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.03586 | 126.34 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 110.85 | 15.49
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07797 | 147.99 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 133.24 | 14.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07749 | 147.99 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 133.24 | 14.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00252 | 102.51 | P23:345:MEC:LOUISA 954 | External | 100.17 | 2.34
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 102.51 | P23:345:MEC:LOUISA 954 | External | 100.17 | 2.34
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.8408 | 111.46 | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00078 | 123.32 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 123.17 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336069 6TEZCUCO% 230 336189 6IRONMAN% 230 1 | 519 | 519 | 0.00079 | 123.32 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 123.17 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06832 | 127.25 | P23:345:MEC:MONTEZUMA 902 | External | 123.98 | 3.27
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06956 | 127.25 | P23:345:MEC:MONTEZUMA 902 | External | 123.98 | 3.27
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08129 | 110.06 | P13:161:MEC:NORWALK 9T1 | External | 105.31 | 4.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08296 | 110.06 | P13:161:MEC:NORWALK 9T1 | External | 105.31 | 4.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0265 | 120.31 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02715 | 120.31 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06372 | 128.69 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 125.82 | 2.87
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06483 | 128.69 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 125.82 | 2.87
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01677 | 102.26 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300068 5CHILLI 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01645 | 102.26 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02779 | 123.28 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 117.68 | 5.6
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02825 | 123.28 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 117.68 | 5.6
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01717 | 118.42 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 111.33 | 7.09
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.0168 | 118.42 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 111.33 | 7.09
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.0603 | 235.82 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 226.5 | 9.32
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.06181 | 235.82 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 226.5 | 9.32
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08209 | 102.46 | P23:345:MEC:GDMEC 903 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08395 | 102.46 | P23:345:MEC:GDMEC 903 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13117 | 110.89 | P42:345:NPPD:BKR-C-3322-2 | Internal | 100.9 | 9.99
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12778 | 110.89 | P42:345:NPPD:BKR-C-3322-2 | Internal | 100.9 | 9.99
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.0532 | 141.79 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 128.85 | 12.94
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.05286 | 141.79 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 128.85 | 12.94
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13024 | 112.58 | P42:345:NPPD:BKR-CPR-3322 | Internal | 102.84 | 9.74
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12641 | 112.58 | P42:345:NPPD:BKR-CPR-3322 | Internal | 102.84 | 9.74
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 109.66 | P11:25:EES:WATERF:1 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 4e-05 | 109.66 | P11:25:EES:WATERF:1 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01017 | 165.91 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01062 | 165.91 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.03815 | 116.73 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 100.67 | 16.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.03995 | 116.73 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 100.67 | 16.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00408 | 101.76 | P13:161-345:ALTW:AUTO-SINGLE:HUNTLEY5:HUNTLEY3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00435 | 101.76 | P13:161-345:ALTW:AUTO-SINGLE:HUNTLEY5:HUNTLEY3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01124 | 120.1 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.93 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01171 | 120.1 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.93 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03769 | 138.89 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 132.01 | 6.88
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03892 | 138.89 | 631115 OTTUMWA5 161 629075 OTTUMW1G 24 1: 631115 OTTUMWA5 161 629075 OTTUMW1G 24.0 1 | External | 132.01 | 6.88
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0227 | 100.26 | P23:345:MEC:GDMEC 902 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02287 | 100.26 | P23:345:MEC:GDMEC 902 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 106.41 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00555 | 106.41 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01532 | 112 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 105.93 | 6.07
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01495 | 112 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 105.93 | 6.07
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01006 | 100.94 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01058 | 100.94 | P21:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02313 | 104.8 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 100.07 | 4.73
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02338 | 104.8 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 100.07 | 4.73
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 523959 POTTER_CO 6 230 998118 WAUK 90343-A 230 1 | 516 | 559 | 0.03009 | 105.28 | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | Internal
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.0532 | 141.79 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 128.85 | 12.94
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.05286 | 141.79 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 128.85 | 12.94
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02337 | 110.01 | P23:345:MEC:SYCAMORE 905 | External | 106 | 4.01
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02379 | 110.01 | P23:345:MEC:SYCAMORE 905 | External | 106 | 4.01
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00396 | 107.95 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 105.38 | 2.57
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00414 | 107.95 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 105.38 | 2.57
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04796 | 109.32 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 107.65 | 1.67
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04854 | 109.32 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 107.65 | 1.67
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00465 | 102.88 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 100.06 | 2.82
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00477 | 102.88 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 100.06 | 2.82
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00397 | 102.62 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00407 | 102.62 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 335 | 335 | 0.02047 | 103.97 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 335 | 335 | 0.02108 | 103.97 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 2e-05 | 132.26 | 608616 HILLTOP4 230 3WXFMR HIL1 1: 608616 HILLTOP4 230 997598 HIL1 115 1 608672 HILLTOP7 115 997598 HIL1 115 1 608577 HILTPTR9 13.8 997598 HIL1 115 1 | External | 131.83 | 0.43
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 132.26 | 608616 HILLTOP4 230 3WXFMR HIL1 1: 608616 HILLTOP4 230 997598 HIL1 115 1 608672 HILLTOP7 115 997598 HIL1 115 1 608577 HILTPTR9 13.8 997598 HIL1 115 1 | External | 131.83 | 0.43
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02313 | 104.8 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 100.07 | 4.73
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02338 | 104.8 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 100.07 | 4.73
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00108 | 113.18 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 112.43 | 0.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00111 | 113.18 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 112.43 | 0.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05381 | 108.22 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05672 | 108.22 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 103.16 | 5.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00046 | 104.73 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 104.63 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00047 | 104.73 | 336066 6FRISCO! 230 336067 6DUTBYU% 230 1: 336066 6FRISCO! 230 336067 6DUTBYU% 230 1 | External | 104.63 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00951 | 141.69 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 137.65 | 4.04
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01001 | 141.69 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 137.65 | 4.04
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00063 | 113.81 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 112.75 | 1.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00067 | 113.81 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 112.75 | 1.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01058 | 148.32 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 141.92 | 6.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01114 | 148.32 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 141.92 | 6.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09988 | 130.9 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 125.32 | 5.58
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10143 | 130.9 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 125.32 | 5.58
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04796 | 106.22 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 104.04 | 2.18
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04854 | 106.22 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 104.04 | 2.18
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00466 | 112.92 | P23:345:MEC:GDMEC 902 | External | 109.02 | 3.9
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00478 | 112.92 | P23:345:MEC:GDMEC 902 | External | 109.02 | 3.9
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00397 | 101.73 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00407 | 101.73 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.02688 | 106.25 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.02681 | 106.25 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02763 | 121.52 | P23:345:MEC:GDMEC 901 | External | 116.1 | 5.42
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02806 | 121.52 | P23:345:MEC:GDMEC 901 | External | 116.1 | 5.42
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 118.83 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00446 | 118.83 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10765 | 128.65 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 122.93 | 5.72
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.11012 | 128.65 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 122.93 | 5.72
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.0019 | 101.69 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00196 | 101.69 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.02753 | 109.22 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.02745 | 109.22 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10519 | 137.83 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 130.99 | 6.84
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10642 | 137.83 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External | 130.99 | 6.84
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01852 | 100.67 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.01941 | 100.67 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03769 | 138.89 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 132.01 | 6.88
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03892 | 138.89 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | External | 132.01 | 6.88
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00335 | 106.03 | P23:345:ALTW:MITCHLCO:1160 | External | 104.41 | 1.62
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00358 | 106.03 | P23:345:ALTW:MITCHLCO:1160 | External | 104.41 | 1.62
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00078 | 144.73 | P12:161:DPC:RCE-HAR5 | External | 143.3 | 1.43
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00083 | 144.73 | P12:161:DPC:RCE-HAR5 | External | 143.3 | 1.43
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01088 | 135.14 | P23:345:MEC:GDMEC 901 | External | 130.92 | 4.22
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01135 | 135.14 | P23:345:MEC:GDMEC 901 | External | 130.92 | 4.22
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09988 | 130.9 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 125.32 | 5.58
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10143 | 130.9 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 125.32 | 5.58
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00335 | 105.02 | P23:345:ALTW:MITCHLCO:1150 | External | 103.41 | 1.61
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00358 | 105.02 | P23:345:ALTW:MITCHLCO:1150 | External | 103.41 | 1.61
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 118.83 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00446 | 118.83 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 106.31 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 103.98 | 2.33
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00036 | 106.31 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 103.98 | 2.33
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0265 | 120.31 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02715 | 120.31 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.0532 | 122.37 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 111.09 | 11.28
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.05286 | 122.37 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 111.09 | 11.28
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00146 | 125.32 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 124.18 | 1.14
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00149 | 125.32 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 124.18 | 1.14
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04796 | 110.06 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 108.22 | 1.84
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04854 | 110.06 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 108.22 | 1.84
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02645 | 120.31 | P23:345:MEC:GDMEC 901 | External | 115.69 | 4.62
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02709 | 120.31 | P23:345:MEC:GDMEC 901 | External | 115.69 | 4.62
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00419 | 106.91 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 104.66 | 2.25
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00448 | 106.91 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP | External | 104.66 | 2.25
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04796 | 102.43 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 100.61 | 1.82
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04854 | 102.43 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 100.61 | 1.82
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01189 | 100.06 | P23:345:MEC:GDMEC 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01163 | 100.06 | P23:345:MEC:GDMEC 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00069 | 122.13 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0007 | 122.13 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0115 | 131.99 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 127.1 | 4.89
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01208 | 131.99 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 127.1 | 4.89
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07797 | 145.02 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 131 | 14.02
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541401 EASTOWN5 161 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07749 | 145.02 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 131 | 14.02
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04796 | 125.6 | Base Case | External | 122.85 | 2.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04854 | 125.6 | Base Case | External | 122.85 | 2.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00069 | 122.13 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0007 | 122.13 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03815 | 141.72 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal | 124.36 | 17.36
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03995 | 141.72 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal | 124.36 | 17.36
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08565 | 130.05 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 124.65 | 5.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.08746 | 130.05 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 124.65 | 5.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 602021 EAU CLA5 161 997646 EAU CL 3 161 9 | 300 | 334.6 | 0.00237 | 108.17 | P23:345:XEL:8E5 ECL BS | External | 103.23 | 4.94
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 602021 EAU CLA5 161 997646 EAU CL 3 161 9 | 300 | 334.6 | 0.00257 | 108.17 | P23:345:XEL:8E5 ECL BS | External | 103.23 | 4.94
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.02991 | 105.19 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.03125 | 105.19 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00949 | 141.37 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 137.34 | 4.03
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00999 | 141.37 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 137.34 | 4.03
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04796 | 126.6 | Base Case | External | 124.17 | 2.43
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04854 | 126.6 | Base Case | External | 124.17 | 2.43
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02781 | 125.86 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 120.6 | 5.26
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02829 | 125.86 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 120.6 | 5.26
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01127 | 118.37 | P23:345:MEC:GDMEC 902 | External | 114.2 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01176 | 118.37 | P23:345:MEC:GDMEC 902 | External | 114.2 | 4.17
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00042 | 105.42 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 105.34 | 0.08
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00043 | 105.42 | 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 | External | 105.34 | 0.08
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.0532 | 139.77 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 127.05 | 12.72
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.05286 | 139.77 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 127.05 | 12.72
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00078 | 130.92 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 129.45 | 1.47
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00083 | 130.92 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 129.45 | 1.47
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.01014 | 154.24 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 150.16 | 4.08
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.0106 | 154.24 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 150.16 | 4.08
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00097 | 131.02 | P23:500:EES-EAI:WH_BLF:B7914 | External | 131.08 | -0.06
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00098 | 131.02 | P23:500:EES-EAI:WH_BLF:B7914 | External | 131.08 | -0.06
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00465 | 116.56 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 113.27 | 3.29
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00477 | 116.56 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 113.27 | 3.29
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03422 | 150.54 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 135.16 | 15.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03586 | 150.54 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 135.16 | 15.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00355 | 107.97 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 106.07 | 1.9
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00372 | 107.97 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 106.07 | 1.9
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82835 | 140 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 601028 EAU CL 3 345 997646 EAU CL 3 161 9 | 300 | 334.6 | 0.00237 | 105.12 | P23:345:XEL:8E5 ECL BS | External | 101.29 | 3.83
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 601028 EAU CL 3 345 997646 EAU CL 3 161 9 | 300 | 334.6 | 0.00257 | 105.12 | P23:345:XEL:8E5 ECL BS | External | 101.29 | 3.83
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00069 | 122.13 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.0007 | 122.13 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00069 | 122.13 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0007 | 122.13 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02941 | 132.28 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 121.53 | 10.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.0293 | 132.28 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 121.53 | 10.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00393 | 113.58 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 109.53 | 4.05
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00404 | 113.58 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 109.53 | 4.05
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02655 | 122.77 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 118.12 | 4.65
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02723 | 122.77 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 118.12 | 4.65
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00335 | 103.82 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 102.23 | 1.59
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00358 | 103.82 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 102.23 | 1.59
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.0603 | 207.63 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 200.93 | 6.7
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.06181 | 207.63 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 200.93 | 6.7
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00457 | 100.39 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 347840 5NIOTA 161 631216 WEVER5 161 1 | 175 | 175 | 0.00468 | 100.39 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02991 | 116.94 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 106.43 | 10.51
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.03125 | 116.94 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 106.43 | 10.51
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00252 | 102.67 | P22:345:MEC:SUB 92 | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0026 | 102.67 | P22:345:MEC:SUB 92 | External | 100.29 | 2.38
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01085 | 145.89 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 141.05 | 4.84
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01139 | 145.89 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 141.05 | 4.84
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08209 | 102.46 | P23:345:MEC:GDMEC 904 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08395 | 102.46 | P23:345:MEC:GDMEC 904 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08165 | 111.32 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 106.54 | 4.78
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08336 | 111.32 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 106.54 | 4.78
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.0603 | 235.29 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 226.37 | 8.92
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.06181 | 235.29 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 226.37 | 8.92
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.02753 | 112.38 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 102.23 | 10.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.02745 | 112.38 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 102.23 | 10.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00422 | 118.83 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00446 | 118.83 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 116.43 | 2.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07797 | 147.99 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 133.24 | 14.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 997756 EASTOWNE11 161 11 | 400 | 440 | 0.07749 | 147.99 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 133.24 | 14.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.03584 | 111.01 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.03755 | 111.01 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00069 | 122.13 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.0007 | 122.13 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 122.03 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02332 | 100.84 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02328 | 100.84 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 6e-05 | 136.05 | 608665 THOMSON7 115 608667 POTLTCH7 115 1: 608665 THOMSON7 115 608667 POTLTCH7 115 1 | External | 135.43 | 0.62
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 8e-05 | 136.05 | 608665 THOMSON7 115 608667 POTLTCH7 115 1: 608665 THOMSON7 115 608667 POTLTCH7 115 1 | External | 135.43 | 0.62
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00798 | 114.28 | Base Case | External | 110.96 | 3.32
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.00838 | 114.28 | Base Case | External | 110.96 | 3.32
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.03897 | 100.57 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.04067 | 100.57 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00396 | 107.95 | P21:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 105.38 | 2.57
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00414 | 107.95 | P21:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 105.38 | 2.57
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.0532 | 139.77 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 127.05 | 12.72
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.05286 | 139.77 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 127.05 | 12.72
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01191 | 138.63 | P23:345:MEC:GDMEC 902 | External | 132.12 | 6.51
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01242 | 138.63 | P23:345:MEC:GDMEC 902 | External | 132.12 | 6.51
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04796 | 102.19 | Base Case | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04854 | 102.19 | Base Case | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03769 | 114.12 | Base Case | External | 107.36 | 6.76
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 478 | 478 | 0.03892 | 114.12 | Base Case | External | 107.36 | 6.76
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.1304 | 112.44 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 102.69 | 9.75
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.1266 | 112.44 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 102.69 | 9.75
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01017 | 165.91 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 238 | 238 | 0.01062 | 165.91 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 163.26 | 2.65
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01207 | 113.55 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 110.81 | 2.74
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.0122 | 113.55 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 110.81 | 2.74
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06832 | 127.19 | P23:345:MEC:MONTEZUMA 902 | External | 123.93 | 3.26
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06956 | 127.19 | P23:345:MEC:MONTEZUMA 902 | External | 123.93 | 3.26
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00149 | 166.19 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 166.06 | 0.13
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00152 | 166.19 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 166.06 | 0.13
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06439 | 129.38 | P23:345:AMMO::ZACHARY:1 | External | 126.67 | 2.71
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06549 | 129.38 | P23:345:AMMO::ZACHARY:1 | External | 126.67 | 2.71
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00046 | 104.73 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 104.63 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00047 | 104.73 | P12:230:EES:FRISCO_E:DBAYOU:1 | External | 104.63 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04796 | 109.32 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 107.65 | 1.67
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04854 | 109.32 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 107.65 | 1.67
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01006 | 100.94 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01058 | 100.94 | P12:345:ALTW-MEC:AUTO-SINGLE:HAZLTON3:BLACKHAWK3:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00067 | 107.22 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 107.07 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00068 | 107.22 | P12:HV:EES::6IRONMAN%:6GYPSY%:1 | External | 107.07 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04796 | 102.63 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 100.42 | 2.21
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04854 | 102.63 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 100.42 | 2.21
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06832 | 122.18 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 118.96 | 3.22
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06956 | 122.18 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 118.96 | 3.22
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00646 | 104.31 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 100.97 | 3.34
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00689 | 104.31 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 100.97 | 3.34
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02485 | 115.04 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 106.56 | 8.48
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02479 | 115.04 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 106.56 | 8.48
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0265 | 120.31 | P23:345:MEC:MONTEZUMA 901 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02715 | 120.31 | P23:345:MEC:MONTEZUMA 901 | External | 115.81 | 4.5
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 106.41 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00555 | 106.41 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02314 | 106.86 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.47 | 4.39
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0234 | 106.86 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.47 | 4.39
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00466 | 112.92 | P23:345:MEC:GDMEC 901 | External | 109.02 | 3.9
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00478 | 112.92 | P23:345:MEC:GDMEC 901 | External | 109.02 | 3.9
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.0053 | 106.41 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00555 | 106.41 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.97 | 2.44
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.0112 | 106.31 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 101.82 | 4.49
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01164 | 106.31 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 101.82 | 4.49
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.02688 | 106.25 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.02681 | 106.25 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00065 | 107.78 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.63 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336065 6CONVNT! 230 336066 6FRISCO! 230 1 | 434 | 434 | 0.00066 | 107.78 | 67854: 336055 3LAPLAC 115 336220 3GYPSY% 115 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | External | 107.63 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.0019 | 101.69 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00196 | 101.69 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00046 | 106.58 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 103.5 | 3.08
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631037 MPWSPLIT 161 631108 DENMARK5 161 1 | 150 | 150 | 0.00036 | 106.58 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 103.5 | 3.08
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00397 | 113.6 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 110.02 | 3.58
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00407 | 113.6 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 110.02 | 3.58
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00149 | 141.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 141.43 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00152 | 141.53 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 141.43 | 0.1
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 3e-05 | 109.66 | P11:HV:EES::1WAT U3!:1 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 608666 FONDULAC 115 608676 HIBBARD7 115 1 | 42 | 42 | 4e-05 | 109.66 | P11:HV:EES::1WAT U3!:1 | External | 109 | 0.66
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0227 | 100.26 | P23:345:MEC:GDMEC 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02287 | 100.26 | P23:345:MEC:GDMEC 901 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01006 | 100.94 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | 325 | 325 | 0.01058 | 100.94 | 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03983 | 112.77 | 104895: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | Internal | 111.21 | 1.56
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03897 | 112.77 | 104895: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | Internal | 111.21 | 1.56
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01672 | 119.11 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | External | 113.91 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01707 | 119.11 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | External | 113.91 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01207 | 122.32 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 118.93 | 3.39
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.0122 | 122.32 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 118.93 | 3.39
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00408 | 101.76 | 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1: 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00435 | 101.76 | 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1: 631193 HUNTLEY3 345 631045 HUNTLEY5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02645 | 120.31 | P23:345:MEC:GDMEC 902 | External | 115.69 | 4.62
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02709 | 120.31 | P23:345:MEC:GDMEC 902 | External | 115.69 | 4.62
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03445 | 110.91 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 109.94 | 0.97
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03366 | 110.91 | 81732: 514801 MINCO 7 345 514901 CIMARON7 345 1 514880 NORTWST7 345 514901 CIMARON7 345 1 514901 CIMARON7 345 514934 DRAPER 7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 1 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515610 FSHRTAP7 345 1 514901 CIMARON7 345 998305 CIMARON1 138 1 514901 CIMARON7 345 998304 CIMARON2 138 1 | Internal | 109.94 | 0.97
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00393 | 101.17 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00404 | 101.17 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01672 | 119.11 | P23:345:MEC:BONDURANT 906 | External | 113.91 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01707 | 119.11 | P23:345:MEC:BONDURANT 906 | External | 113.91 | 5.2
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01088 | 135.14 | P23:345:MEC:GDMEC 902 | External | 130.92 | 4.22
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01135 | 135.14 | P23:345:MEC:GDMEC 902 | External | 130.92 | 4.22
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02779 | 123.28 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 117.68 | 5.6
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02825 | 123.28 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 117.68 | 5.6
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03983 | 112.77 | 81377: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | Internal | 111.21 | 1.56
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 514880 NORTWST7 345 515497 MATHWSN7 345 1 | 1195 | 1195 | 0.03897 | 112.77 | 81377: 514901 CIMARON7 345 515497 MATHWSN7 345 2 514901 CIMARON7 345 515497 MATHWSN7 345 1 | Internal | 111.21 | 1.56
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00065 | 128.58 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 128.43 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00066 | 128.58 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 128.43 | 0.15
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01229 | 153.99 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 146.68 | 7.31
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.0129 | 153.99 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 146.68 | 7.31
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 9e-05 | 120.63 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.62 | 0.01
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 9e-05 | 120.63 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 120.62 | 0.01
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04796 | 109.9 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 108.39 | 1.51
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04854 | 109.9 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 108.39 | 1.51
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01056 | 148.06 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 141.66 | 6.4
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01113 | 148.06 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 141.66 | 6.4
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06372 | 125.08 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 121.56 | 3.52
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06483 | 125.08 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 121.56 | 3.52
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00427 | 100.87 | P23:345:XEL:8S23 WLM | External
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 613370 RUTLAND5 161 631042 FOX LK 5 161 1 | 168 | 168 | 0.00457 | 100.87 | P23:345:XEL:8S23 WLM | External
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01085 | 136.94 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 132.89 | 4.05
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01131 | 136.94 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 132.89 | 4.05
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04796 | 109.9 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 108.39 | 1.51
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04854 | 109.9 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 108.39 | 1.51
Thermal | 09NR | S2 | 24L0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02753 | 116.04 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.44 | 9.6
Thermal | 09NR | S2 | 24L0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02745 | 116.04 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.44 | 9.6
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00095 | 154.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 154.23 | 0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00097 | 154.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 154.23 | 0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00081 | 105.64 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 105.64 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00098 | 139.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.77 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00099 | 139.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 139.77 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00153 | 110.85 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.61 | 0.24
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00156 | 110.85 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.61 | 0.24
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00093 | 117.51 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 117.31 | 0.2
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00095 | 117.51 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 117.31 | 0.2
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00153 | 106 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.74 | 0.26
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00156 | 106 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.74 | 0.26
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01514 | 100.84 | P24:345:AMMO::MCCREDIE:1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01447 | 100.84 | P24:345:AMMO::MCCREDIE:1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00155 | 149.82 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 148.6 | 1.22
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00159 | 149.82 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 148.6 | 1.22
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 603020 MAPLE R7 115 997609 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00056 | 128.02 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 127.81 | 0.21
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 603020 MAPLE R7 115 997609 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00058 | 128.02 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 127.81 | 0.21
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00132 | 125.49 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 124.22 | 1.27
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.0013 | 125.49 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 124.22 | 1.27
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00039 | 105.35 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.26 | 0.09
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.0004 | 105.35 | P23:500:EES-EAI:WH_BLF:B7914 | External | 105.26 | 0.09
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00044 | 105.96 | P23:345:ALTW:MITCHLCO:1150 | External | 105.23 | 0.73
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00048 | 105.96 | P23:345:ALTW:MITCHLCO:1150 | External | 105.23 | 0.73
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00604 | 130.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 129.77 | 0.35
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00617 | 130.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 129.77 | 0.35
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00132 | 125.49 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 124.22 | 1.27
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.0013 | 125.49 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 124.22 | 1.27
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00078 | 102.67 | P23:345:OTP:BUFFALO3:3655:V2016 | External | 102.37 | 0.3
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00084 | 102.67 | P23:345:OTP:BUFFALO3:3655:V2016 | External | 102.37 | 0.3
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 129.57 | P13:161-69:EES-EAI:HERGET:AT1 | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 129.57 | P13:161-69:EES-EAI:HERGET:AT1 | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 127.59 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 127.59 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 127.59 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 127.59 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00032 | 109.32 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 108.65 | 0.67
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00034 | 109.32 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 108.65 | 0.67
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 129.2 | P13:161-69:EES-EAI:HERGET:AT2 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 129.2 | P13:161-69:EES-EAI:HERGET:AT2 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 108.94 | Base Case | External | 108.96 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 2e-05 | 108.94 | Base Case | External | 108.96 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00153 | 112.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.74 | 0.25
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00156 | 112.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.74 | 0.25
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00078 | 102.75 | P23:345:OTP:JAMESTN3:3145:V2020 | External | 102.44 | 0.31
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00084 | 102.75 | P23:345:OTP:JAMESTN3:3145:V2020 | External | 102.44 | 0.31
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00078 | 102.74 | P23:345:OTP:JAMESTN3:3135:V2020 | External | 102.48 | 0.26
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00084 | 102.74 | P23:345:OTP:JAMESTN3:3135:V2020 | External | 102.48 | 0.26
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 129.57 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 129.57 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00057 | 104.6 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 104.41 | 0.19
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334411 4STONGAT! 138 334412 4MID CO% 138 1 | 241 | 241 | 0.00057 | 104.6 | 67886: 334397 4OILLA 138 334430 4SABINE% 138 1 334398 4HAMPTON 138 334430 4SABINE% 138 1 | External | 104.41 | 0.19
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00116 | 139.47 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 138.59 | 0.88
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00119 | 139.47 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 138.59 | 0.88
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00032 | 109.32 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 108.65 | 0.67
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00034 | 109.32 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 108.65 | 0.67
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0007 | 122.91 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 121.96 | 0.95
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00074 | 122.91 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 121.96 | 0.95
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00604 | 144.55 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 144.24 | 0.31
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00617 | 144.55 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 144.24 | 0.31
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 6e-05 | 129.57 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 129.57 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 129.6 | -0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00028 | 102.94 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 102.87 | 0.07
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00026 | 102.94 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 102.87 | 0.07
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00033 | 111.55 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 110.86 | 0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00035 | 111.55 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 110.86 | 0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00016 | 104.45 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 104.27 | 0.18
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00016 | 104.45 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 104.27 | 0.18
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 155.37 | P12:161:DPC:RCE-HAR5 | External | 154.27 | 1.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 155.37 | P12:161:DPC:RCE-HAR5 | External | 154.27 | 1.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00107 | 148.36 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 147.12 | 1.24
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00112 | 148.36 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 147.12 | 1.24
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 129.2 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 129.2 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00183 | 105.73 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 105.26 | 0.47
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00177 | 105.73 | 300110 5PITTSV 161 300124 5HOLDEN 161 1: 300110 5PITTSV 161 300124 5HOLDEN 161 1 | External | 105.26 | 0.47
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 602021 EAU CLA5 161 997642 EAU CL 3 161 9 | 330 | 334.6 | 0.00313 | 106.05 | P23:345:XEL:8E5 ECL BS | External | 105.09 | 0.96
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 602021 EAU CLA5 161 997642 EAU CL 3 161 9 | 330 | 334.6 | 0.00332 | 106.05 | P23:345:XEL:8E5 ECL BS | External | 105.09 | 0.96
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01058 | 100.66 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01045 | 100.66 | 300500 5HUNTSDL 161 345409 5OVERTON 161 1: 300500 5HUNTSDL 161 345409 5OVERTON 161 1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00155 | 149.82 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 148.6 | 1.22
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00159 | 149.82 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 148.6 | 1.22
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00023 | 115.33 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 116.02 | -0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00021 | 115.33 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 116.02 | -0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00081 | 105.64 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 105.64 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00081 | 105.64 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 105.64 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00044 | 107.36 | P23:345:ALTW:MITCHLCO:1160 | External | 106.62 | 0.74
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00048 | 107.36 | P23:345:ALTW:MITCHLCO:1160 | External | 106.62 | 0.74
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00099 | 142.44 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.44 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00101 | 142.44 | P23:500:EES-EAI:WH_BLF:B7914 | External | 142.44 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82922 | 121.66 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00081 | 105.64 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 105.64 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 601028 EAU CL 3 345 997642 EAU CL 3 161 9 | 330 | 334.6 | 0.00313 | 104.36 | P23:345:XEL:8E5 ECL BS | External | 103.41 | 0.95
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 601028 EAU CL 3 345 997642 EAU CL 3 161 9 | 330 | 334.6 | 0.00332 | 104.36 | P23:345:XEL:8E5 ECL BS | External | 103.41 | 0.95
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01058 | 100.66 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01045 | 100.66 | P12:161:AMMO-AECI::CWL:OVERTON:1 | External
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00081 | 105.64 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 105.64 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00088 | 138.7 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 137.57 | 1.13
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00093 | 138.7 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 137.57 | 1.13
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00081 | 105.64 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 105.64 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 105.54 | 0.1
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00177 | 138.08 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 138.03 | 0.05
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0018 | 138.08 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 138.03 | 0.05
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 117.86 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.85 | 0.01
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 117.86 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 117.85 | 0.01
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 127.41 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 127.41 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 127.41 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 127.41 | 0
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 8e-05 | 101.27 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 101.26 | 0.01
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 6e-05 | 101.27 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 101.26 | 0.01
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00023 | 115.4 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 116.09 | -0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00021 | 115.4 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 116.09 | -0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00016 | 104.45 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 104.27 | 0.18
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00016 | 104.45 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 104.27 | 0.18
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00177 | 117.76 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 117.72 | 0.04
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.0018 | 117.76 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 117.72 | 0.04
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 117.79 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 117.77 | 0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 117.79 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 117.77 | 0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00033 | 111.55 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 110.86 | 0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00035 | 111.55 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 110.86 | 0.69
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 117.25 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.23 | 0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 117.25 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 117.23 | 0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00078 | 107.25 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 107.05 | 0.2
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00079 | 107.25 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 107.05 | 0.2
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 103.87 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.84 | 0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 103.87 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 103.84 | 0.03
Thermal | 00LVER | S1 | 24WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 6e-05 | 129.2 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 129.2 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 129.22 | -0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00094 | 149.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 149.42 | 0.11
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00096 | 149.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 149.42 | 0.11
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.0003 | 103.13 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 103.1 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615600 GRE-COAL CR4 230 615901 GRE-STANTON4 230 1 | 430.2 | 430.2 | 0.00029 | 103.13 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 103.1 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00049 | 102.98 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 102.57 | 0.41
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00051 | 102.98 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 102.57 | 0.41
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00101 | 135.31 | P23:500:EES-EAI:WH_BLF:B7914 | External | 135.22 | 0.09
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00103 | 135.31 | P23:500:EES-EAI:WH_BLF:B7914 | External | 135.22 | 0.09
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 114.36 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.33 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | 239 | 262.9 | 1e-05 | 114.36 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | External | 114.33 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 129.12 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 129.12 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00088 | 100.18 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0009 | 100.18 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00127 | 104.63 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 103.74 | 0.89
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300651 2LAMR 69.0 300794 5LAMAR 161 1 | 84 | 84 | 0.00125 | 104.63 | 87091: 547501 RIV453 5 161 547643 R13G167 13.8 1 547501 RIV453 5 161 547642 R12G4531 13.8 1 547502 RIV167 5 161 547503 RIV452T 5 161 1 547725 RIV452 1 12.5 997729 RIVERTON 69.0 1 532937 NEOSHO 5 161 547469 RIV4525 161 1 547467 ORO110 5 161 547469 RIV4525 161 1 547469 RIV4525 161 547487 HOC404 5 161 1 547469 RIV4525 161 547498 STL439 5 161 1 547469 RIV4525 161 547503 RIV452T 5 161 1 547469 RIV4525 161 997729 RIVERTON 69.0 1 547501 RIV453 5 161 547503 RIV452T 5 161 1 | External | 103.74 | 0.89
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00116 | 147.8 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 146.44 | 1.36
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00122 | 147.8 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 146.44 | 1.36
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00157 | 102.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.2 | 0.33
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.0016 | 102.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.2 | 0.33
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 171.24 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 170.02 | 1.22
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00157 | 171.24 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 170.02 | 1.22
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00037 | 100.42 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 100.17 | 0.25
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00038 | 100.42 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 100.17 | 0.25
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.42 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 102.94 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.42 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1 | External | 102.94 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00341 | 112.48 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 111.67 | 0.81
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00348 | 112.48 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 111.67 | 0.81
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 111.98 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 111.98 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 111.98 | 672610 POPLAR 4 230 672311 POPLAR 2G 18 1: 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1 | External | 111.98 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00135 | 121.41 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 119.97 | 1.44
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00133 | 121.41 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 119.97 | 1.44
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 125.86 | P23:500:EES-EAI:WH_BLF:B7914 | External | 125.71 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00038 | 125.86 | P23:500:EES-EAI:WH_BLF:B7914 | External | 125.71 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00587 | 104.27 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00612 | 104.27 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00516 | 114.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 114.25 | 0.26
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00528 | 114.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 114.25 | 0.26
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.00257 | 101.4 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 100.48 | 0.92
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 303134 4E_OPELUSAS! 138 335455 4CHAMPAGNE! 138 1 | 225 | 225 | 0.0026 | 101.4 | 80255: 335367 8RICHARD% 500 335368 8WELLS% 500 1 335368 8WELLS% 500 335500 8WEBRE% 500 1 335368 8WELLS% 500 500940 WELLS 6 230 1 335368 8WELLS% 500 500940 WELLS 6 230 2 335360 6CANKTON% 230 500940 WELLS 6 230 1 500920 WSTFORK6 230 500940 WELLS 6 230 1 500940 WELLS 6 230 502410 PMOUTON6 230 1 | External | 100.48 | 0.92
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00135 | 121.41 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 119.97 | 1.44
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 56 | 56 | 0.00133 | 121.41 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 119.97 | 1.44
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 104.44 | Base Case | External | 103.94 | 0.5
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 104.44 | Base Case | External | 103.94 | 0.5
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00157 | 110.42 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.11 | 0.31
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.0016 | 110.42 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.11 | 0.31
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 129.49 | P13:161-69:EES-EAI:HERGET:AT1 | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 129.49 | P13:161-69:EES-EAI:HERGET:AT1 | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00011 | 126.45 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.43 | 0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00012 | 126.45 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.43 | 0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00587 | 104.27 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00612 | 104.27 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 114.36 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.33 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 1 | 239 | 262.9 | 1e-05 | 114.36 | 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2: 672638 BEATTY 4 230 672639 ABERDEEN 4 230 2 | External | 114.33 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00037 | 107.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.44 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337634 3DIERKS! 115 337958 3SHERRILL 115 1 | 98 | 98 | 0.00038 | 107.59 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.44 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00157 | 111.71 | P23:500:EES-EAI:WH_BLF:B7914 | External | 111.39 | 0.32
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.0016 | 111.71 | P23:500:EES-EAI:WH_BLF:B7914 | External | 111.39 | 0.32
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.001 | 104.09 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.92 | 0.17
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00101 | 104.09 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.92 | 0.17
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00014 | 100.15 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00012 | 100.15 | 300505 2STURGN 69 300508 5STURGN 161 2: 300505 2STURGN 69.0 300508 5STURGN 161 2 | External
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 129.49 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 129.49 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00587 | 104.27 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00612 | 104.27 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 102.21 | 2.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00037 | 102.27 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.12 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337958 3SHERRILL 115 338753 3ENGLAND# 115 1 | 98 | 98 | 0.00038 | 102.27 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.12 | 0.15
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00286 | 107.12 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 106.36 | 0.76
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.0029 | 107.12 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 106.36 | 0.76
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00013 | 105.38 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.0002 | 105.38 | P12:EHV:EES::8ISES%:8JB-EHV%:1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00114 | 161.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 160.79 | 0.88
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00116 | 161.67 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 160.79 | 0.88
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00036 | 110.7 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 110.23 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00038 | 110.7 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 110.23 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00049 | 102.98 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 102.57 | 0.41
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 80.5 | 0.00051 | 102.98 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 102.57 | 0.41
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00077 | 122.55 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 121.61 | 0.94
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0008 | 122.55 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 121.61 | 0.94
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00516 | 134.17 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 133.96 | 0.21
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 430.2 | 430.2 | 0.00528 | 134.17 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 133.96 | 0.21
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00012 | 105.35 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 105.19 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00013 | 105.35 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1 | External | 105.19 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00012 | 105.25 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 105.09 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00013 | 105.25 | P12:LV-HV:EES::5WPLAIN!:2WSTPL3!:1(1) | External | 105.09 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 2e-05 | 129.49 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998885 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 129.49 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 129.5 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00037 | 112.95 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 112.47 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00038 | 112.95 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 112.47 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00097 | 151.23 | P12:161:DPC:RCE-HAR5 | External | 150.06 | 1.17
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00102 | 151.23 | P12:161:DPC:RCE-HAR5 | External | 150.06 | 1.17
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00386 | 110.76 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 109.4 | 1.36
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00402 | 110.76 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 109.4 | 1.36
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00013 | 105.38 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.0002 | 105.38 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1: 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 129.12 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 129.12 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00154 | 171.24 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 170.02 | 1.22
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00157 | 171.24 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 170.02 | 1.22
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00034 | 104.09 | Base Case | External | 103.66 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00036 | 104.09 | Base Case | External | 103.66 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00023 | 111.76 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 111.16 | 0.6
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00021 | 111.76 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 111.16 | 0.6
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.00013 | 105.38 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338138 5MOOREFIELD 161 338142 5ISES% 161 1 | 310 | 310 | 0.0002 | 105.38 | P12:500:EES-EAI:ND:8ISES%:8JB-EHV%:1 | External | 105.44 | -0.06
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00034 | 113.39 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4 | External | 112.95 | 0.44
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00036 | 113.39 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4 | External | 112.95 | 0.44
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00341 | 112.48 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 111.67 | 0.81
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00348 | 112.48 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 111.67 | 0.81
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00012 | 105.25 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 105.09 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | 56 | 56 | 0.00013 | 105.25 | 301123 2WSTPL3 69 300123 5WPLAIN 161 2: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | External | 105.09 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00103 | 137.89 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.81 | 0.08
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00104 | 137.89 | P23:500:EES-EAI:WH_BLF:B7914 | External | 137.81 | 0.08
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00034 | 112.98 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 112.55 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00036 | 112.98 | 631052 LANSING L1 5 161 629072 LANS5 4G 22 1: 631052 LANSING L1 5 161 629072 LANS5 4G 22.0 1 | External | 112.55 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 25 | 31 | 0.00017 | 108.16 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 108.14 | 0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997046 GLENHAM TR1 115 1 | 25 | 31 | 0.00017 | 108.16 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 108.14 | 0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82895 | 121.83 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.69 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.22 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.69 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3 | External | 103.22 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 111.98 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 111.98 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 111.98 | 672610 POPLAR 4 230 672310 POPLAR 1G 18 1: 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1 | External | 111.98 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00036 | 110.7 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 110.23 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997535 161/69 69.0 2 | 70 | 70 | 0.00038 | 110.7 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 110.23 | 0.47
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 100.82 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.79 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 0.0001 | 100.82 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.79 | 0.03
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00097 | 145.34 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 144.14 | 1.2
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00102 | 145.34 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 144.14 | 1.2
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.42 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 102.94 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00211 | 103.42 | 681523 GENOA 5 161 681522 GENOA53G 24 1: 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | External | 102.94 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0019 | 118.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.5 | 0.19
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00192 | 118.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.5 | 0.19
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00011 | 121.21 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 121.21 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.00012 | 121.21 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 121.21 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00386 | 113.77 | P11:024:DPC:ALMA2:6 | External | 112.45 | 1.32
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00402 | 113.77 | P11:024:DPC:ALMA2:6 | External | 112.45 | 1.32
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00012 | 105.35 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 105.19 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 301123 2WSTPL3 69.0 300123 5WPLAIN 161 2 | 56 | 56 | 0.00013 | 105.35 | 301123 2WSTPL3 69 300123 5WPLAIN 161 1: 301123 2WSTPL3 69.0 300123 5WPLAIN 161 1 | External | 105.19 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 126.27 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.26 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00011 | 126.27 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 126.26 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 6e-05 | 107.48 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 107.5 | -0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 4e-05 | 107.48 | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | External | 107.5 | -0.02
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00348 | 118.95 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 118.02 | 0.93
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00355 | 118.95 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 118.02 | 0.93
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00023 | 111.83 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 111.24 | 0.59
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00021 | 111.83 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 111.24 | 0.59
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 112.61 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 112.61 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 672615 YORKTON 4 230 672515 YORKTON 6 138 1 | 143.4 | 143.4 | 1e-05 | 112.61 | 672601 BD 4 230 672306 BD 6G 18 1: 672601 BD 4 230 672306 BD 6G 18.0 1 | External | 112.61 | 0
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.02 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.01 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 346156 1HITT 34.5 344270 5HITT 161 1 | 56 | 56 | 1e-05 | 109.02 | 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1: 346147 3VIADUCT 115 345890 1VIAD 1 34.5 1 | External | 109.01 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00202 | 101.2 | Base Case | External | 100.77 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00202 | 101.2 | Base Case | External | 100.77 | 0.43
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00026 | 109.07 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 109.02 | 0.05
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00024 | 109.07 | 300110 5PITTSV 161 300320 5LEVASY 161 1: 300110 5PITTSV 161 300320 5LEVASY 161 1 | External | 109.02 | 0.05
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00386 | 113.77 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 112.45 | 1.32
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00402 | 113.77 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 112.45 | 1.32
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.0019 | 101.28 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.12 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00192 | 101.28 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 101.12 | 0.16
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00348 | 118.95 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 118.02 | 0.93
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 201 | 221 | 0.00355 | 118.95 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 118.02 | 0.93
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00037 | 112.95 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 112.47 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997536 161/69 69.0 1 | 70 | 70 | 0.00038 | 112.95 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 112.47 | 0.48
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 120.6 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 120.59 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.00011 | 120.6 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 120.59 | 0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00026 | 107.21 | 104053: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 107.16 | 0.05
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 227 | 227 | 0.00023 | 107.21 | 104053: 300098 5MOCITY 161 548808 ECKLES-161 161 1 300320 5LEVASY 161 548808 ECKLES-161 161 1 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | External | 107.16 | 0.05
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 344282 5CAPE GIR2 161 351006 5JOPPA SR 161 1 | 250 | 297 | 0.0034 | 104.6 | P23:345:AMIL::JOPPA:V5 | External | 103.89 | 0.71
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 344282 5CAPE GIR2 161 351006 5JOPPA SR 161 1 | 250 | 297 | 0.00352 | 104.6 | P23:345:AMIL::JOPPA:V5 | External | 103.89 | 0.71
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00014 | 100.65 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 100.37 | 0.28
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00013 | 100.65 | 300505 2STURGN 69 300508 5STURGN 161 1: 300505 2STURGN 69.0 300508 5STURGN 161 1 | External | 100.37 | 0.28
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 2e-05 | 129.12 | P13:161-69:EES-EAI:HERGET:AT2 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998884 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 129.12 | P13:161-69:EES-EAI:HERGET:AT2 | External | 129.13 | -0.01
Thermal | 00LVER | S1 | 24SP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00278 | 101.68 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.02 | 0.66
Thermal | 00LVER | S1 | 24SP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 223 | 248 | 0.00281 | 101.68 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 101.02 | 0.66
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 335 | 335 | 0.02868 | 105.68 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 335 | 335 | 0.02911 | 105.68 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00085 | 147.23 | P23:500:EES-EAI:WH_BLF:B7914 | External | 147.16 | 0.07
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00088 | 147.23 | P23:500:EES-EAI:WH_BLF:B7914 | External | 147.16 | 0.07
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646221 S1221 5 161 646231 S1231 5 161 1 | 217 | 217 | 0.07503 | 111.14 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 145.4 | -34.26
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00594 | 117.94 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 115.75 | 2.19
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00621 | 117.94 | 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1: 613042 MURPHY CR 5 161 631044 HAYWARD L2 5 161 1 | External | 115.75 | 2.19
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00119 | 103.5 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | External | 102.44 | 1.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00126 | 103.5 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | External | 102.44 | 1.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08958 | 113.55 | Base Case | External | 109.68 | 3.87
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.09141 | 113.55 | Base Case | External | 109.68 | 3.87
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00344 | 114.99 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 110.63 | 4.36
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00349 | 114.99 | 635670 DMOINES5 161 635671 DMOINES8 69 2: 635670 DMOINES5 161 635671 DMOINES8 69.0 2 | External | 110.63 | 4.36
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 114.32 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.32 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00587 | 123.06 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 121.38 | 1.68
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00707 | 123.06 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 121.38 | 1.68
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 100.1 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.07 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 100.1 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.07 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06708 | 101.32 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.069 | 101.32 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.0125 | 108.74 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.29 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01287 | 108.74 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1: 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | External | 108.29 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01124 | 103.77 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.01178 | 103.77 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00094 | 138.03 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.02 | 0.01
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00095 | 138.03 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.02 | 0.01
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 25 | 31 | 0.00027 | 105.23 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 104.85 | 0.38
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997056 GLENHAM TR1 115 1 | 25 | 31 | 0.00027 | 105.23 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 104.85 | 0.38
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01106 | 116.02 | Base Case | External | 114.53 | 1.49
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01097 | 116.02 | Base Case | External | 114.53 | 1.49
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00031 | 137.91 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 136.91 | 1
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00033 | 137.91 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 136.91 | 1
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 106.58 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 106.58 | P12:500:EES:MOLIVE:EL_EHV:1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.0013 | 111.3 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.78 | 2.52
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00128 | 111.3 | 104036: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.78 | 2.52
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00652 | 111.95 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 110.07 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00666 | 111.95 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 110.07 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.0003 | 135.17 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 134.19 | 0.98
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.00032 | 135.17 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 134.19 | 0.98
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 111.28 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.25 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 111.28 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 111.25 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00288 | 149.92 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 144.4 | 5.52
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00315 | 149.92 | 300073 5GENTRY 161 300104 5NODWAY 161 1: 300073 5GENTRY 161 300104 5NODWAY 161 1 | External | 144.4 | 5.52
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00105 | 212.16 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 207.27 | 4.89
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00111 | 212.16 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 207.27 | 4.89
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00145 | 102.74 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.47 | 0.27
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00148 | 102.74 | P23:500:EES-EAI:WH_BLF:B7914 | External | 102.47 | 0.27
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00365 | 108.04 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 106.07 | 1.97
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00373 | 108.04 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 106.07 | 1.97
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01263 | 122.51 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 122.51 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 116.92 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 115.31 | 1.61
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 116.92 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 115.31 | 1.61
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 100.56 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 100.56 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 168.6 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 169.66 | -1.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00162 | 168.6 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 169.66 | -1.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 113.15 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 113.15 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00731 | 100.41 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00708 | 100.41 | 104176: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03388 | 110.91 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 104.78 | 6.13
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03362 | 110.91 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 104.78 | 6.13
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10423 | 104.43 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10401 | 104.43 | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00028 | 107.78 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 108.55 | -0.77
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00027 | 107.78 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 108.55 | -0.77
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.0013 | 111.3 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.78 | 2.52
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300336 2HOLDEN 69.0 300124 5HOLDEN 161 1 | 64 | 64 | 0.00128 | 111.3 | 300071 5CLINTN 161 300124 5HOLDEN 161 1: 300071 5CLINTN 161 300124 5HOLDEN 161 1 | External | 108.78 | 2.52
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00408 | 107.26 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.35 | 3.91
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00419 | 107.26 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 103.35 | 3.91
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 113.15 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 113.15 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00186 | 103.37 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External | 100.29 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 630013 VIELE 8 69.0 1 | 84 | 84 | 0.00193 | 103.37 | P12:161:AMMO-ALTW:AUTO-SINGLE:5CARBIDT:VIELE5:1 | External | 100.29 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04936 | 100.62 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.05002 | 100.62 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00038 | 108.76 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.13 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0004 | 108.76 | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z: 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | External | 108.13 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06749 | 101.93 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06942 | 101.93 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00408 | 104.48 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 102.63 | 1.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00419 | 104.48 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 102.63 | 1.85
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03098 | 117.63 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 113.39 | 4.24
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03054 | 117.63 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 113.39 | 4.24
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00036 | 139.85 | P23:345:ALTW:MITCHLCO:1150 | External | 136.14 | 3.71
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00039 | 139.85 | P23:345:ALTW:MITCHLCO:1150 | External | 136.14 | 3.71
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.01634 | 108.31 | Base Case | External | 104.04 | 4.27
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.018 | 108.31 | Base Case | External | 104.04 | 4.27
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00615 | 109.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 108.28 | 1.16
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00625 | 109.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 108.28 | 1.16
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08668 | 105.3 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 102.01 | 3.29
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08845 | 105.3 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 102.01 | 3.29
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00216 | 110.49 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 107.63 | 2.86
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00226 | 110.49 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 107.63 | 2.86
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 92 | 92 | 0.00025 | 105.15 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 104.52 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 92 | 92 | 0.00028 | 105.15 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 104.52 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00917 | 102.37 | Base Case | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00961 | 102.37 | Base Case | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00029 | 109.21 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.94 | -0.73
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00028 | 109.21 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.94 | -0.73
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00031 | 137.91 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 136.91 | 1
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00033 | 137.91 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 136.91 | 1
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07276 | 116.34 | P23:345:MEC:GRIMES 901 | External | 113.64 | 2.7
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.07474 | 116.34 | P23:345:MEC:GRIMES 901 | External | 113.64 | 2.7
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00355 | 142.67 | Base Case | External | 140.82 | 1.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00373 | 142.67 | Base Case | External | 140.82 | 1.85
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03312 | 106.97 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 100.88 | 6.09
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03285 | 106.97 | 104211: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542976 LEVEE 5 161 543665 HAWTHN5 161 1 | Internal | 100.88 | 6.09
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00011 | 223.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 8e-05 | 223.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0023 | 103.4 | Base Case | External | 102.57 | 0.83
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00239 | 103.4 | Base Case | External | 102.57 | 0.83
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 119.37 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 119.37 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00121 | 121.28 | P23:345:OTP:BUFFALO3:3655:V2016 | External | 119.96 | 1.32
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00127 | 121.28 | P23:345:OTP:BUFFALO3:3655:V2016 | External | 119.96 | 1.32
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0492 | 109.17 | P23:345:ALTW:MITCHLCO:1160 | External | 107.28 | 1.89
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04985 | 109.17 | P23:345:ALTW:MITCHLCO:1160 | External | 107.28 | 1.89
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 114.32 | P13:161-69:EES-EAI:HERGET:AT1 | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.32 | P13:161-69:EES-EAI:HERGET:AT1 | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01249 | 107.31 | P23:345:MEC:GDMEC 901 | External | 102.59 | 4.72
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.013 | 107.31 | P23:345:MEC:GDMEC 901 | External | 102.59 | 4.72
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.00023 | 116.64 | P13:115:XEL:COL TR5 AS- | External | 115.89 | 0.75
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.00025 | 116.64 | P13:115:XEL:COL TR5 AS- | External | 115.89 | 0.75
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00145 | 107.72 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.48 | 0.24
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00148 | 107.72 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.48 | 0.24
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00019 | 106.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.81 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00019 | 106.84 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.81 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02233 | 141.77 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 135.81 | 5.96
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.0245 | 141.77 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 135.81 | 5.96
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646347 S1347 161 1 | 217 | 217 | 0.84154 | 121.56 | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0492 | 109.19 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 106.74 | 2.45
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04985 | 109.19 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 106.74 | 2.45
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03018 | 108.47 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 107.86 | 0.61
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00652 | 112.14 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 110.4 | 1.74
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00666 | 112.14 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 110.4 | 1.74
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00587 | 104.58 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 103.29 | 1.29
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00707 | 104.58 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 103.29 | 1.29
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00479 | 101.68 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00491 | 101.68 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 92 | 92 | 0.00025 | 109.26 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 108.38 | 0.88
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 92 | 92 | 0.00028 | 109.26 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 108.38 | 0.88
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00029 | 114.22 | 71561: 615477 GRE-SPRGCK15 161 615478 GRE-SPRGCK25 161 Z 615478 GRE-SPRGCK25 161 616900 GRE-RAVENNA5 161 1 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 602001 PR ISLD5 161 616900 GRE-RAVENNA5 161 1 | External | 113.57 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997544 161/69 69.0 1 | 70 | 70 | 0.00031 | 114.22 | 71561: 615477 GRE-SPRGCK15 161 615478 GRE-SPRGCK25 161 Z 615478 GRE-SPRGCK25 161 616900 GRE-RAVENNA5 161 1 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 602001 PR ISLD5 161 616900 GRE-RAVENNA5 161 1 | External | 113.57 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02233 | 144.13 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 140.23 | 3.9
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.0245 | 144.13 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 140.23 | 3.9
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00121 | 121.66 | P23:345:OTP:JAMESTN3:3145:V2020 | External | 120.82 | 0.84
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00127 | 121.66 | P23:345:OTP:JAMESTN3:3145:V2020 | External | 120.82 | 0.84
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07088 | 125.2 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 124.04 | 1.16
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07214 | 125.2 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External | 124.04 | 1.16
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00607 | 103.93 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00638 | 103.93 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00121 | 121.51 | P23:345:OTP:JAMESTN3:3135:V2020 | External | 120.77 | 0.74
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00127 | 121.51 | P23:345:OTP:JAMESTN3:3135:V2020 | External | 120.77 | 0.74
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.01634 | 102.8 | Base Case | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.018 | 102.8 | Base Case | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01577 | 110.96 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01666 | 110.96 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 319 | 319 | 0.03037 | 103.77 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0023 | 105.38 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 104.61 | 0.77
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00239 | 105.38 | 657700 PILSBRY4 230 657754 MAPLE R4 230 1: 657700 PILSBRY4 230 657754 MAPLE R4 230 1 | External | 104.61 | 0.77
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00514 | 106.54 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 104.45 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00541 | 106.54 | P13:161-69:ITCM:HAYWD#25 T2:MN | External | 104.45 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0009 | 106.41 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 104.3 | 2.11
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00093 | 106.41 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External | 104.3 | 2.11
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03018 | 111.99 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 112.03 | -0.04
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.07088 | 119.01 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 118.02 | 0.99
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.07214 | 119.01 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 118.02 | 0.99
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 110.26 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 108.32 | 1.94
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 64 | 64 | 0.00381 | 110.26 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 108.32 | 1.94
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00379 | 171 | P23:345:ALTW:MITCHLCO:1160 | External | 167.42 | 3.58
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00402 | 171 | P23:345:ALTW:MITCHLCO:1160 | External | 167.42 | 3.58
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00029 | 108.49 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 109.26 | -0.77
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00028 | 108.49 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 109.26 | -0.77
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.0853 | 105.56 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 102.61 | 2.95
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08703 | 105.56 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 102.61 | 2.95
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 113.99 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.99 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00028 | 106.72 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 107.5 | -0.78
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00027 | 106.72 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 107.5 | -0.78
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.22234 | 102.99 | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | Internal | 101.18 | 1.81
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00011 | 223.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 8e-05 | 223.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01204 | 104.8 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 104.36 | 0.44
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.0124 | 104.8 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 104.36 | 0.44
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06749 | 101.93 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06942 | 101.93 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.00082 | 127.74 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 123.91 | 3.83
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 1 | 34 | 34 | 0.00089 | 127.74 | 300258 2MARYVL 69 300097 5MARYVL 161 2: 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | External | 123.91 | 3.83
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00731 | 102.65 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 273 | 273 | 0.00789 | 102.65 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00118 | 155.8 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 152.86 | 2.94
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00121 | 155.8 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 152.86 | 2.94
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.02233 | 141.77 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 135.81 | 5.96
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 252 | 252 | 0.0245 | 141.77 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 135.81 | 5.96
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603020 MAPLE R7 115 997616 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00065 | 118.72 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 118.65 | 0.07
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603020 MAPLE R7 115 997616 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00067 | 118.72 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 118.65 | 0.07
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06749 | 101.93 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | 1055 | 1319 | 0.06942 | 101.93 | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.01891 | 101.57 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.01967 | 101.57 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00615 | 128.73 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 128.28 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00625 | 128.73 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 128.28 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 335 | 335 | 0.02783 | 122.5 | P23:345:MEC:GDMEC 901 | External | 117.44 | 5.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 335 | 335 | 0.02848 | 122.5 | P23:345:MEC:GDMEC 901 | External | 117.44 | 5.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00093 | 107.53 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 105.86 | 1.67
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00097 | 107.53 | P13:161-69:ITCM:LORE 5 T2:IA-NE | External | 105.86 | 1.67
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04893 | 103.31 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 101.79 | 1.52
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04952 | 103.31 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 101.79 | 1.52
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 6e-05 | 102.23 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 101.73 | 0.5
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00019 | 102.23 | P12:161:MEC:AUTO-SINGLE:VICTORY5:CARROLL5:1 | External | 101.73 | 0.5
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 335 | 335 | 0.02868 | 105.68 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 335 | 335 | 0.02911 | 105.68 | P23:345:MEC:GDMEC 901 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00594 | 117.94 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 115.75 | 2.19
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 631127 HAYWARD L1 5 161 1 | 233 | 233 | 0.00621 | 117.94 | P12:161:SMMPA-ALTW:AUTO-SINGLE:MURPHYCR5:HAYWARDL25:1 | External | 115.75 | 2.19
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 119.37 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 119.37 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.0003 | 135.17 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 134.19 | 0.98
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997543 161/69 69.0 2 | 70 | 70 | 0.00032 | 135.17 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 134.19 | 0.98
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01204 | 104.8 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 104.36 | 0.44
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.0124 | 104.8 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 104.36 | 0.44
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03098 | 117.63 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 113.39 | 4.24
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03054 | 117.63 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 113.39 | 4.24
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.00038 | 108.76 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.13 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 630197 LIME CK J1 8 69.0 1 | 74.7 | 74.7 | 0.0004 | 108.76 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:LIMECKL25:Z | External | 108.13 | 0.63
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00408 | 107.76 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 103.78 | 3.98
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00419 | 107.76 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 103.78 | 3.98
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03018 | 108.47 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH | Internal | 107.86 | 0.61
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0492 | 109.21 | P23:345:ALTW:MITCHLCO:1160 | External | 107.31 | 1.9
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04985 | 109.21 | P23:345:ALTW:MITCHLCO:1160 | External | 107.31 | 1.9
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03388 | 107.61 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 102.04 | 5.57
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03362 | 107.61 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 102.04 | 5.57
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00155 | 107.27 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 105.22 | 2.05
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00165 | 107.27 | 636300 FLOYD 5 161 656087 BREMER CO5 161 1: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 | External | 105.22 | 2.05
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02233 | 135.64 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 129.42 | 6.22
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.0245 | 135.64 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 129.42 | 6.22
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.03239 | 103.42 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal | 100.2 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.03212 | 103.42 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal | 100.2 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00386 | 134.05 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 132.88 | 1.17
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00401 | 134.05 | 681543 ALMA 5 161 681542 JPM 24 1: 681543 ALMA 5 161 681542 JPM 24.0 1 | External | 132.88 | 1.17
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00607 | 103.93 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00638 | 103.93 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 168.6 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 169.66 | -1.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00162 | 168.6 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 169.66 | -1.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00069 | 114.88 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 111.92 | 2.96
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00072 | 114.88 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 111.92 | 2.96
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00025 | 104.1 | Base Case | External | 102.27 | 1.83
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00027 | 104.1 | Base Case | External | 102.27 | 1.83
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07088 | 125.14 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 123.99 | 1.15
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07214 | 125.14 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External | 123.99 | 1.15
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00587 | 104.85 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 103.49 | 1.36
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.00707 | 104.85 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1: 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | External | 103.49 | 1.36
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00023 | 121.25 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 122.38 | -1.13
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00021 | 121.25 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 122.38 | -1.13
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00288 | 149.98 | 300097 5MARYVL 161 300104 5NODWAY 161 1: 300097 5MARYVL 161 300104 5NODWAY 161 1 | External | 144.43 | 5.55
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300258 2MARYVL 69.0 300097 5MARYVL 161 2 | 57 | 57 | 0.00315 | 149.98 | 300097 5MARYVL 161 300104 5NODWAY 161 1: 300097 5MARYVL 161 300104 5NODWAY 161 1 | External | 144.43 | 5.55
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00027 | 127.97 | P23:500:EMI-EES:ABF_FRKLN-A | External | 127.79 | 0.18
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336111 3AMITE! 115 336517 3GILLSBURG+ 115 1 | 112 | 112 | 0.00027 | 127.97 | P23:500:EMI-EES:ABF_FRKLN-A | External | 127.79 | 0.18
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01263 | 122.51 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 122.51 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00197 | 113.18 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External | 109.49 | 3.69
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00202 | 113.18 | 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1: 631081 M-TOWN 5 161 631004 M-TOWN 7 115 1 | External | 109.49 | 3.69
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04893 | 124.17 | Base Case | External | 121.79 | 2.38
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04952 | 124.17 | Base Case | External | 121.79 | 2.38
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00735 | 100.99 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 100.43 | 0.56
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00711 | 100.99 | 104175: 300071 5CLINTN 161 542969 STILWEL5 161 1 541207 ARCHIE 5 161 541341 S.HARP 5 161 1 | External | 100.43 | 0.56
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 113.99 | P13:161-69:EES-EAI:HERGET:AT2 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.99 | P13:161-69:EES-EAI:HERGET:AT2 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00028 | 108.5 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.22 | -0.72
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 28 | 28 | 0.00027 | 108.5 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 109.22 | -0.72
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 319 | 319 | 0.03052 | 105.11 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21434 | 100.51 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00408 | 104.4 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 102.68 | 1.72
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00419 | 104.4 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 102.68 | 1.72
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.08958 | 105.24 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 102.18 | 3.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 1055 | 1228 | 0.09141 | 105.24 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 102.18 | 3.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00036 | 141.88 | P23:345:ALTW:MITCHLCO:1160 | External | 138.03 | 3.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00039 | 141.88 | P23:345:ALTW:MITCHLCO:1160 | External | 138.03 | 3.85
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00358 | 118.54 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 116.51 | 2.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00366 | 118.54 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 116.51 | 2.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00128 | 101.52 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 100.12 | 1.4
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00137 | 101.52 | 86693: 636300 FLOYD 5 161 656087 BREMER CO5 161 1 636200 BLACKHAWK 5 161 656087 BREMER CO5 161 1 | External | 100.12 | 1.4
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04893 | 124.13 | Base Case | External | 122.07 | 2.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04952 | 124.13 | Base Case | External | 122.07 | 2.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00216 | 110.49 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 107.63 | 2.86
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00226 | 110.49 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 107.63 | 2.86
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.0007 | 118.84 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 116.66 | 2.18
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00072 | 118.84 | 631056 LORE 5 161 631060 TRK RIV5 161 1: 631056 LORE 5 161 631060 TRK RIV5 161 1 | External | 116.66 | 2.18
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00145 | 109.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.59 | 0.25
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00148 | 109.84 | P23:500:EES-EAI:WH_BLF:B7914 | External | 109.59 | 0.25
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00051 | 105.59 | 603157 RIVFL T7 115 603199 RIVFLSN7 115 1: 603157 RIVFL T7 115 603199 RIVFLSN7 115 1 | External | 104.38 | 1.21
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00054 | 105.59 | 603157 RIVFL T7 115 603199 RIVFLSN7 115 1: 603157 RIVFL T7 115 603199 RIVFLSN7 115 1 | External | 104.38 | 1.21
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00079 | 103.47 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 101.36 | 2.11
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681526 BELLCTR5 161 680075 BELLCNTR 69.0 1 | 71 | 71 | 0.00083 | 103.47 | 71524: 681519 STONEMAN 161 699010 NED 161 161 1 681525 GRANGRAE 161 699010 NED 161 161 1 699020 NED 138 138 699010 NED 161 161 1 681521 SENECA 5 161 681525 GRANGRAE 161 1 699959 GRANGRAE 69.0 681525 GRANGRAE 161 1 | External | 101.36 | 2.11
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00096 | 140.67 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.66 | 0.01
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00097 | 140.67 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.66 | 0.01
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03388 | 110.91 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 104.78 | 6.13
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03362 | 110.91 | 104210: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 543000 BLUEVLY5 161 543665 HAWTHN5 161 2 | Internal | 104.78 | 6.13
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03098 | 113.4 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 109.45 | 3.95
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03054 | 113.4 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 | Internal | 109.45 | 3.95
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00197 | 113.18 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External | 109.49 | 3.69
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631081 M-TOWN 5 161 629105 M-TOWN 9 34.5 1 | 96 | 96 | 0.00202 | 113.18 | P13:115-161:ALTW:AUTO-SINGLE:M-TOWN7:M-TOWN5:1 | External | 109.49 | 3.69
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0492 | 100.23 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04985 | 100.23 | P23:345:ALTW:MITCHLCO:1160 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00096 | 107.76 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 105.94 | 1.82
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00101 | 107.76 | P12:161:ALTW:AUTO-SINGLE:LORE5:HCKRYCK5:1 | External | 105.94 | 1.82
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01244 | 107.25 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.78 | 0.47
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01281 | 107.25 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 106.78 | 0.47
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0492 | 109.15 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 106.71 | 2.44
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04985 | 109.15 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 106.71 | 2.44
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.14923 | 112.99 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.87 | 8.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.14811 | 112.99 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.87 | 8.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0023 | 105.38 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 104.61 | 0.77
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00239 | 105.38 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1 | External | 104.61 | 0.77
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01199 | 103.44 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 102.92 | 0.52
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 335 | 335 | 0.01234 | 103.44 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 102.92 | 0.52
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00358 | 118.54 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.51 | 2.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00366 | 118.54 | 681521 SENECA 5 161 681523 GENOA 5 161 1: 681521 SENECA 5 161 681523 GENOA 5 161 1 | External | 116.51 | 2.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82989 | 114.03 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03312 | 103.79 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03285 | 103.79 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00408 | 104.4 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 102.68 | 1.72
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 120 | 120 | 0.00419 | 104.4 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 102.68 | 1.72
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00344 | 114.99 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 110.63 | 4.36
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635671 DMOINES8 69.0 1 | 100 | 100 | 0.00349 | 114.99 | P13:161-69:MEC:AUTO-SINGLE:DMOINES5:DMOINES8:2 | External | 110.63 | 4.36
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00155 | 107.27 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 105.22 | 2.05
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636300 FLOYD 5 161 636301 FLOYD 8 69.0 1 | 117.1 | 128.8 | 0.00165 | 107.27 | P12:161:MEC-WAPA:AUTO-SINGLE:FLOYD5:BREMERCO5:1 | External | 105.22 | 2.05
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 143 | 157.3 | 0.00025 | 104.53 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 103.97 | 0.56
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 608721 ETCO 7 115 608722 FORBES 7 115 1 | 143 | 157.3 | 0.00027 | 104.53 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 103.97 | 0.56
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00158 | 104.19 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.88 | 1.31
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603053 ALDRICH7 115 603075 FIFTHST7 115 1 | 188.8 | 220.5 | 0.00166 | 104.19 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 102.88 | 1.31
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00379 | 167.47 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 165.04 | 2.43
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00402 | 167.47 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 165.04 | 2.43
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00479 | 101.68 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00491 | 101.68 | P23:345:MEC:GDMEC 902 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0009 | 106.47 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 104.27 | 2.2
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00093 | 106.47 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 104.27 | 2.2
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 106.58 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 106.58 | P12:EHV:EES::8MT_OLIVE%:8EL DORADO%:1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.0004 | 115.61 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 112.02 | 3.59
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00043 | 115.61 | 603058 AS KING7 115 603155 WILOWRV7 115 1: 603058 AS KING7 115 603155 WILOWRV7 115 1 | External | 112.02 | 3.59
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03018 | 111.99 | 104236: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542951 HAW G5 1 22.0 541 1544 5 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 112.03 | -0.04
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.02233 | 135.64 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 129.42 | 6.22
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 269 | 269 | 0.0245 | 135.64 | 104493: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 129.42 | 6.22
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00731 | 100.41 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300071 5CLINTN 161 300124 5HOLDEN 161 1 | 252 | 252 | 0.00708 | 100.41 | 104655: 300071 5CLINTN 161 542969 STILWEL5 161 1 541341 S.HARP 5 161 542969 STILWEL5 161 1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 113.15 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 113.15 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1: 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | External | 110.07 | 3.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00339 | 105.16 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 102.92 | 2.24
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631060 TRK RIV5 161 681519 STONEMAN 161 1 | 252 | 274 | 0.00346 | 105.16 | P12:161:DPC:AUTO-SINGLE:SENECA5:GRANGRAE:1 | External | 102.92 | 2.24
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00607 | 103.93 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631047 LIME CK L1 5 161 631160 LIME CK L2 5 161 Z | 335 | 335 | 0.00638 | 103.93 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 101.85 | 2.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0009 | 106.47 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 104.27 | 2.2
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00093 | 106.47 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External | 104.27 | 2.2
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00404 | 119.37 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 601002 ADAMS 3 345 997678 ADAMS 3 161 9 | 330 | 334.6 | 0.00446 | 119.37 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1 | External | 116.03 | 3.34
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01249 | 107.31 | P23:345:MEC:GDMEC 902 | External | 102.59 | 4.72
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.013 | 107.31 | P23:345:MEC:GDMEC 902 | External | 102.59 | 4.72
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03098 | 113.4 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 109.45 | 3.95
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997747 HAWTHORN22 161 22 | 550 | 605 | 0.03054 | 113.4 | 104213: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | Internal | 109.45 | 3.95
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00127 | 106.58 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337544 3WYATT! 115 337545 3PARNELL RD 115 1 | 159 | 159 | 0.00128 | 106.58 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1: 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | External | 105.93 | 0.65
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.0078 | 119.69 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 116.43 | 3.26
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.00847 | 119.69 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 116.43 | 3.26
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10423 | 104.43 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.10401 | 104.43 | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00386 | 111.07 | Base Case | External | 109.95 | 1.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00401 | 111.07 | Base Case | External | 109.95 | 1.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.0007 | 118.84 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 116.66 | 2.18
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630282 TURK RV8 69.0 631060 TRK RIV5 161 1 | 34 | 34 | 0.00072 | 118.84 | P12:161:ALTW:AUTO-SINGLE:LORE5:TRKRIV5:1 | External | 116.66 | 2.18
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00148 | 110.56 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.48 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.0015 | 110.56 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 110.48 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03388 | 107.61 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 102.04 | 5.57
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 543665 HAWTHN5 161 997748 HAWTHORN20 161 20 | 500 | 550 | 0.03362 | 107.61 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 | Internal | 102.04 | 5.57
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00652 | 111.95 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 110.07 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00666 | 111.95 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External | 110.07 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 560 | 700 | 0.02861 | 100.59 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 997480 DGG9T1 161 1 | 560 | 700 | 0.02926 | 100.59 | P23:345:MEC:SYCAMORE 905 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 111.63 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.59 | 0.04
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 111.63 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.59 | 0.04
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01577 | 110.96 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01666 | 110.96 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 7e-05 | 114.32 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998882 HGT X1 69.0 1 | 100 | 112 | 8e-05 | 114.32 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 114.24 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05472 | 108.2 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 104.98 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05394 | 108.2 | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 104.98 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00386 | 135.99 | P11:024:DPC:ALMA2:6 | External | 134.76 | 1.23
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00401 | 135.99 | P11:024:DPC:ALMA2:6 | External | 134.76 | 1.23
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0024 | 123.39 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 121.3 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00234 | 123.39 | 104648: 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 121.3 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00238 | 123.15 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 121.03 | 2.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00231 | 123.15 | 301342 5BUTLER 161 541208 NEVADA 5 161 1: 301342 5BUTLER 161 541208 NEVADA 5 161 1 | External | 121.03 | 2.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00587 | 122.63 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 120.79 | 1.84
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 997476 WEB AB 161 1 | 560 | 560 | 0.00707 | 122.63 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1: 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | External | 120.79 | 1.84
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00019 | 106.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.66 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00019 | 106.69 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 106.66 | 0.03
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 335 | 335 | 0.02127 | 106.85 | P23:345:MEC:SYCAMORE 905 | External | 104.57 | 2.28
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635614 100 54 5 161 635617 JOHNSTON 5 161 1 | 335 | 335 | 0.02189 | 106.85 | P23:345:MEC:SYCAMORE 905 | External | 104.57 | 2.28
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00023 | 121.33 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 122.46 | -1.13
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00021 | 121.33 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 122.46 | -1.13
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.0004 | 115.61 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 112.02 | 3.59
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603158 RIV FLS7 115 600073 RVRFLSMG 69.0 5 | 70 | 91 | 0.00043 | 115.61 | P12:115:XEL:AUTO-SINGLE:ASKING7:WILOWRV7:1 | External | 112.02 | 3.59
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08506 | 104.2 | P23:345:MEC:NORWALK 901 | External | 101.24 | 2.96
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 1055 | 1245 | 0.08675 | 104.2 | P23:345:MEC:NORWALK 901 | External | 101.24 | 2.96
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.00242 | 109.71 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 108.91 | 0.8
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620327 HANKSON4 230 620329 WAHPETN4 230 1 | 319 | 351 | 0.0025 | 109.71 | 105816: 602036 PAYNES 4 230 619975 GRE-WILLMAR4 230 1 619975 GRE-WILLMAR4 230 652550 GRANITF4 230 1 619975 GRE-WILLMAR4 230 997515 230/69 69.0 1 652292 GRANITF29 13.8 997144 GF KV8A 115 1 652298 GRANITF8 69.0 997143 GF KY2A 69.0 1 602008 MINVALT4 230 602009 MNVLTAP4 230 1 602009 MNVLTAP4 230 615529 GRE-PANTHER4 230 1 602009 MNVLTAP4 230 652550 GRANITF4 230 1 587710 GEN-2016-036 115 652551 GRANITF7 115 1 603030 MINVALY7 115 652551 GRANITF7 115 1 620211 CANBY 7 115 652551 GRANITF7 115 1 652551 GRANITF7 115 655461 MRSHLXCL-ER7 115 1 652551 GRANITF7 115 997145 GF KV3A 115 1 652551 GRANITF7 115 997144 GF KV8A 115 1 652551 GRANITF7 115 997143 GF KY2A 69.0 1 602008 MINVALT4 230 652550 GRANITF4 230 1 652550 GRANITF4 230 652554 MORRIS 4 230 1 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 652550 GRANITF4 230 655465 BLAIR-ER4 230 1 652550 GRANITF4 230 997145 GF KV3A 115 1 652550 GRANITF4 230 997144 GF KV8A 115 1 | External | 108.91 | 0.8
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 0.00011 | 223.01 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 8e-05 | 223.01 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 223.03 | -0.02
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04936 | 109.7 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.82 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.05002 | 109.7 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.82 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.0024 | 123.39 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 121.3 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300689 2BUTLER 69.0 301342 5BUTLER 161 1 | 64 | 64 | 0.00234 | 123.39 | 84407: 301342 5BUTLER 161 541208 NEVADA 5 161 1 541306 APCITY 2 69.0 541308 NEVADA 2 69.0 1 | External | 121.3 | 2.09
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00386 | 135.99 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 134.76 | 1.23
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 262 | 288 | 0.00401 | 135.99 | P11:24:DPC:AUTO-SINGLE:JPM:6 | External | 134.76 | 1.23
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.01891 | 100.9 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636000 WEBSTER3 345 997476 WEB AB 161 1 | 560 | 560 | 0.01967 | 100.9 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00096 | 107.76 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 105.94 | 1.82
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631100 LIBERTY5 161 630019 LIBERTY8 69.0 1 | 84 | 84 | 0.00101 | 107.76 | 631056 LORE 5 161 631159 HCKRYCK5 161 1: 631056 LORE 5 161 631159 HCKRYCK5 161 1 | External | 105.94 | 1.82
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 189 | 220.9 | 0.00131 | 102.01 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 100.73 | 1.28
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603075 FIFTHST7 115 603088 MAIN ST7 115 1 | 189 | 220.9 | 0.00139 | 102.01 | 71568: 601024 TERMINL3 345 997655 90198-B 115 10 603110 TERMINL7 115 997655 90198-B 115 10 605516 TERTER19 34.5 997655 90198-B 115 10 601019 COON CK3 345 601024 TERMINL3 345 1 601021 KOLMNLK3 345 997662 C0512551 115 9 603084 KOLMNLK7 115 997662 C0512551 115 9 605702 KHLMN TR9 T9 13.8 997662 C0512551 115 9 601019 COON CK3 345 601021 KOLMNLK3 345 1 | External | 100.73 | 1.28
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 335 | 335 | 0.02783 | 122.5 | P23:345:MEC:GDMEC 902 | External | 117.44 | 5.06
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 335 | 335 | 0.02848 | 122.5 | P23:345:MEC:GDMEC 902 | External | 117.44 | 5.06
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00379 | 169.29 | P23:345:ALTW:MITCHLCO:1150 | External | 166.18 | 3.11
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00402 | 169.29 | P23:345:ALTW:MITCHLCO:1150 | External | 166.18 | 3.11
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.0125 | 108.74 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.29 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | 335 | 335 | 0.01287 | 108.74 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:1 | External | 108.29 | 0.45
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14414 | 115.74 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 134.93 | -19.19
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.06708 | 101.32 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | 1247 | 1319 | 0.069 | 101.32 | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04936 | 109.74 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.86 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.05002 | 109.74 | P22:345:XEL:ADAMS 3 N1:MN | External | 107.86 | 1.88
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01263 | 122.51 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 450 | 450 | 0.01334 | 122.51 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External | 117.39 | 5.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00408 | 107.76 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 103.78 | 3.98
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 120 | 120 | 0.00419 | 107.76 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 103.78 | 3.98
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00365 | 108.04 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 106.07 | 1.97
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 681519 STONEMAN 161 699010 NED 161 161 1 | 262 | 288 | 0.00373 | 108.04 | P12:161:DPC:AUTO-SINGLE:SENECA5:GENOA5:1 | External | 106.07 | 1.97
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00087 | 102.28 | 344004 5ADAIR1 161 346005 2ADAIR 1 69 1: 344004 5ADAIR1 161 346005 2ADAIR 1 69.0 1 | External | 101.49 | 0.79
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 346006 2ADAIR 2 69.0 344006 5ADAIR3 161 1 | 61 | 77.8 | 0.00092 | 102.28 | 344004 5ADAIR1 161 346005 2ADAIR 1 69 1: 344004 5ADAIR1 161 346005 2ADAIR 1 69.0 1 | External | 101.49 | 0.79
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 560 | 700 | 0.02861 | 102.65 | P23:345:MEC:SYCAMORE 905 | External | 100.49 | 2.16
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635600 GRIMES 3 345 997480 DGG9T1 161 1 | 560 | 700 | 0.02926 | 102.65 | P23:345:MEC:SYCAMORE 905 | External | 100.49 | 2.16
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01577 | 110.96 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01666 | 110.96 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External | 106.11 | 4.85
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.21472 | 100.07 | 82347: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 | Internal
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.0127 | 118.9 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.36 | 6.54
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 246 | 281 | 0.01331 | 118.9 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 112.36 | 6.54
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.02233 | 144.13 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 140.23 | 3.9
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.0245 | 144.13 | 84814: 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | External | 140.23 | 3.9
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 7e-05 | 113.99 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998881 HGT X2 69.0 1 | 100 | 112 | 8e-05 | 113.99 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 113.91 | 0.08
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.14923 | 112.99 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.87 | 8.12
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.14811 | 112.99 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal | 104.87 | 8.12
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.01634 | 113.9 | Base Case | External | 110.63 | 3.27
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 252 | 252 | 0.018 | 113.9 | Base Case | External | 110.63 | 3.27
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05472 | 108.2 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 104.98 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | 1016 | 1016 | 0.05394 | 108.2 | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | Internal | 104.98 | 3.22
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00924 | 100.8 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1195.1 | 1195.1 | 0.00981 | 100.8 | P22:345:XEL:ADAMS 3 N1:MN | External
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00029 | 107.42 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 108.2 | -0.78
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 28 | 28 | 0.00028 | 107.42 | P12:161:AECI:M:HINTON2:BOLSTAD:1 | External | 108.2 | -0.78
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00086 | 209.29 | P12:161:DPC:RCE-HAR5 | External | 204.3 | 4.99
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00091 | 209.29 | P12:161:DPC:RCE-HAR5 | External | 204.3 | 4.99
Thermal | 00NR | S2 | 19WP0 | GEN_025_028 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 6e-05 | 102.23 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 101.73 | 0.5
Thermal | 00NR | S2 | 19WP0 | GEN_043_044_045 | FROM -> TO | 635300 MONONA 5 161 635301 MONONA 8 69.0 1 | 41.7 | 60 | 0.00019 | 102.23 | 635310 VICTORY5 161 635320 CARROLL5 161 1: 635310 VICTORY5 161 635320 CARROLL5 161 1 | External | 101.73 | 0.5
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02818 | 115.7 | P23:345:MEC:GDMEC 902 | External | 109.49 | 6.21
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0286 | 115.7 | P23:345:MEC:GDMEC 902 | External | 109.49 | 6.21
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00096 | 158.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 158.17 | 0.09
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00098 | 158.26 | P23:500:EES-EAI:WH_BLF:B7914 | External | 158.17 | 0.09
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0908 | 129.65 | Base Case | External | 123.54 | 6.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09264 | 129.65 | Base Case | External | 123.54 | 6.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.1288 | 106.54 | 92469: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12624 | 106.54 | 92469: 542964 HAWCT8 1 13.8 542976 LEVEE 5 161 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 542967 HAW G9 1 13.8 542973 HAWTHS5 161 1 542961 HAWCT6 1 16.0 542973 HAWTHS5 161 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542963 HAWCT7 1 13.8 542976 LEVEE 5 161 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01709 | 106.69 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 100.72 | 5.97
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01744 | 106.69 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External | 100.72 | 5.97
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03484 | 127.22 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 114.03 | 13.19
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03561 | 127.22 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 114.03 | 13.19
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07141 | 127.91 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 125.24 | 2.67
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.07268 | 127.91 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 125.24 | 2.67
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04591 | 107.7 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04511 | 107.7 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.02933 | 101.2 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.0293 | 101.2 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00099 | 138.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.5 | 0.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00101 | 138.53 | P23:500:EES-EAI:WH_BLF:B7914 | External | 138.5 | 0.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 184 | 199 | 0.03484 | 132.41 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 118.19 | 14.22
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 184 | 199 | 0.03561 | 132.41 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 118.19 | 14.22
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.03751 | 152.74 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 142.94 | 9.8
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.03741 | 152.74 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 142.94 | 9.8
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00155 | 110.3 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.06 | 0.24
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00158 | 110.3 | P23:500:EES-EAI:WH_BLF:B7914 | External | 110.06 | 0.24
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00217 | 105.59 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 103.17 | 2.42
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00227 | 105.59 | 636050 WRIGHT 5 161 636235 WALL LK5 161 1: 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | External | 103.17 | 2.42
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0028 | 101.9 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00288 | 101.9 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00324 | 103.04 | Base Case | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00332 | 103.04 | Base Case | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05017 | 105.71 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05307 | 105.71 | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00649 | 100.49 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00662 | 100.49 | P13:20-161:ALTW:AUTO-SINGLE:BURLIN1G:BRLGTN5:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | 864 | 864 | 0.06745 | 105.2 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | 864 | 864 | 0.07317 | 105.2 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.07077 | 133.2 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 118.83 | 14.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.07047 | 133.2 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 118.83 | 14.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01193 | 130.74 | P23:345:MEC:GDMEC 901 | External | 126.29 | 4.45
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01242 | 130.74 | P23:345:MEC:GDMEC 901 | External | 126.29 | 4.45
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04599 | 107.85 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04519 | 107.85 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.15108 | 106.09 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.14996 | 106.09 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01575 | 128.01 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 125.72 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01528 | 128.01 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 125.72 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.0351 | 127.88 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 119.77 | 8.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.03503 | 127.88 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 119.77 | 8.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00043 | 110.59 | P23:345:AMMO::MONTGOMERY:V43 | External | 109.55 | 1.04
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 110.59 | P23:345:AMMO::MONTGOMERY:V43 | External | 109.55 | 1.04
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00115 | 145.72 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 144.01 | 1.71
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00121 | 145.72 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 144.01 | 1.71
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.03048 | 125.84 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 119.11 | 6.73
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0309 | 125.84 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External | 119.11 | 6.73
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03018 | 109.32 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00155 | 108.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.5 | 0.27
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00158 | 108.77 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.5 | 0.27
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 55 | 55 | 0.00039 | 104.79 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 103.49 | 1.3
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 608718 16L TAP7 115 608720 COTTNTP7 115 1 | 55 | 55 | 0.00041 | 104.79 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 103.49 | 1.3
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1254 | 1254 | 0.05416 | 109.09 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal | 106.3 | 2.79
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1254 | 1254 | 0.05326 | 109.09 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal | 106.3 | 2.79
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04486 | 106.78 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 104.6 | 2.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04414 | 106.78 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal | 104.6 | 2.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 400 | 440 | 0.03449 | 105.97 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 101.4 | 4.57
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 400 | 440 | 0.03369 | 105.97 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 101.4 | 4.57
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 115.62 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 110.48 | 5.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 115.62 | 300107 5OSBORN 161 301310 5REX 161 1: 300107 5OSBORN 161 301310 5REX 161 1 | External | 110.48 | 5.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00155 | 148.93 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 147.77 | 1.16
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00159 | 148.93 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 147.77 | 1.16
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01991 | 122.26 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 115.83 | 6.43
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01955 | 122.26 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 115.83 | 6.43
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02187 | 110.85 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02238 | 110.85 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.0351 | 118 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 109.82 | 8.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.03503 | 118 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 109.82 | 8.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 102.24 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 101.69 | 0.55
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 102.24 | 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1: 608668 CLOQUET7 115 618019 GRE-KNFFLTP7 115 1 | External | 101.69 | 0.55
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00619 | 101.79 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0064 | 101.79 | 631109 BRLGTN 5 161 631216 WEVER5 161 1: 631109 BRLGTN 5 161 631216 WEVER5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00043 | 110.57 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 109.64 | 0.93
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 110.57 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 109.64 | 0.93
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0665 | 131.76 | P23:345:AMMO::ZACHARY:1 | External | 129.39 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06761 | 131.76 | P23:345:AMMO::ZACHARY:1 | External | 129.39 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01252 | 152.76 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 148.07 | 4.69
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01302 | 152.76 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 148.07 | 4.69
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01712 | 106.94 | P23:345:MEC:GDMEC 901 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01746 | 106.94 | P23:345:MEC:GDMEC 901 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 184 | 199 | 0.03484 | 132.41 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 118.19 | 14.22
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 184 | 199 | 0.03561 | 132.41 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 118.19 | 14.22
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02183 | 107.86 | P23:345:MEC:GDMEC 901 | External | 103.66 | 4.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02234 | 107.86 | P23:345:MEC:GDMEC 901 | External | 103.66 | 4.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 112.79 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 110.53 | 2.26
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00027 | 112.79 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 110.53 | 2.26
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.0351 | 115.08 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.78 | 8.3
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.03503 | 115.08 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.78 | 8.3
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05017 | 105.71 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05307 | 105.71 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00874 | 122.87 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 118.61 | 4.26
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00923 | 122.87 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 118.61 | 4.26
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01101 | 142.2 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 136.72 | 5.48
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01156 | 142.2 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 136.72 | 5.48
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05422 | 105.3 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 102.62 | 2.68
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05347 | 105.3 | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 102.62 | 2.68
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.02933 | 104.35 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.0293 | 104.35 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00411 | 132.61 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 128.99 | 3.62
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00422 | 132.61 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 128.99 | 3.62
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.03507 | 109.22 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300104 5NODWAY 161 1 | 227 | 227 | 0.03642 | 109.22 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08759 | 108.34 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 103.8 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08937 | 108.34 | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | External | 103.8 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04591 | 107.7 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04511 | 107.7 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04852 | 111.98 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 110.02 | 1.96
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04911 | 111.98 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 110.02 | 1.96
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00411 | 121.29 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 117.51 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00422 | 121.29 | P12:115:ITCM:BL PLN - M-TOWN 7:IA-SW | External | 117.51 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01236 | 123.85 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 120.83 | 3.02
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01251 | 123.85 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External | 120.83 | 3.02
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 55 | 55 | 0.00039 | 102.16 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.9 | 1.26
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 608720 COTTNTP7 115 618001 GRE-BERGNTP7 115 1 | 55 | 55 | 0.00041 | 102.16 | 608615 ARROWHD4 230 608624 FORBES 4 230 1: 608615 ARROWHD4 230 608624 FORBES 4 230 1 | External | 100.9 | 1.26
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00924 | 128.86 | Base Case | External | 125.14 | 3.72
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.00968 | 128.86 | Base Case | External | 125.14 | 3.72
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0908 | 127.31 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 121.92 | 5.39
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09264 | 127.31 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | External | 121.92 | 5.39
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.14145 | 102.43 | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13809 | 102.43 | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02088 | 106.88 | P42:345:NPPD:BKR-C-3322-2 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02178 | 106.88 | P42:345:NPPD:BKR-C-3322-2 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 7e-05 | 128.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 128.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02187 | 110.85 | P23:345:MEC:MONTEZUMA 901 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02238 | 110.85 | P23:345:MEC:MONTEZUMA 901 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01703 | 108.91 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.76 | 6.15
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01736 | 108.91 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 102.76 | 6.15
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01245 | 120.88 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 114.76 | 6.12
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01288 | 120.88 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 114.76 | 6.12
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01099 | 141.87 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 136.41 | 5.46
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01154 | 141.87 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 136.41 | 5.46
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.0659 | 130.34 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 128.03 | 2.31
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.06702 | 130.34 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 128.03 | 2.31
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 606 | 606 | 0.06594 | 106.51 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 606 | 606 | 0.06319 | 106.51 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01259 | 150.07 | P23:345:MEC:GDMEC 901 | External | 145.4 | 4.67
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01311 | 150.07 | P23:345:MEC:GDMEC 901 | External | 145.4 | 4.67
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0665 | 131.28 | P23:345:AMMO::ZACHARY:1 | External | 128.15 | 3.13
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06761 | 131.28 | P23:345:AMMO::ZACHARY:1 | External | 128.15 | 3.13
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.05871 | 100.78 | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.06026 | 100.78 | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0028 | 101.84 | P23:345:MEC:LOUISA 954 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00288 | 101.84 | P23:345:MEC:LOUISA 954 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00649 | 100.85 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00662 | 100.85 | P11:20:ALTW:AUTO-SINGLE:BURLIN1G:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10374 | 123.42 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 105.22 | 18.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10329 | 123.42 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 105.22 | 18.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0659 | 124.01 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 121.34 | 2.67
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06702 | 124.01 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 121.34 | 2.67
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02321 | 105.83 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | External | 100.59 | 5.24
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.02324 | 105.83 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | External | 100.59 | 5.24
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00483 | 116.95 | P23:345:MEC:GDMEC 901 | External | 113.01 | 3.94
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00494 | 116.95 | P23:345:MEC:GDMEC 901 | External | 113.01 | 3.94
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00874 | 110.04 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 105.93 | 4.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00923 | 110.04 | 627062 BISON 3 345 631197 LEDYARD3 345 1: 627062 BISON 3 345 631197 LEDYARD3 345 1 | External | 105.93 | 4.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0659 | 132.07 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 129.76 | 2.31
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06702 | 132.07 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 129.76 | 2.31
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02837 | 117.09 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 110.89 | 6.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02882 | 117.09 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 110.89 | 6.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00155 | 113.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.88 | 0.26
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00158 | 113.14 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.88 | 0.26
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01991 | 122.26 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 115.83 | 6.43
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01955 | 122.26 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 115.83 | 6.43
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 606 | 606 | 0.06594 | 106.51 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300039 7FAIRPT 345 3 | 606 | 606 | 0.06319 | 106.51 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08711 | 101.08 | P23:345:MEC:GDMEC 903 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.089 | 101.08 | P23:345:MEC:GDMEC 903 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.17416 | 119.75 | P42:345:NPPD:BKR-C-3322-2 | Internal | 107.61 | 12.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.17085 | 119.75 | P42:345:NPPD:BKR-C-3322-2 | Internal | 107.61 | 12.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.07077 | 148.55 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 132.01 | 16.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.07047 | 148.55 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 132.01 | 16.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01159 | 115.44 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01205 | 115.44 | 631140 SALEM 3 345 631191 HCKRYCK3 345 1: 631140 SALEM 3 345 631191 HCKRYCK3 345 1 | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.0342 | 113.4 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 103.82 | 9.58
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.03415 | 113.4 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 103.82 | 9.58
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 114.76 | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 114.76 | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08599 | 107.17 | P23:345:MEC:NORWALK 901 | External | 102.62 | 4.55
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08769 | 107.17 | P23:345:MEC:NORWALK 901 | External | 102.62 | 4.55
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01186 | 133.34 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 128.86 | 4.48
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01234 | 133.34 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 128.86 | 4.48
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02385 | 100.71 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02387 | 100.71 | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 107.22 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 102.57 | 4.65
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 107.22 | 300036 5MPLTAP 161 301310 5REX 161 1: 300036 5MPLTAP 161 301310 5REX 161 1 | External | 102.57 | 4.65
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02455 | 103.4 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02472 | 103.4 | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 114.76 | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 114.76 | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 113.53 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 111.26 | 2.27
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00027 | 113.53 | 300499 5HINTON 161 300953 5HARRSBRG 161 1: 300499 5HINTON 161 300953 5HARRSBRG 161 1 | External | 111.26 | 2.27
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08621 | 108.17 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 103.58 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08795 | 108.17 | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | External | 103.58 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04591 | 107.66 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04511 | 107.66 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01734 | 116.37 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 111.27 | 5.1
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.01698 | 116.37 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 111.27 | 5.1
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.07077 | 148.55 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 132.01 | 16.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541258 WOODBIN5 161 1 | 334 | 334 | 0.07047 | 148.55 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 132.01 | 16.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02429 | 107.62 | P23:345:MEC:SYCAMORE 905 | External | 103.8 | 3.82
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635601 GRIMES 5 161 635605 GRNGRTP5 161 1 | 373 | 395 | 0.02471 | 107.62 | P23:345:MEC:SYCAMORE 905 | External | 103.8 | 3.82
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04591 | 107.66 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 997784 ST. JOSEPH33 161 33 | 300 | 330 | 0.04511 | 107.66 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03484 | 127.22 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 114.03 | 13.19
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03561 | 127.22 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 114.03 | 13.19
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 7e-05 | 128.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 128.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 112.68 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 110.4 | 2.28
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00027 | 112.68 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 110.4 | 2.28
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01201 | 103.42 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 101.39 | 2.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01236 | 103.42 | 631110 WAPELLO5 161 631115 OTTUMWA5 161 2: 631110 WAPELLO5 161 631115 OTTUMWA5 161 2 | External | 101.39 | 2.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00468 | 107.28 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 104.14 | 3.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00488 | 107.28 | 631140 SALEM 3 345 631141 ROCK CK3 345 1: 631140 SALEM 3 345 631141 ROCK CK3 345 1 | External | 104.14 | 3.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04852 | 111.9 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 109.89 | 2.01
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04911 | 111.9 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 109.89 | 2.01
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00479 | 120.79 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 117.24 | 3.55
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.0049 | 120.79 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 117.24 | 3.55
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00115 | 134.72 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 134.01 | 0.71
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00118 | 134.72 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 134.01 | 0.71
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01048 | 128.65 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 123.47 | 5.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.011 | 128.65 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 123.47 | 5.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01123 | 100.4 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01143 | 100.4 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00075 | 109.49 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 108.28 | 1.21
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00079 | 109.49 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 108.28 | 1.21
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01169 | 163.18 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 157.13 | 6.05
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01227 | 163.18 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 157.13 | 6.05
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10985 | 132.33 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 124.02 | 8.31
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.11144 | 132.33 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 124.02 | 8.31
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04852 | 109.32 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 107.57 | 1.75
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04911 | 109.32 | 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1: 635740 DIAMOND TRL3 345 637067 DIAM TR WIND 345 1 | External | 107.57 | 1.75
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00483 | 126.84 | P23:345:MEC:GDMEC 902 | External | 123.31 | 3.53
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00494 | 126.84 | P23:345:MEC:GDMEC 902 | External | 123.31 | 3.53
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1215 | 1325 | 0.09066 | 102.18 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1215 | 1325 | 0.08981 | 102.18 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02818 | 115.7 | P23:345:MEC:GDMEC 901 | External | 109.49 | 6.21
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.0286 | 115.7 | P23:345:MEC:GDMEC 901 | External | 109.49 | 6.21
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00498 | 120.9 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00522 | 120.9 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00864 | 103.18 | P23:345:MEC:BLACK HAWK 901 | External | 100.27 | 2.91
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00901 | 103.18 | P23:345:MEC:BLACK HAWK 901 | External | 100.27 | 2.91
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04599 | 107.89 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04519 | 107.89 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13888 | 100.08 | P42:345:NPPD:BKR-CPR-3304 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13384 | 100.08 | P42:345:NPPD:BKR-CPR-3304 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01159 | 115.44 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01205 | 115.44 | P12:345:ALTW:AUTO-SINGLE:SALEM3:HCKRYCK3:1 | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.14145 | 102.43 | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.13809 | 102.43 | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02837 | 117.09 | P23:345:MEC:MONTEZUMA 901 | External | 110.89 | 6.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02882 | 117.09 | P23:345:MEC:MONTEZUMA 901 | External | 110.89 | 6.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.116 | 129.08 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 121.51 | 7.57
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.11852 | 129.08 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 121.51 | 7.57
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 102.52 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 101.98 | 0.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 102.52 | 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1: 608663 FLDWDTP7 115 608670 MDWLNDS7 115 1 | External | 101.98 | 0.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01201 | 103.42 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 101.39 | 2.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01236 | 103.42 | P12:161:ALTW:AUTO-SINGLE:WAPELLO5:OTTUMWA5:2 | External | 101.39 | 2.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 111.95 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 109.68 | 2.27
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00027 | 111.95 | 300499 5HINTON 161 343001 5BOLSTAD 161 1: 300499 5HINTON 161 343001 5BOLSTAD 161 1 | External | 109.68 | 2.27
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.0351 | 115.08 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.78 | 8.3
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 300091 5LATHRP 161 1 | 227 | 227 | 0.03503 | 115.08 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 106.78 | 8.3
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 105.89 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 105.17 | 0.72
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00037 | 105.89 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 105.17 | 0.72
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00411 | 121.79 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 118.01 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00422 | 121.79 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 118.01 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00468 | 107.28 | P12:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 104.14 | 3.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00488 | 107.28 | P12:345:ALTW:AUTO-SINGLE:SALEM3:ROCKCK3:1 | External | 104.14 | 3.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00416 | 106.63 | P23:345:ALTW:MITCHLCO:1160 | External | 104.22 | 2.41
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00439 | 106.63 | P23:345:ALTW:MITCHLCO:1160 | External | 104.22 | 2.41
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00095 | 138.95 | P12:161:DPC:RCE-HAR5 | External | 137.03 | 1.92
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.001 | 138.95 | P12:161:DPC:RCE-HAR5 | External | 137.03 | 1.92
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01153 | 119.05 | P23:345:MEC:GDMEC 901 | External | 114.49 | 4.56
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.012 | 119.05 | P23:345:MEC:GDMEC 901 | External | 114.49 | 4.56
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10374 | 127.83 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 108.31 | 19.52
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10329 | 127.83 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 108.31 | 19.52
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.10985 | 132.33 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 124.02 | 8.31
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.11144 | 132.33 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 124.02 | 8.31
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 400 | 440 | 0.03449 | 105.97 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 101.4 | 4.57
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541202 SIBLEY 5 161 997782 SIBLEY11 161 11 | 400 | 440 | 0.03369 | 105.97 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 101.4 | 4.57
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00498 | 120.9 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00522 | 120.9 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01673 | 137.92 | P24:345:AMMO::MCCREDIE:1 | External | 136.32 | 1.6
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01587 | 137.92 | P24:345:AMMO::MCCREDIE:1 | External | 136.32 | 1.6
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 104.37 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300290 2OSBORN 69.0 300107 5OSBORN 161 1 | 56 | 56 | 0.00382 | 104.37 | 300036 5MPLTAP 161 300091 5LATHRP 161 1: 300036 5MPLTAP 161 300091 5LATHRP 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00843 | 108.46 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 105.97 | 2.49
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00858 | 108.46 | 300044 7MCCRED 345 300049 7THOMHL 345 1: 300044 7MCCRED 345 300049 7THOMHL 345 1 | External | 105.97 | 2.49
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 400 | 440 | 0.03449 | 104.54 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 100.35 | 4.19
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 400 | 440 | 0.03369 | 104.54 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 100.35 | 4.19
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.0908 | 128.84 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 123.74 | 5.1
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 926 | 1010 | 0.09264 | 128.84 | 635730 MNTZUMA3 345 635737 J475-J555POI 345 1: 635730 MNTZUMA3 345 635737 J475-J555POI 345 1 | External | 123.74 | 5.1
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1215 | 1325 | 0.09066 | 102.18 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1215 | 1325 | 0.08981 | 102.18 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07141 | 127.85 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 125.19 | 2.66
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.07268 | 127.85 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External | 125.19 | 2.66
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.07077 | 133.2 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 118.83 | 14.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 541258 WOODBIN5 161 1 | 357 | 390 | 0.07047 | 133.2 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 118.83 | 14.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00155 | 148.93 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 147.77 | 1.16
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00159 | 148.93 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 147.77 | 1.16
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03274 | 113.04 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal | 105.78 | 7.26
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03194 | 113.04 | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | Internal | 105.78 | 7.26
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631036 NIW 5 161 631202 COLBY5 161 1 | 200 | 200 | 0.00745 | 108.74 | P23:345:MEC:BLACK HAWK 901 | External | 105.8 | 2.94
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631036 NIW 5 161 631202 COLBY5 161 1 | 200 | 200 | 0.00774 | 108.74 | P23:345:MEC:BLACK HAWK 901 | External | 105.8 | 2.94
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04852 | 112.32 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 110.85 | 1.47
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04911 | 112.32 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 110.85 | 1.47
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00041 | 105.78 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 105.05 | 0.73
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 25 | 25 | 0.00037 | 105.78 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External | 105.05 | 0.73
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02726 | 118.94 | P23:345:MEC:GDMEC 901 | External | 113.67 | 5.27
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02788 | 118.94 | P23:345:MEC:GDMEC 901 | External | 113.67 | 5.27
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00043 | 110.71 | P23:345:AMMO::MONTGOMERY:V43 | External | 109.66 | 1.05
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 110.71 | P23:345:AMMO::MONTGOMERY:V43 | External | 109.66 | 1.05
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02731 | 119.02 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02794 | 119.02 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04852 | 105.16 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 103.32 | 1.84
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04911 | 105.16 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 103.32 | 1.84
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01198 | 140.6 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 135.31 | 5.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01255 | 140.6 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 135.31 | 5.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.05871 | 100.78 | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.06026 | 100.78 | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02326 | 105.28 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 101.24 | 4.04
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02396 | 105.28 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 101.24 | 4.04
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10374 | 123.42 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 105.22 | 18.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541401 EASTOWN5 161 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10329 | 123.42 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 105.22 | 18.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.08316 | 102.97 | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.08158 | 102.97 | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01712 | 106.94 | P23:345:MEC:BONDURANT 906 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01746 | 106.94 | P23:345:MEC:BONDURANT 906 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04852 | 129.35 | Base Case | External | 126.86 | 2.49
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04911 | 129.35 | Base Case | External | 126.86 | 2.49
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00999 | 125.04 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 123.62 | 1.42
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00969 | 125.04 | 92351: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | External | 123.62 | 1.42
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07796 | 104.52 | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.07667 | 104.52 | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.0442 | 151.15 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal | 131.49 | 19.66
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.04601 | 151.15 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal | 131.49 | 19.66
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.03507 | 100.83 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300097 5MARYVL 161 300104 5NODWAY 161 1 | 247 | 247 | 0.03642 | 100.83 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00028 | 114.04 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 111.02 | 3.02
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 1 | 25 | 25 | 0.00027 | 114.04 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 111.02 | 3.02
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00411 | 132.97 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 129.48 | 3.49
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00422 | 132.97 | P12:161:ALTW:AUTO-SINGLE:TOLEDO5:M-TOWN5:1 | External | 129.48 | 3.49
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 113.92 | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 110.89 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 113.92 | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | Internal | 110.89 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01046 | 128.26 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 123.1 | 5.16
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01097 | 128.26 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 123.1 | 5.16
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04599 | 107.85 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541253 ST JOE 5 161 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04519 | 107.85 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04852 | 129.99 | Base Case | External | 127.81 | 2.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04911 | 129.99 | Base Case | External | 127.81 | 2.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02845 | 119.85 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 113.56 | 6.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631117 REASNOR5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02891 | 119.85 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 113.56 | 6.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00217 | 105.59 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 103.17 | 2.42
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636051 WRIGHT 8 69.0 1 | 83.3 | 83.3 | 0.00227 | 105.59 | P12:161:MEC:AUTO-SINGLE:WRIGHT5:WALLLK5:1 | External | 103.17 | 2.42
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01193 | 130.74 | P23:345:MEC:GDMEC 902 | External | 126.29 | 4.45
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.01242 | 130.74 | P23:345:MEC:GDMEC 902 | External | 126.29 | 4.45
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.07077 | 115.96 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.07047 | 115.96 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00095 | 140.4 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 138.11 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.001 | 140.4 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 138.11 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.01151 | 154.33 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 150.23 | 4.1
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631051 HAZLTON L2 5 161 636210 WASHBRN5 161 1 | 196 | 196 | 0.012 | 154.33 | 69846: 631139 HAZLTON3 345 636199 BLACKHAWK 3 345 1 631050 HAZLTON L1 5 161 636200 BLACKHAWK 5 161 1 | External | 150.23 | 4.1
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 114.76 | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 542980 NASHUA 7 345 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 114.76 | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 111.81 | 2.95
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02187 | 110.85 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02238 | 110.85 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | External | 105.88 | 4.97
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00101 | 141.17 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.15 | 0.02
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00103 | 141.17 | P23:500:EES-EAI:WH_BLF:B7914 | External | 141.15 | 0.02
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01855 | 104.3 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01861 | 104.3 | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 601028 EAU CL 3 345 997656 EAU CL 3 161 9 | 300 | 334.6 | 0.00335 | 114.21 | P23:345:XEL:8E5 ECL BS | External | 112.17 | 2.04
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 601028 EAU CL 3 345 997656 EAU CL 3 161 9 | 300 | 334.6 | 0.00354 | 114.21 | P23:345:XEL:8E5 ECL BS | External | 112.17 | 2.04
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00876 | 110.64 | Base Case | External | 107.03 | 3.61
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.00918 | 110.64 | Base Case | External | 107.03 | 3.61
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 113.91 | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 110.88 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 113.91 | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 110.88 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03484 | 122.38 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 110.09 | 12.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03561 | 122.38 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 110.09 | 12.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00479 | 131.25 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 127.75 | 3.5
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.0049 | 131.25 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 127.75 | 3.5
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.01196 | 101.97 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 100.04 | 1.93
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631115 OTTUMWA5 161 1 | 307 | 307 | 0.0123 | 101.97 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 2:IA-SW | External | 100.04 | 1.93
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.00422 | 107.71 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 105.46 | 2.25
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631059 8TH ST.5 161 681520 GALENA 5 161 1 | 127 | 127 | 0.0044 | 107.71 | P23:345:ITCM:ROCK CK3 180-181-182:IA-EC | External | 105.46 | 2.25
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82989 | 128.96 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.03751 | 152.74 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 142.94 | 9.8
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.03741 | 152.74 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 142.94 | 9.8
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00411 | 132.97 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 129.48 | 3.49
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00422 | 132.97 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 129.48 | 3.49
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02753 | 121.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.62 | 5.47
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.0282 | 121.09 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 115.62 | 5.47
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01712 | 106.94 | P23:345:MEC:GDMEC 902 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01746 | 106.94 | P23:345:MEC:GDMEC 902 | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 400 | 440 | 0.03449 | 104.54 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 100.35 | 4.19
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541201 SIBLEY 7 345 997782 SIBLEY11 161 11 | 400 | 440 | 0.03369 | 104.54 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 100.35 | 4.19
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02183 | 107.86 | P23:345:MEC:GDMEC 902 | External | 103.66 | 4.2
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631143 OTTUMWA3 345 631115 OTTUMWA5 161 1 | 400 | 400 | 0.02234 | 107.86 | P23:345:MEC:GDMEC 902 | External | 103.66 | 4.2
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00416 | 106.54 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 104.16 | 2.38
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00439 | 106.54 | P55:345:ITCM:MITCHLCO3 N9-N10:IA | External | 104.16 | 2.38
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00483 | 116.95 | P23:345:MEC:GDMEC 902 | External | 113.01 | 3.94
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00494 | 116.95 | P23:345:MEC:GDMEC 902 | External | 113.01 | 3.94
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00786 | 103.16 | P24:345:AMMO::MCCREDIE:1 | External | 100.81 | 2.35
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300120 5THMHILB1 161 300126 5MOBTAP 161 1 | 372 | 372 | 0.00808 | 103.16 | P24:345:AMMO::MCCREDIE:1 | External | 100.81 | 2.35
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.03507 | 119.59 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 107.89 | 11.7
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.03642 | 119.59 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 107.89 | 11.7
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631036 NIW 5 161 631202 COLBY5 161 1 | 200 | 200 | 0.00707 | 105.16 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External | 102.42 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631036 NIW 5 161 631202 COLBY5 161 1 | 200 | 200 | 0.00734 | 105.16 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External | 102.42 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0028 | 101.9 | P22:345:MEC:SUB 92 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00288 | 101.9 | P22:345:MEC:SUB 92 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.0028 | 101.9 | P23:345:MEC:HILLS 9114 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631022 SUTLIFF7 115 631023 CALAMUS7 115 1 | 73 | 73 | 0.00288 | 101.9 | P23:345:MEC:HILLS 9114 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01133 | 127.32 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 121.71 | 5.61
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01187 | 127.32 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 121.71 | 5.61
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.08711 | 101.08 | P23:345:MEC:GDMEC 904 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 956 | 1152 | 0.089 | 101.08 | P23:345:MEC:GDMEC 904 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01278 | 161.47 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 155.9 | 5.57
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01339 | 161.47 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | External | 155.9 | 5.57
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00999 | 125.2 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 123.79 | 1.41
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00969 | 125.2 | 92355: 300003 1THLG3 24.0 300049 7THOMHL 345 1 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 123.79 | 1.41
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01159 | 115.44 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631056 LORE 5 161 631159 HCKRYCK5 161 1 | 335 | 335 | 0.01205 | 115.44 | P14:345:ITCM:HCKRYCK-SALEM 40MVAR:IA-SS | External | 113.07 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.00619 | 101.79 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631084 VIELE 5 161 631108 DENMARK5 161 1 | 162 | 162 | 0.0064 | 101.79 | P12:161:ALTW:AUTO-SINGLE:BRLGTN5:WEVER5:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01618 | 102.24 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01708 | 102.24 | P12:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01575 | 128.01 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 125.72 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01528 | 128.01 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External | 125.72 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00498 | 120.9 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00522 | 120.9 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 118.16 | 2.74
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00828 | 100.62 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631154 BARTON5 161 631160 LIME CK L2 5 161 1 | 240 | 240 | 0.00864 | 100.62 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1: 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05017 | 105.71 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 864 | 864 | 0.05307 | 105.71 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | External | 101.12 | 4.59
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03587 | 113.92 | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 110.89 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 543028 NASHUA-5 161 997751 NASHUA11 161 11 | 650 | 715 | 0.03535 | 113.92 | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal | 110.89 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.02933 | 114.6 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 107.43 | 7.17
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.0293 | 114.6 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 107.43 | 7.17
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.17264 | 122.11 | P42:345:NPPD:BKR-CPR-3322 | Internal | 110.23 | 11.88
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.1689 | 122.11 | P42:345:NPPD:BKR-CPR-3322 | Internal | 110.23 | 11.88
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02731 | 119.02 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02794 | 119.02 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.04368 | 111.67 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635031 BUNGE 5 161 635032 HASTING5 161 1 | 199 | 199 | 0.04539 | 111.67 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03292 | 114.49 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal | 107.31 | 7.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03211 | 114.49 | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | Internal | 107.31 | 7.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.07077 | 115.96 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 334 | 334 | 0.07047 | 115.96 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01259 | 150.07 | P23:345:MEC:GDMEC 902 | External | 145.4 | 4.67
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01311 | 150.07 | P23:345:MEC:GDMEC 902 | External | 145.4 | 4.67
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00155 | 107.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.7 | 0.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00158 | 107.99 | P23:500:EES-EAI:WH_BLF:B7914 | External | 107.7 | 0.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04852 | 105.66 | Base Case | External | 103.37 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04911 | 105.66 | Base Case | External | 103.37 | 2.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01309 | 101.49 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01333 | 101.49 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03484 | 122.38 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 110.09 | 12.29
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 184 | 199 | 0.03561 | 122.38 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal | 110.09 | 12.29
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.17269 | 121.67 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 109.99 | 11.68
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.16897 | 121.67 | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal | 109.99 | 11.68
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.0351 | 118 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 109.82 | 8.18
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300036 5MPLTAP 161 301310 5REX 161 1 | 227 | 227 | 0.03503 | 118 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 109.82 | 8.18
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.0442 | 124.81 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 106.71 | 18.1
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635034 CLRNDA 5 161 635038 BRADDYVILLE5 161 1 | 199 | 199 | 0.04601 | 124.81 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | External | 106.71 | 18.1
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01236 | 116.53 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 113.6 | 2.93
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01251 | 116.53 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | External | 113.6 | 2.93
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00649 | 100.49 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631111 JEFF 5 161 1 | 223 | 223 | 0.00662 | 100.49 | 631109 BRLGTN 5 161 629071 BURLIN1G 20 1: 631109 BRLGTN 5 161 629071 BURLIN1G 20.0 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 446 | 446 | 0.03449 | 104.64 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 100.1 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 446 | 446 | 0.03369 | 104.64 | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Internal | 100.1 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00026 | 102.3 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 101.75 | 0.55
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 608665 THOMSON7 115 608667 POTLTCH7 115 1 | 84 | 84 | 0.00028 | 102.3 | 608670 MDWLNDS7 115 608671 BURNETT7 115 1: 608670 MDWLNDS7 115 608671 BURNETT7 115 1 | External | 101.75 | 0.55
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10374 | 127.83 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 108.31 | 19.52
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541400 EASTOWN7 345 997766 EASTOWNE11 161 11 | 400 | 440 | 0.10329 | 127.83 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal | 108.31 | 19.52
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.0665 | 133.64 | P23:345:AMMO::ZACHARY:1 | External | 131.27 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.06761 | 133.64 | P23:345:AMMO::ZACHARY:1 | External | 131.27 | 2.37
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04852 | 111.9 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 109.89 | 2.01
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 956 | 1152 | 0.04911 | 111.9 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 109.89 | 2.01
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04852 | 105.27 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 103.49 | 1.78
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.04911 | 105.27 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1 | External | 103.49 | 1.78
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00179 | 101.88 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:DENMARK5:1 | External | 101.63 | 0.25
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00182 | 101.88 | P12:161:ALTW:AUTO-SINGLE:HENRYCO5:DENMARK5:1 | External | 101.63 | 0.25
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.0086 | 121.04 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 116.82 | 4.22
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631045 HUNTLEY5 161 631180 FREEBORN5 161 1 | 200 | 200 | 0.00908 | 121.04 | P42:345:ITCM:COLBY3-LEDYARD3 9450-9460:IA-MVP | External | 116.82 | 4.22
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01855 | 104.3 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.01861 | 104.3 | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.03125 | 136.75 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 127.89 | 8.86
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300107 5OSBORN 161 1 | 227 | 227 | 0.0312 | 136.75 | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | External | 127.89 | 8.86
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02731 | 119.02 | P23:345:MEC:MONTEZUMA 901 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02794 | 119.02 | P23:345:MEC:MONTEZUMA 901 | External | 113.91 | 5.11
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 602021 EAU CLA5 161 997656 EAU CL 3 161 9 | 300 | 334.6 | 0.00335 | 117.74 | P23:345:XEL:8E5 ECL BS | External | 115.49 | 2.25
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 602021 EAU CLA5 161 997656 EAU CL 3 161 9 | 300 | 334.6 | 0.00354 | 117.74 | P23:345:XEL:8E5 ECL BS | External | 115.49 | 2.25
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00588 | 106.93 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00613 | 106.93 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00043 | 110.69 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 109.76 | 0.93
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 25 | 25 | 0.00041 | 110.69 | P12:345:AMMO::MONTGOMERY:OVERTON:5 | External | 109.76 | 0.93
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 7e-05 | 128.03 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 661008 BEULAH 7 115 661018 COYOTE 7 115 1 | 120 | 131 | 4e-05 | 128.03 | 657791 CENTER 3 345 661016 COYOTE 3 345 1: 657791 CENTER 3 345 661016 COYOTE 3 345 1 | External | 127.89 | 0.14
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00028 | 114.78 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 111.75 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300505 2STURGN 69.0 300508 5STURGN 161 2 | 25 | 25 | 0.00027 | 114.78 | 300066 5HIGBEE 161 300953 5HARRSBRG 161 1: 300066 5HIGBEE 161 300953 5HARRSBRG 161 1 | External | 111.75 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02349 | 102.14 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635670 DMOINES5 161 635675 RISING SUN 5 161 1 | 325 | 325 | 0.02374 | 102.14 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00483 | 126.84 | P23:345:MEC:GDMEC 901 | External | 123.31 | 3.53
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631013 BLRSTWN7 115 631017 PRAR CK7 115 1 | 81 | 81 | 0.00494 | 126.84 | P23:345:MEC:GDMEC 901 | External | 123.31 | 3.53
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05758 | 122.36 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal | 119.11 | 3.25
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05672 | 122.36 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | Internal | 119.11 | 3.25
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00588 | 106.93 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00613 | 106.93 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02088 | 106.85 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300073 5GENTRY 161 300076 5FAIRPT 161 1 | 227 | 227 | 0.02178 | 106.85 | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00999 | 125.2 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 123.79 | 1.41
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300076 5FAIRPT 161 300087 5HICKCK 161 1 | 203 | 203 | 0.00969 | 125.2 | 104738: 300002 1THLG2 22.0 300132 5THMHLB2 161 1 300001 1THLG1 20.0 300120 5THMHILB1 161 1 300003 1THLG3 24.0 300049 7THOMHL 345 1 546702 NMGEN N1 20.0 546703 NMISOBUS 20.0 1 | External | 123.79 | 1.41
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01245 | 115.07 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 110.31 | 4.76
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 631112 APANOSE5 161 1 | 171 | 171 | 0.01288 | 115.07 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External | 110.31 | 4.76
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.0342 | 113.4 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 103.82 | 9.58
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300091 5LATHRP 161 300098 5MOCITY 161 1 | 227 | 227 | 0.03415 | 113.4 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 103.82 | 9.58
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04599 | 107.89 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541199 ST JOE 3 345 997785 ST. JOSEPH22 161 22 | 300 | 330 | 0.04519 | 107.89 | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 152 | 171 | 0.03018 | 109.31 | P42:345:NPPD:BKR-C-3322-2 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01712 | 106.94 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631107 JASPER 5 161 635710 NEANKNY5 161 1 | 212 | 212 | 0.01746 | 106.94 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | External | 100.91 | 6.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.08316 | 102.97 | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 531451 MINGO 7 345 640325 REDWILO3 345 1 | 785 | 785 | 0.08158 | 102.97 | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Internal
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01236 | 123.88 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 120.85 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631085 PARNEL 5 161 631113 POWESHK5 161 1 | 240 | 240 | 0.01251 | 123.88 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | External | 120.85 | 3.03
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00416 | 106.63 | P23:345:ALTW:MITCHLCO:1150 | External | 104.22 | 2.41
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00439 | 106.63 | P23:345:ALTW:MITCHLCO:1150 | External | 104.22 | 2.41
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 646209 S1209 5 161 646231 S1231 5 161 1 | 238 | 238 | 0.14423 | 104.89 | 82319: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 | Internal | 123.96 | -19.07
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00411 | 121.79 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 118.01 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631004 M-TOWN 7 115 631013 BLRSTWN7 115 1 | 90 | 90 | 0.00422 | 121.79 | 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1: 631001 TOLEDO 5 161 631081 M-TOWN 5 161 1 | External | 118.01 | 3.78
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01153 | 119.05 | P23:345:MEC:GDMEC 902 | External | 114.49 | 4.56
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.012 | 119.05 | P23:345:MEC:GDMEC 902 | External | 114.49 | 4.56
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01618 | 102.24 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01708 | 102.24 | 631198 COLBY3 345 631199 KILLDEER3 345 1: 631198 COLBY3 345 631199 KILLDEER3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01618 | 102.24 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631198 COLBY3 345 631202 COLBY5 161 1 | 450 | 450 | 0.01708 | 102.24 | P21:345:ALTW:AUTO-SINGLE:COLBY3:KILLDEER3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00588 | 106.93 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 681532 WABACO 5 161 681537 ROCHSTR5 161 1 | 201 | 221.1 | 0.00613 | 106.93 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 103.54 | 3.39
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 446 | 446 | 0.03449 | 104.64 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 100.1 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 446 | 446 | 0.03369 | 104.64 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | Internal | 100.1 | 4.54
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04852 | 112.24 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 110.71 | 1.53
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04911 | 112.24 | 629074 ARNOLD1G 22 631088 ARNOLD 5 161 1: 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | External | 110.71 | 1.53
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01167 | 162.85 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 156.81 | 6.04
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.01225 | 162.85 | 627062 BISON 3 345 631198 COLBY3 345 1: 627062 BISON 3 345 631198 COLBY3 345 1 | External | 156.81 | 6.04
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00179 | 101.88 | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | External | 101.63 | 0.25
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300439 2HENRY 69.0 631106 HENRYCO5 161 1 | 56 | 56 | 0.00182 | 101.88 | 631106 HENRYCO5 161 631108 DENMARK5 161 1: 631106 HENRYCO5 161 631108 DENMARK5 161 1 | External | 101.63 | 0.25
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01123 | 100.29 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631083 TRAER 5 161 631086 DYSART 5 161 1 | 258 | 258 | 0.01143 | 100.29 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.0659 | 129.3 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 126.24 | 3.06
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 1010 | 0.06702 | 129.3 | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | External | 126.24 | 3.06
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02726 | 118.94 | P23:345:MEC:GDMEC 902 | External | 113.67 | 5.27
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 631113 POWESHK5 161 631117 REASNOR5 161 1 | 311 | 311 | 0.02788 | 118.94 | P23:345:MEC:GDMEC 902 | External | 113.67 | 5.27
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.05871 | 100.78 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | 1195 | 1304 | 0.06026 | 100.78 | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | External
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01146 | 121.84 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 117.18 | 4.66
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.01192 | 121.84 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External | 117.18 | 4.66
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04852 | 112.24 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 110.71 | 1.53
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 956 | 1152 | 0.04911 | 112.24 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1 | External | 110.71 | 1.53
Thermal | 09NR | S2 | 20G0 | GEN_025_028 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.0351 | 127.88 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 119.77 | 8.11
Thermal | 09NR | S2 | 20G0 | GEN_043_044_045 | FROM -> TO | 300107 5OSBORN 161 301310 5REX 161 1 | 227 | 227 | 0.03503 | 127.88 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | External | 119.77 | 8.11
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00092 | 159.32 | P23:500:EES-EAI:WH_BLF:B7914 | External | 159.49 | -0.17
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | 253 | 253 | 0.00094 | 159.32 | P23:500:EES-EAI:WH_BLF:B7914 | External | 159.49 | -0.17
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 100.68 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00084 | 100.68 | P12:230:EES:FRISCO_E:TEZCUC:2 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.00098 | 140.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.98 | -0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 1 | 420 | 420 | 0.001 | 140.83 | P23:500:EES-EAI:WH_BLF:B7914 | External | 140.98 | -0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00153 | 113.72 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.61 | 0.11
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | 266 | 266 | 0.00156 | 113.72 | P23:500:EES-EAI:WH_BLF:B7914 | External | 113.61 | 0.11
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00093 | 113.44 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 113.28 | 0.16
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 | 519 | 519 | 0.00094 | 113.44 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 113.28 | 0.16
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01545 | 102.7 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01498 | 102.7 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1: 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | External
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00108 | 150.22 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 148.84 | 1.38
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00114 | 150.22 | 631046 ADAMS 5 161 681527 BVR CRK5 161 1: 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | External | 148.84 | 1.38
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00153 | 108.63 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.49 | 0.14
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00156 | 108.63 | P23:500:EES-EAI:WH_BLF:B7914 | External | 108.49 | 0.14
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 146.9 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 145.67 | 1.23
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00162 | 146.9 | P13:69-161:ALTW:AUTO-SINGLE:WAPELLO8:WAPELLO5:1 | External | 145.67 | 1.23
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00037 | 112.33 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.38 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | 98 | 98 | 0.00038 | 112.33 | P23:500:EES-EAI:WH_BLF:B7914 | External | 112.38 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00445 | 128.25 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 127.98 | 0.27
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00455 | 128.25 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | External | 127.98 | 0.27
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00019 | 119.06 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 119.03 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 1 | 580 | 580 | 0.00019 | 119.06 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 119.03 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 603020 MAPLE R7 115 997612 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00052 | 121.89 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 121.81 | 0.08
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 603020 MAPLE R7 115 997612 MAPLE RIVER 69.0 1 | 129 | 140 | 0.00053 | 121.89 | 93772: 652435 FARGO 4 230 997173 FA KV1A 115 1 652436 FARGO 7 115 997173 FA KV1A 115 1 652434 FARGOSVC 13.2 997173 FA KV1A 115 1 652435 FARGO 4 230 652553 MOORHED4 230 1 652553 MOORHED4 230 652554 MORRIS 4 230 1 652553 MOORHED4 230 652587 MOORHED7 115 1 652553 MOORHED4 230 652587 MOORHED7 115 2 652435 FARGO 4 230 997172 FA KV2A 115 2 652436 FARGO 7 115 997172 FA KV2A 115 2 652434 FARGOSVC 13.2 997172 FA KV2A 115 2 602006 SHEYNNE4 230 652435 FARGO 4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 1 652435 FARGO 4 230 652444 JAMESTN4 230 2 | External | 121.81 | 0.08
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00032 | 109.38 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 108.95 | 0.43
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00033 | 109.38 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK15:GRE-SPRNGCK8:GRE-SPRNGC1T:1 | External | 108.95 | 0.43
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00153 | 115.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 115.7 | 0.12
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | 253 | 253 | 0.00156 | 115.82 | P23:500:EES-EAI:WH_BLF:B7914 | External | 115.7 | 0.12
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 121.34 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.34 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00027 | 102 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 101.56 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00029 | 102 | P11:34:DPC:AUTO-SINGLE:MCNEIL_W:1 | External | 101.56 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 601028 EAU CL 3 345 997643 EAU CL 3 161 9 | 330 | 334.6 | 0.00304 | 114.94 | P23:345:XEL:8E5 ECL BS | External | 114.06 | 0.88
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 601028 EAU CL 3 345 997643 EAU CL 3 161 9 | 330 | 334.6 | 0.00322 | 114.94 | P23:345:XEL:8E5 ECL BS | External | 114.06 | 0.88
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00118 | 136.62 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 135.89 | 0.73
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.0012 | 136.62 | P12:161:ITCM:OTTUMWA5 - WAPELLO5 1:IA-SW | External | 135.89 | 0.73
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.0007 | 121.46 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 120.45 | 1.01
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00074 | 121.46 | 681527 BVR CRK5 161 681528 HARMONY5 161 1: 681527 BVR CRK5 161 681528 HARMONY5 161 1 | External | 120.45 | 1.01
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00445 | 141.87 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 141.64 | 0.23
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615901 GRE-STANTON4 230 657756 SQBUTTE4 230 1 | 478 | 478 | 0.00455 | 141.87 | 65139: 615600 GRE-COAL CR4 230 615606 GRE-COALFB34 230 Z 615353 GRE-DICKNSN3 345 615357 GRE-DICKFB23 345 Z 615353 GRE-DICKNSN3 345 615356 GRE-DICKFB13 345 Z 615600 GRE-COAL CR4 230 615605 GRE-COALFB24 230 Z 615600 GRE-COAL CR4 230 615002 GRE-COAL 42G 22.0 1 615001 GRE-COAL 41G 22.0 | External | 141.64 | 0.23
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 121.69 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.69 | P13:161-69:EES-EAI:HERGET:AT1 | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00473 | 106.76 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00497 | 106.76 | 601039 NROC 3 345 601044 BRIGGS RD 3 345 1: 601039 NROC 3 345 601044 BRIGGS RD 3 345 1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00032 | 109.38 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 108.95 | 0.43
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615478 GRE-SPRGCK25 161 997539 161/69 69.0 2 | 70 | 70 | 0.00033 | 109.38 | 615477 GRE-SPRGCK15 161 3WXFMR 161/69 1: 615477 GRE-SPRGCK15 161 997545 161/69 69.0 1 615479 GRE-SPRNGCK8 69.0 997545 161/69 69.0 1 615480 GRE-SPRNGC1T 13.8 997545 161/69 69.0 1 | External | 108.95 | 0.43
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00013 | 100.8 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 100.62 | 0.18
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 100.8 | P12:230:OTP:AUTO-SINGLE:BROWNSV4:HANKSON4:1 | External | 100.62 | 0.18
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00089 | 155.46 | P12:161:DPC:RCE-HAR5 | External | 154.17 | 1.29
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00094 | 155.46 | P12:161:DPC:RCE-HAR5 | External | 154.17 | 1.29
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00473 | 106.76 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00497 | 106.76 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01644 | 111.22 | P24:345:AMMO::MCCREDIE:1 | External | 108.59 | 2.63
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01557 | 111.22 | P24:345:AMMO::MCCREDIE:1 | External | 108.59 | 2.63
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00158 | 146.9 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 145.67 | 1.23
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631110 WAPELLO5 161 630048 WAPELLO8 69.0 2 | 72 | 72 | 0.00162 | 146.9 | 631110 WAPELLO5 161 630048 WAPELLO8 69 1: 631110 WAPELLO5 161 630048 WAPELLO8 69.0 1 | External | 145.67 | 1.23
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.00022 | 110.59 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 110.08 | 0.51
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | 28 | 28 | 0.0002 | 110.59 | 300517 2KINGDM 69 300090 5KINGDM 161 2: 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | External | 110.08 | 0.51
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 100.68 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00084 | 100.68 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 100.68 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00084 | 100.68 | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1: 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00032 | 111.61 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 111.17 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00034 | 111.61 | P13:161-69-13:XEL:AUTO-SINGLE:GRE-SPRGCK25:GRE-SPRNGCK8:GRE-SPRNGC2T:2 | External | 111.17 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00041 | 101.05 | P23:345:ALTW:MITCHLCO:1160 | External | 100.32 | 0.73
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00045 | 101.05 | P23:345:ALTW:MITCHLCO:1160 | External | 100.32 | 0.73
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00089 | 138.86 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 137.67 | 1.19
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 630139 ADAMS 8 69.0 631046 ADAMS 5 161 1 | 72 | 72 | 0.00094 | 138.86 | P12:161:DPC-ITCM:ADAMS S5- HARMONY5:MN | External | 137.67 | 1.19
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.001 | 143.52 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.67 | -0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337651 8WHT BLUFF% 500 337648 3WHT BLUFF! 115 2 | 420 | 420 | 0.00102 | 143.52 | P23:500:EES-EAI:WH_BLF:B7914 | External | 143.67 | -0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 646254 S1254 5 161 646281 S1281 5 161 1 | 298 | 298 | 0.82966 | 121.85 | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | Internal
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 100.68 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00084 | 100.68 | P12:230:EES:FRISCO_E:TEZCUC:1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 100.79 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.76 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 251 | 251 | 9e-05 | 100.79 | 67836: 303132 4JUDICE! 138 335383 4MEAUXSPLT! 138 1 335381 6MEAUX! 230 500776 SELLRD6 230 1 | External | 100.76 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01545 | 102.7 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 345409 5OVERTON 161 345411 5OVERTON 2 161 Z | 335 | 335 | 0.01498 | 102.7 | P21:345:AMMO::MCCREDIE:MONTGOMERY | External
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00473 | 106.76 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 631046 ADAMS 5 161 681527 BVR CRK5 161 1 | 223 | 223 | 0.00497 | 106.76 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1 | External | 105.16 | 1.6
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00082 | 100.68 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 2 | 641 | 641 | 0.00084 | 100.68 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1 | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00153 | 101.76 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.61 | 0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | 253 | 253 | 0.00156 | 101.76 | P23:500:EES-EAI:WH_BLF:B7914 | External | 101.61 | 0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00082 | 100.68 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336066 6FRISCO! 230 336069 6TEZCUCO% 230 1 | 641 | 641 | 0.00084 | 100.68 | P12:HV:EES::6FRISCO!:6TEZCUCO%:1(1) | External | 100.58 | 0.1
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 602021 EAU CLA5 161 997643 EAU CL 3 161 9 | 330 | 334.6 | 0.00304 | 118.07 | P23:345:XEL:8E5 ECL BS | External | 117.15 | 0.92
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 602021 EAU CLA5 161 997643 EAU CL 3 161 9 | 330 | 334.6 | 0.00322 | 118.07 | P23:345:XEL:8E5 ECL BS | External | 117.15 | 0.92
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00149 | 147.27 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 147.15 | 0.12
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336150 8WATERFO 500 336154 6WATFRD% 230 1 | 1049 | 1049 | 0.00152 | 147.27 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 147.15 | 0.12
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 111.35 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.31 | 0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | 159 | 159 | 0.0001 | 111.35 | 334600 2KOLBS_2! 69 334437 6KOLBS% 230 2: 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | External | 111.31 | 0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00019 | 118.89 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.86 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336154 6WATFRD% 230 336190 6GYPSY% 230 2 | 580 | 580 | 0.00019 | 118.89 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 118.86 | 0.03
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.00022 | 110.66 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 110.15 | 0.51
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 300517 2KINGDM 69.0 300090 5KINGDM 161 2 | 28 | 28 | 0.0002 | 110.66 | 300517 2KINGDM 69 300090 5KINGDM 161 3: 300517 2KINGDM 69.0 300090 5KINGDM 161 3 | External | 110.15 | 0.51
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00013 | 100.8 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 100.62 | 0.18
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 620325 BROWNSV4 230 620125 BROWNSV9 41.6 1 | 26 | 32.5 | 0.00014 | 100.8 | 620325 BROWNSV4 230 620327 HANKSON4 230 1: 620325 BROWNSV4 230 620327 HANKSON4 230 1 | External | 100.62 | 0.18
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00149 | 125.55 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 125.44 | 0.11
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 | 1210.7 | 1210.7 | 0.00152 | 125.55 | 67809: 336138 6FAIRVW! 230 500510 MADISON6 230 1 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 336189 6IRONMAN% 230 336190 6GYPSY% 230 1 336054 3BLPNT! 115 336055 3LAPLAC 115 1 336190 6GYPSY% 230 336193 6UCITY! 230 1 336068 6BLPNT! 230 336190 6GYPSY% 230 1 336138 6FAIRVW! 230 336190 6GYPSY% 230 1 336190 6GYPSY% 230 336195 6PONTCH! 230 1 336190 6GYPSY% 230 336210 6WESCO% 230 1 336055 3LAPLAC 115 336220 3GYPSY% 115 1 | External | 125.44 | 0.11
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 121.34 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.34 | 338351 2JB HERGETT! 69 3WXFMR HGT X1 1: 338351 2JB HERGETT! 69.0 998892 HGT X1 69.0 1 338350 5JB HERGETT! 161 998892 HGT X1 69.0 1 338373 1HGT X1 13.8 998892 HGT X1 69.0 1 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00032 | 111.61 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 111.17 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 615477 GRE-SPRGCK15 161 997540 161/69 69.0 1 | 70 | 70 | 0.00034 | 111.61 | 615478 GRE-SPRGCK25 161 3WXFMR 161/69 2: 615478 GRE-SPRGCK25 161 997544 161/69 69.0 2 615479 GRE-SPRNGCK8 69.0 997544 161/69 69.0 2 615481 GRE-SPRNGC2T 13.8 997544 161/69 69.0 2 | External | 111.17 | 0.44
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 3e-05 | 121.34 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998879 HGT X2 69.0 1 | 100 | 112 | 4e-05 | 121.34 | P13:161-69:EES-EAI:HERGET:AT2 | External | 121.38 | -0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 121.69 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.69 | 338351 2JB HERGETT! 69 3WXFMR HGT X2 1: 338351 2JB HERGETT! 69.0 998891 HGT X2 69.0 1 338350 5JB HERGETT! 161 998891 HGT X2 69.0 1 338374 1HGT X2 13.8 998891 HGT X2 69.0 1 | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 3e-05 | 121.69 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 338350 5JB HERGETT! 161 998880 HGT X1 69.0 1 | 100 | 112 | 4e-05 | 121.69 | P12:LV-HV:EES::5JB HERGETT!:2JB HERGETT!:1(1) | External | 121.74 | -0.05
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 111.01 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 110.97 | 0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 334600 2KOLBS_2! 69.0 334437 6KOLBS% 230 2 | 159 | 159 | 0.0001 | 111.01 | 334599 2KOLBS_1! 69 334437 6KOLBS% 230 1: 334599 2KOLBS_1! 69.0 334437 6KOLBS% 230 1 | External | 110.97 | 0.04
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00078 | 103.24 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.09 | 0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 336068 6BLPNT! 230 336190 6GYPSY% 230 1 | 441 | 441 | 0.00079 | 103.24 | 67793: 336069 6TEZCUCO% 230 336154 6WATFRD% 230 1 335618 8WILLOW_GL% 500 336150 8WATERFO 500 1 336220 3GYPSY% 115 336223 3LULING! 115 1 | External | 103.09 | 0.15
Thermal | 00LVER | S1 | 19WP0 | GEN_025_028 | FROM -> TO | 661035 GLENHAM7 115 997052 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 110.31 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 110.29 | 0.02
Thermal | 00LVER | S1 | 19WP0 | GEN_043_044_045 | FROM -> TO | 661035 GLENHAM7 115 997052 GLENHAM TR1 115 1 | 25 | 31 | 0.00022 | 110.31 | 661038 GLENHAM4 230 3WXFMR GLENHAM TR2 2: 661038 GLENHAM4 230 997056 GLENHAM TR2 115 2 661035 GLENHAM7 115 997056 GLENHAM TR2 115 2 661600 GLENHAM9 41.6 997056 GLENHAM TR2 115 2 | External | 110.29 | 0.02
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03259 | NConv | P23:345:XEL:8S27 WLM AS | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03428 | NConv | P23:345:XEL:8S27 WLM AS | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03259 | NConv | P12:345:XEL:SPS WLM-SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03428 | NConv | P12:345:XEL:SPS WLM-SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03286 | NConv | P12:345:XEL:SPS HNA-SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03456 | NConv | P12:345:XEL:SPS HNA-SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03537 | NConv | P23:345:XEL:8S22 WLM | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03725 | NConv | P23:345:XEL:8S22 WLM | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03286 | NConv | P23:345:XEL:SPS 8S81 SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03456 | NConv | P23:345:XEL:SPS 8S81 SSL | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03537 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03725 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03259 | NConv | P23:345:XEL:8S25 WLM AS | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03428 | NConv | P23:345:XEL:8S25 WLM AS | NA | non-Converged in the BC | N/A
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03537 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03725 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03537 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00LVER | S1 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03725 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104105: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104105: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03253 | NConv | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03223 | NConv | 105017: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104096: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104096: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 82900: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 82900: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:GDMEC 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:GDMEC 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P22:345:OPPD:S3456-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P22:345:OPPD:S3456-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78002: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78002: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | P42:345:NPPD:BKR-PLN-3310 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | P42:345:NPPD:BKR-PLN-3310 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03561 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03793 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P12:345:OPPD:S3456-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P12:345:OPPD:S3456-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 84390: 541225 PHILL 5 161 541243 LKWINGB5 161 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 84390: 541225 PHILL 5 161 541243 LKWINGB5 161 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P12:345:AMMO::MAYWOOD:SPENCERCREEK:90 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P12:345:AMMO::MAYWOOD:SPENCERCREEK:90 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03421 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 7803: 532771 RENO 7 345 532796 WICHITA7 345 1 533015 BENTLEY4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92240: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92240: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 7802: 532771 RENO 7 345 532796 WICHITA7 345 1 533040 EVANS N4 138 533065 SG12COL4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P23:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P23:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03996 | NConv | P23:345:OPPD:S3456-S3455&CB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03421 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P22:345:OPPD:S3458-S3456 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P22:345:OPPD:S3458-S3456 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03996 | NConv | P42:345:MEC-OPPD:S3456-S3455&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 848401: 541256 IND PRK5 161 541401 EASTOWN5 161 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 848401: 541256 IND PRK5 161 541401 EASTOWN5 161 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03421 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92256: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92256: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P43:115-345:LES:T852::WAGENER.T852.CB3001 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P43:115-345:LES:T852::WAGENER.T852.CB3001 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P42:345:OPPD-LES:S3454-S3455&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P42:345:OPPD-LES:S3454-S3455&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 940701: 533394 CORONAD3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P42:345:MEC-OPPD:S3456-S3458&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P42:345:MEC-OPPD:S3456-S3458&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | P21:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | P21:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03449 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03527 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | P12:345:OKGE:BKRBKR357_2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | P12:345:OKGE:BKRBKR357_2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05071 | NConv | P12:345:WERE:87TH-STRA_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05017 | NConv | P12:345:WERE:87TH-STRA_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05832 | NConv | 94300: 650214 NW68HOLDRG7 115 997235 T141 115 1 650114 NW68HOLDRG3 345 997235 T141 115 1 650314 NW68HOL1 9 13.8 997235 T141 115 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640125 COLMB.E3 345 650114 NW68HOLDRG3 345 1 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05271 | NConv | 94300: 650214 NW68HOLDRG7 115 997235 T141 115 1 650114 NW68HOLDRG3 345 997235 T141 115 1 650314 NW68HOL1 9 13.8 997235 T141 115 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640125 COLMB.E3 345 650114 NW68HOLDRG3 345 1 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 846851: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 846851: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104700: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 104700: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05071 | NConv | P23:345:WERE:STRA_345-100:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05017 | NConv | P23:345:WERE:STRA_345-100:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.51326 | NConv | P1-2 POI - S1363: 646362 S1362 5 161 646363 S1363 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P12:345:AEPW:DELWARE7:N.E.S.-7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P12:345:AEPW:DELWARE7:N.E.S.-7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06105 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0633 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | 8613: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 94092: 532771 RENO 7 345 532796 WICHITA7 345 1 533732 BURRTON2 69.0 533736 HALSTED2 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0938 | NConv | P12:161:OPPD:S1214-S1287 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | 84129: 509807 ONETA--7 345 510406 N.E.S.-7 345 1 509852 T.NO.--7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 510406 N.E.S.-7 345 1 511840 NES3-1 22.0 510406 N.E.S.-7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | 84129: 509807 ONETA--7 345 510406 N.E.S.-7 345 1 509852 T.NO.--7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 510406 N.E.S.-7 345 1 511840 NES3-1 22.0 510406 N.E.S.-7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04834 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04894 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1387 | NConv | P23:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12549 | NConv | P23:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11855 | NConv | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1106 | NConv | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P42:345:OPPD:S3454-S3451&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P42:345:OPPD:S3454-S3451&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P23:345:OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P23:345:OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P12:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P12:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04707 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04625 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 105016: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | 69832: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635641 NORWLK5 161 635653 GRENFLD5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84445: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84445: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 8584: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 533413 CIRCLE 3 115 533416 RENO 3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 7793: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84459: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84459: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0375 | NConv | 47130011: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03711 | NConv | 47130011: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 539801 THISTLE7 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | P23:345:MEC:NORWALK 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | P23:345:MEC:NORWALK 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | P12:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | P12:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:230:OTP:AUTO-SINGLE:WILTON4:WINGER4:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:230:OTP:AUTO-SINGLE:WILTON4:WINGER4:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84457: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84457: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | P23:345:XEL:8S27 WLM AS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | P23:345:XEL:8S27 WLM AS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1: 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | P23:345:MEC:SYCAMORE 906 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | P23:345:MEC:SYCAMORE 906 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P23:345:OPPD:S3456-S3458&CB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P23:345:OPPD:S3456-S3458&CB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 20631: 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 20631: 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P23:345:XEL:8S22 WLM | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P23:345:XEL:8S22 WLM | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104540: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104540: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 42932: 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104116: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104116: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0938 | NConv | P12:161:OPPD:S1281-S1287 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104128: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104128: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05832 | NConv | P43:115-345:LES:T141::NW68&HOLDREGE.T141.CB3003 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05271 | NConv | P43:115-345:LES:T141::NW68&HOLDREGE.T141.CB3003 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04834 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04894 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104245: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104245: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06105 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0633 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | P21:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | P21:345:MEC:AUTO-SINGLE:NORWLK3:SEPOLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78291: 533416 RENO 3 115 533438 WMCPHER3 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | 82339: 645454 S3454 3 345 650185 WAGENER 3 345 1 645451 S3451 3 345 997274 S3451 T4 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 648351 S3451T49 13.8 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 648251 S3451T39 13.8 997275 S3451 T3 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | 82339: 645454 S3454 3 345 650185 WAGENER 3 345 1 645451 S3451 3 345 997274 S3451 T4 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 648351 S3451T49 13.8 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 648251 S3451T39 13.8 997275 S3451 T3 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 1045321: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 1045321: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0731 | NConv | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07318 | NConv | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P22:345:MEC:SUB 92 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P22:345:MEC:SUB 92 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | P12:345:WERE:87TH-CRAIG_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | P12:345:WERE:87TH-CRAIG_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03366 | NConv | 635568 S HILLS 3 345 635630 BOONVIL3 345 1: 635568 S HILLS 3 345 635630 BOONVIL3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0311 | NConv | 635568 S HILLS 3 345 635630 BOONVIL3 345 1: 635568 S HILLS 3 345 635630 BOONVIL3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | P12:345:WERE:N345-LACY_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | P12:345:WERE:N345-LACY_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998316 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998316 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 85453: 640215 HASTING7 115 640313 PAULINE7 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 85453: 640215 HASTING7 115 640313 PAULINE7 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P12:345:WERE:STRA-IATAN_345_1:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | P12:345:WERE:STRA-IATAN_345_1:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P22:345:OPPD:S3451-S3454 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P42:161-345:GMO:PLEASANTHILL_R8-9::PHILLT11&PHILL-SIBLEY&PHILL-PECULIAR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P42:161-345:GMO:PLEASANTHILL_R8-9::PHILLT11&PHILL-SIBLEY&PHILL-PECULIAR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | P23:345:MEC:WEBSTER 905 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | P23:345:MEC:WEBSTER 905 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | 635640 NORWLK3 345 635650 SE POLK 3 345 1: 635640 NORWLK3 345 635650 SE POLK 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | 635640 NORWLK3 345 635650 SE POLK 3 345 1: 635640 NORWLK3 345 635650 SE POLK 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03649 | NConv | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03754 | NConv | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92284: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:8S72 HNA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:8S72 HNA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | 82355: 647916 S916 8 69.0 647917 S917 8 69.0 1 647917 S917 8 69.0 647918 S918 8 69.0 1 647917 S917 8 69.0 997259 S1217 T1 69.0 1 646210 S1210 5 161 646217 S1217 5 161 1 646216 S1216 5 161 646217 S1217 5 161 1 646217 S1217 5 161 646227 S1227 5 161 1 646217 S1217 5 161 997259 S1217 T1 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0721 | NConv | 82355: 647916 S916 8 69.0 647917 S917 8 69.0 1 647917 S917 8 69.0 647918 S918 8 69.0 1 647917 S917 8 69.0 997259 S1217 T1 69.0 1 646210 S1210 5 161 646217 S1217 5 161 1 646216 S1216 5 161 646217 S1217 5 161 1 646217 S1217 5 161 646227 S1227 5 161 1 646217 S1217 5 161 997259 S1217 T1 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0731 | NConv | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07318 | NConv | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | 69835: 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 636001 WEBSTER5 161 636020 SUB T FD 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | 69835: 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 636001 WEBSTER5 161 636020 SUB T FD 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03999 | NConv | P42:345:OKGE:SB_REOW7382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03956 | NConv | P42:345:OKGE:SB_REOW7382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04163 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04289 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | P42:345:OKGE:SB_REOW7389 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | P42:345:OKGE:SB_REOW7389 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | 635635 MADISON3 345 635640 NORWLK3 345 1: 635635 MADISON3 345 635640 NORWLK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | 635635 MADISON3 345 635640 NORWLK3 345 1: 635635 MADISON3 345 635640 NORWLK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 828720: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 828720: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 84328: 541218 GRNWD 5 161 541313 HARRIS 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541225 PHILL 5 161 541313 HARRIS 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 84328: 541218 GRNWD 5 161 541313 HARRIS 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541225 PHILL 5 161 541313 HARRIS 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | 106389: 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | 106389: 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | P23:345:MEC:SYCAMORE 905 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | P23:345:MEC:SYCAMORE 905 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | 82320: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.29304 | NConv | 82320: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P23:161-345:KCPL:CRAIG_R8-11::CRAIG-WGARD-CRAIGT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P23:161-345:KCPL:CRAIG_R8-11::CRAIG-WGARD-CRAIGT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P42:345:NPPD:BKR-SW-3306 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P42:345:NPPD:BKR-SW-3306 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104487: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541254 EAST 5 161 541401 EASTOWN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104487: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541254 EAST 5 161 541401 EASTOWN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | 635017 ATCHSN 3 345 640139 COOPER 3 345 1: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | 84810: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 7830: 532771 RENO 7 345 532796 WICHITA7 345 1 533416 RENO 3 115 533429 MOUNDRG3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P24:345:ITCM:LAKEFLD 885 FUT:MN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P24:345:ITCM:LAKEFLD 885 FUT:MN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P23:345:AMMO::SPENCERCREEK:V3 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P23:345:AMMO::SPENCERCREEK:V3 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104157: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104157: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | 104489: 532772 STRANGR7 345 542982 IATAN 7 345 2 541350 IATAN5 161 541351 WESTON 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84486: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84486: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P12:345:OPPD:S3451-S3454 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P23:345:OPPD:S3451-S3454&FCS:LT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04163 | NConv | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04289 | NConv | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | 84370: 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | 84370: 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04042 | NConv | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04031 | NConv | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84828: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542978 CRAIG 5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84828: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542978 CRAIG 5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03561 | NConv | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03793 | NConv | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1: 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | P12:345:WERE:RENO-WICH_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | P12:345:WERE:RENO-WICH_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104214: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104214: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | P12:345:WERE:STRA-IATAN_345_2::FUTURE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | P12:345:WERE:STRA-IATAN_345_2::FUTURE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | P23:345:WERE:STRA_345-96:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | P23:345:WERE:STRA_345-96:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84372: 541261 STALEY 2 69.0 541262 LIBERTY2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84372: 541261 STALEY 2 69.0 541262 LIBERTY2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78000: 532771 RENO 7 345 587884 G16-111-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78000: 532771 RENO 7 345 587884 G16-111-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | P13:161:MEC:NORWALK 9T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | P13:161:MEC:NORWALK 9T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | 104276: 515543 RENFROW7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532798 VIOLA 7 345 588364 G16-153-TAP 345 1 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 532798 VIOLA 7 345 997877 SCJ TX-1 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08476 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08253 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08476 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08253 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04707 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04625 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104080: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104080: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | 345230 7MONTGMRY 345 345992 7SPENCER 345 1: 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | 345230 7MONTGMRY 345 345992 7SPENCER 345 1: 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03449 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03527 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 1045301: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 1045301: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | P42:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P42:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92266: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92266: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92264: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92264: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | 104752: 645454 S3454 3 345 650185 WAGENER 3 345 1 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 650285 WAGENER 7 115 997191 T851 115 1 650185 WAGENER 3 345 997191 T851 115 1 650385 WAGENER1 9 13.8 997191 T851 115 1 650285 WAGENER 7 115 997190 T852 115 2 650185 WAGENER 3 345 997190 T852 115 2 650485 WAGENER2 9 13.8 997190 T852 115 2 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | 104752: 645454 S3454 3 345 650185 WAGENER 3 345 1 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 650285 WAGENER 7 115 997191 T851 115 1 650185 WAGENER 3 345 997191 T851 115 1 650385 WAGENER1 9 13.8 997191 T851 115 1 650285 WAGENER 7 115 997190 T852 115 2 650185 WAGENER 3 345 997190 T852 115 2 650485 WAGENER2 9 13.8 997190 T852 115 2 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05191 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05072 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92252: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92252: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P55:161-345:KCPL:W.GARDNER_BUS_11:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P55:161-345:KCPL:W.GARDNER_BUS_11:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84497: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84497: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P42:161-345:GMO:PECULIAR_R2-9::PECULIART11&PECULIAR-STILWELL&PECULIAR-PHILL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | P42:161-345:GMO:PECULIAR_R2-9::PECULIART11&PECULIAR-STILWELL&PECULIAR-PHILL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P23:161-345:GMO:PHILL_R8-11::PHILL-SIBLEY-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P23:161-345:GMO:PHILL_R8-11::PHILL-SIBLEY-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05219 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05126 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P23:345:AMMO::MAYWOOD:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P23:345:AMMO::MAYWOOD:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P21:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P21:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0311 | NConv | P23:345:AMMO::LOOSECREEK:V3 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03153 | NConv | P23:345:AMMO::LOOSECREEK:V3 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03357 | NConv | 104307: 532913 KELLY 5 161 646399 S1399 5 161 1 532913 KELLY 5 161 532920 TECHILL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03346 | NConv | 104307: 532913 KELLY 5 161 646399 S1399 5 161 1 532913 KELLY 5 161 532920 TECHILL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P42:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P42:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P23:345:WERE:STRA_345-99:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | P23:345:WERE:STRA_345-99:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P45:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P45:345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03296 | NConv | 635570 ORIENT 3 345 635635 MADISON3 345 1: 635570 ORIENT 3 345 635635 MADISON3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03092 | NConv | 635570 ORIENT 3 345 635635 MADISON3 345 1: 635570 ORIENT 3 345 635635 MADISON3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P12:345:XEL:SPS HNA-SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P12:345:XEL:SPS HNA-SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P12:345:OPPD-LES:S3454-WAGENER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P12:345:OPPD-LES:S3454-WAGENER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | P12:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | P12:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1387 | NConv | P12:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12549 | NConv | P12:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03449 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03527 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 852692: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 852692: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 104977: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P23:161-345:GMO:PHILL_R8-9::PHILL-SIBLEY-PECULIAR-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P23:161-345:GMO:PHILL_R8-9::PHILL-SIBLEY-PECULIAR-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03652 | NConv | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03595 | NConv | 105455: 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | P42:345:NPPD:BKR-CPR-3316 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | P42:345:NPPD:BKR-CPR-3316 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P23:345:WERE:STRA_345-98:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | P23:345:WERE:STRA_345-98:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104225: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104225: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 104978: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 104978: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | P42:345:NPPD:BKR-AXT-3306 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | P42:345:NPPD:BKR-AXT-3306 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03253 | NConv | 104976: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03223 | NConv | 104976: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515853 DGRASSE4 138 998203 DGRASSE 138 1 515852 DGRASSE7 345 998203 DGRASSE 138 1 515854 DGRASSE1 13.8 998203 DGRASSE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:MEC:HILLS 914 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:MEC:HILLS 914 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P23:345:MEC:HILLS 934 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P23:345:MEC:HILLS 934 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P23:345:MEC:HILLS 9114 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P23:345:MEC:HILLS 9114 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1387 | NConv | P22:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12549 | NConv | P22:345:OPPD:S3458-S3740 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P45:345:OPPD:S3456-S3458&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P45:345:OPPD:S3456-S3458&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | 104616: 532772 STRANGR7 345 542982 IATAN 7 345 2 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | 104616: 532772 STRANGR7 345 542982 IATAN 7 345 2 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 84389: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 84389: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | P23:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | P23:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104705: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104705: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P23:161-345:GMO:PECULIAR_R8-11::PECULIAR-PHILL-PECULT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | P23:161-345:GMO:PECULIAR_R8-11::PECULIAR-PHILL-PECULT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04264 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04196 | NConv | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | 94301: 645454 S3454 3 345 650185 WAGENER 3 345 1 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 650285 WAGENER 7 115 997191 T851 115 1 650185 WAGENER 3 345 997191 T851 115 1 650385 WAGENER1 9 13.8 997191 T851 115 1 650285 WAGENER 7 115 997190 T852 115 2 650185 WAGENER 3 345 997190 T852 115 2 650485 WAGENER2 9 13.8 997190 T852 115 2 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | 94301: 645454 S3454 3 345 650185 WAGENER 3 345 1 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 650285 WAGENER 7 115 997191 T851 115 1 650185 WAGENER 3 345 997191 T851 115 1 650385 WAGENER1 9 13.8 997191 T851 115 1 650285 WAGENER 7 115 997190 T852 115 2 650185 WAGENER 3 345 997190 T852 115 2 650485 WAGENER2 9 13.8 997190 T852 115 2 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 82901: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 82901: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P43:22-345:OPPD:S3451-54&FCS 1G | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69822: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635039 AVOCA 5 161 635041 TEAKWOOD 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69822: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635039 AVOCA 5 161 635041 TEAKWOOD 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | 82313: 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | 82313: 645458 S3458 3 345 650189 103&ROKEBY3 345 1 645458 S3458 3 345 645740 S3740 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05219 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05126 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:GDMEC 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:GDMEC 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104706: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104706: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | P43:161-345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P43:161-345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09297 | NConv | 635100 RLHILLS3 345 635570 ORIENT 3 345 1: 635100 RLHILLS3 345 635570 ORIENT 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09776 | NConv | 635100 RLHILLS3 345 635570 ORIENT 3 345 1: 635100 RLHILLS3 345 635570 ORIENT 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104074: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104074: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69823: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635041 TEAKWOOD 5 161 638050 ATLANTC5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69823: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635041 TEAKWOOD 5 161 638050 ATLANTC5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | P23:345:WERE:STRA_345-97:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | P23:345:WERE:STRA_345-97:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | P42:345:OKGE:SB_RARD7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | P42:345:OKGE:SB_RARD7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0563 | NConv | 82353: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 646221 S1221 5 161 646255 S1255 5 161 1 646233 S1233 5 161 646255 S1255 5 161 1 646255 S1255 5 161 646259 S1259 5 161 1 646255 S1255 5 161 646260 S1260 5 161 1 646255 S1255 5 161 997272 S3455 T1 161 1 646255 S1255 5 161 997271 S3455 T3 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03996 | NConv | 82353: 645454 S3454 3 345 645455 S3455 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645455 S3455 3 345 645740 S3740 3 345 1 645455 S3455 3 345 997272 S3455 T1 161 1 645455 S3455 3 345 997271 S3455 T3 161 1 646221 S1221 5 161 646255 S1255 5 161 1 646233 S1233 5 161 646255 S1255 5 161 1 646255 S1255 5 161 646259 S1259 5 161 1 646255 S1255 5 161 646260 S1260 5 161 1 646255 S1255 5 161 997272 S3455 T1 161 1 646255 S1255 5 161 997271 S3455 T3 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104525: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104525: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P42:345:OPPD:S3451-S3454&FCS 1G | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03449 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03527 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84461: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84461: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | P23:345:MEC:OVERLAND TRAIL 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | P23:345:MEC:OVERLAND TRAIL 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05219 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05126 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69821: 635012 QUICK 5 161 635039 AVOCA 5 161 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69821: 635012 QUICK 5 161 635039 AVOCA 5 161 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:SPS 8S72 HNA | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:SPS 8S72 HNA | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104539: 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104539: 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104179: 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 542965 W.GRDNR7 345 542968 STILWEL7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 588300 GEN-2016-157 345 1 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104147: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104147: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104127: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104127: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P23:345:OPPD:S3454-S3451&WAGNER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P23:345:OPPD:S3454-S3451&WAGNER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104125: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104125: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06006 | NConv | 84302: 532772 STRANGR7 345 542982 IATAN 7 345 2 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05996 | NConv | 84302: 532772 STRANGR7 345 542982 IATAN 7 345 2 533244 JARBALO3 115 533268 STRANGR3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 7805: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533013 MOUND 4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 828730: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 828730: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P23:161-345:KCPL:CRAIG_R8-33::CRAIG-WGARD-CRAIGT33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P23:161-345:KCPL:CRAIG_R8-33::CRAIG-WGARD-CRAIGT33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P22:345:OPPD:S3454-WAGENER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P22:345:OPPD:S3454-WAGENER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 20630: 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 20630: 640065 AXTELL 3 345 640312 PAULINE3 345 1 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P23:345:AEPW:DELAWARE CB 3405A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P23:345:AEPW:DELAWARE CB 3405A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P23:345:XEL:8S23 WLM | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P23:345:XEL:8S23 WLM | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104224: 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104224: 542965 W.GRDNR7 345 997756 WEST GARDN11 161 11 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04421 | NConv | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04787 | NConv | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04421 | NConv | P23:345:MEC:OBRIEN 903 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04787 | NConv | P23:345:MEC:OBRIEN 903 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | 4013: 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | 4013: 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104129: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104129: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | 635017 ATCHSN 3 345 635018 WESTBORO 3 345 1: 635017 ATCHSN 3 345 635018 WESTBORO 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | P23:345:MEC:GRIMES 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | P23:345:MEC:GRIMES 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | P45:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P45:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | 104244: 532775 87TH 7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | 104244: 532775 87TH 7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 940702: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1387 | NConv | P23:345:OPPD:S3740-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12549 | NConv | P23:345:OPPD:S3740-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104541: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104541: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 828710: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 828710: 532771 RENO 7 345 997950 RENO TX-1 115 1 533416 RENO 3 115 997950 RENO TX-1 115 1 532807 RENO 1X1 14.4 997950 RENO TX-1 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04834 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04894 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104254: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542978 CRAIG 5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104254: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542978 CRAIG 5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | P23:345:XEL:8S25 WLM AS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | P23:345:XEL:8S25 WLM AS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 42930: 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03652 | NConv | P42:345:SPS:FINNEY_OR70_19L | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03595 | NConv | P42:345:SPS:FINNEY_OR70_19L | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P23:345:MEC:WALCOTT 944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P23:345:MEC:WALCOTT 944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | P12:345:WERE:N345-PSO_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | P12:345:WERE:N345-PSO_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05191 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05072 | NConv | 40752: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 530601 HEIZER 3 115 539678 GRTBEND3 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04042 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04031 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | P42:345:OKGE:SB_SOER7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | P42:345:OKGE:SB_SOER7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P23:345:MEC:LOUISA 954 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P23:345:MEC:LOUISA 954 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03768 | NConv | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03876 | NConv | P12:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0375 | NConv | P12:345:WERE:VIOL-WICH_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03711 | NConv | P12:345:WERE:VIOL-WICH_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03059 | NConv | P23:345:AMMO::BLAND:V21 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104092: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104092: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0375 | NConv | 47130010: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03711 | NConv | 47130010: 532796 WICHITA7 345 532798 VIOLA 7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P23:345:OPPD:S3458-S3456 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P23:345:OPPD:S3458-S3456 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 104532: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 104532: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | 82318: 645451 S3451 3 345 645454 S3454 3 345 1 645454 S3454 3 345 645455 S3455 3 345 1 645454 S3454 3 345 650185 WAGENER 3 345 1 645454 S3454 3 345 997273 S1254 T1 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | 82318: 645451 S3451 3 345 645454 S3454 3 345 1 645454 S3454 3 345 645455 S3455 3 345 1 645454 S3454 3 345 650185 WAGENER 3 345 1 645454 S3454 3 345 997273 S1254 T1 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | P42:345:OKGE:SB_REOW7319 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | P42:345:OKGE:SB_REOW7319 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | P43:161-345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.16685 | NConv | P43:161-345:OPPD:S3456-S3458&T4 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P23:345:XEL:SPS 8S81 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P23:345:XEL:SPS 8S81 SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P23:161-345:GMO:PHILL_R9-11::PHILL-PECULIAR-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | P23:161-345:GMO:PHILL_R9-11::PHILL-PECULIAR-PHILLT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04163 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04289 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05071 | NConv | P23:345:WERE:87TH_345_BKRS:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05017 | NConv | P23:345:WERE:87TH_345_BKRS:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P23:345:AEPW:NES CB 3441A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P23:345:AEPW:NES CB 3441A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03253 | NConv | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03223 | NConv | 104980: 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | P23:345:WERE:N345_345-80:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | P23:345:WERE:N345_345-80:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | P23:345:MEC:SE POLK 901 OR 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | P23:345:MEC:SE POLK 901 OR 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | P23:345:WERE:RENO_345-150:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | P23:345:WERE:RENO_345-150:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 104457: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | 104216: 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | 104216: 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03649 | NConv | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03754 | NConv | P21:345:MEC:AUTO-SINGLE:GRIMES3:SYCAMOR3:2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | P23:161-345:GMO:STJOE_R14-33::STJOE-EASTOWNE-STJOET1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | P23:161-345:GMO:STJOE_R14-33::STJOE-EASTOWNE-STJOET1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | 105000: 515576 RANCHRD7 345 515621 OPENSKY7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | 105000: 515576 RANCHRD7 345 515621 OPENSKY7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | 104217: 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84371: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84371: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | 82354: 646249 S1249 5 161 646254 S1254 5 161 1 646254 S1254 5 161 646281 S1281 5 161 1 646254 S1254 5 161 997273 S1254 T1 161 1 645451 S3451 3 345 645454 S3454 3 345 1 645454 S3454 3 345 645455 S3455 3 345 1 645454 S3454 3 345 650185 WAGENER 3 345 1 645454 S3454 3 345 997273 S1254 T1 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | 82354: 646249 S1249 5 161 646254 S1254 5 161 1 646254 S1254 5 161 646281 S1281 5 161 1 646254 S1254 5 161 997273 S1254 T1 161 1 645451 S3451 3 345 645454 S3454 3 345 1 645454 S3454 3 345 645455 S3455 3 345 1 645454 S3454 3 345 650185 WAGENER 3 345 1 645454 S3454 3 345 997273 S1254 T1 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 84827: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 84827: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84829: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84829: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104152: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104152: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05219 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05126 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84491: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84491: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P12:345:AMMO::MONTGOMERY:SPENCERCREEK:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P12:345:AMMO::MONTGOMERY:SPENCERCREEK:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | P13:161:MEC:SE POLK 9T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | P13:161:MEC:SE POLK 9T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1: 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1: 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 7804: 532771 RENO 7 345 532796 WICHITA7 345 1 533011 HALSTD 4 138 533015 BENTLEY4 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05219 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05126 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04402 | NConv | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04539 | NConv | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.29304 | NConv | 82350: 647909 S909 8 69.0 647918 S918 8 69.0 1 647909 S909 8 69.0 647921 S921 8 69.0 1 647909 S909 8 69.0 647937 S937 8 69.0 1 647909 S909 8 69.0 647939 S939 8 69.0 1 647909 S909 8 69.0 997263 S1209 T1 69.0 1 646209 S1209 5 161 646231 S1231 5 161 1 646209 S1209 5 161 646231 S1231 5 161 2 646209 S1209 5 161 646250 S1250 5 161 1 646209 S1209 5 161 646250 S1250 5 161 2 646209 S1209 5 161 646252 S1252 5 161 1 646209 S1209 5 161 997269 S3459 T3 161 1 646209 S1209 5 161 997268 S3459 T6 161 1 646209 S1209 5 161 997263 S1209 T1 69.0 1 645451 S3451 3 345 645459 S3459 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645459 S3459 3 345 997269 S3459 T3 161 1 645459 S3459 3 345 997268 S3459 T6 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P23:161-345:KCPL:WGARDNER_R8-11::WGARD-CRAIG-WGARDT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P23:161-345:KCPL:WGARDNER_R8-11::WGARD-CRAIG-WGARDT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03996 | NConv | P45:345:OPPD:S3456-S3455&CBL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | P21:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | P21:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | 83248: 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104513: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 541198 PECULR 7 345 542968 STILWEL7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104513: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 541198 PECULR 7 345 542968 STILWEL7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03575 | NConv | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104111: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104111: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | P12:161:OPPD:S1281-S1260:LS | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P55:161-345:KCPL:CRAIG_BUS_33_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P55:161-345:KCPL:CRAIG_BUS_33_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0731 | NConv | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07318 | NConv | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | P23:345:WERE:N345_345-20:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | P23:345:WERE:N345_345-20:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03082 | NConv | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0307 | NConv | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | P23:161-345:GMO:SIBLEY_R3-8::SIBLEY-KETCHEM-SIBLEYT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | P23:161-345:GMO:SIBLEY_R3-8::SIBLEY-KETCHEM-SIBLEYT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | P23:345:MEC:OVERLAND TRAIL 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | P23:345:MEC:OVERLAND TRAIL 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05832 | NConv | 104751: 650214 NW68HOLDRG7 115 997235 T141 115 1 650114 NW68HOLDRG3 345 997235 T141 115 1 650314 NW68HOL1 9 13.8 997235 T141 115 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640125 COLMB.E3 345 650114 NW68HOLDRG3 345 1 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05271 | NConv | 104751: 650214 NW68HOLDRG7 115 997235 T141 115 1 650114 NW68HOLDRG3 345 997235 T141 115 1 650314 NW68HOL1 9 13.8 997235 T141 115 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640125 COLMB.E3 345 650114 NW68HOLDRG3 345 1 650114 NW68HOLDRG3 345 650185 WAGENER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | P23:161-345:GMO:PECULIAR_R2-9::PECULIAR-PHILL-STILWELL-PECULT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | P23:161-345:GMO:PECULIAR_R2-9::PECULIAR-PHILL-STILWELL-PECULT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | P12:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | P12:345:MEC:AUTO-SINGLE:MADISON3:NORWLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04264 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04196 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92272: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92272: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12918 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12662 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92270: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92270: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03377 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03547 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | 345435 7MAYWOOD 345 345992 7SPENCER 345 1: 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | 345435 7MAYWOOD 345 345992 7SPENCER 345 1: 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P45:345:OPPD:S3454-S3455&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P45:345:OPPD:S3454-S3455&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 94080: 515852 DGRASSE7 345 539801 THISTLE7 345 2 515852 DGRASSE7 345 539801 THISTLE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03421 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07474 | NConv | 104845: 560062 G15088_T 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.071 | NConv | 104845: 560062 G15088_T 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04276 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04201 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04707 | NConv | P23:345:SUNC:SB_BRK488 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04625 | NConv | P23:345:SUNC:SB_BRK488 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | 84128: 510380 DELWARE7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 998411 DELAWARE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | 84128: 510380 DELWARE7 345 510406 N.E.S.-7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 998411 DELAWARE 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04264 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04196 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03357 | NConv | P12:161:WERE-OPPD:S1399-KELLY | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03346 | NConv | P12:161:WERE-OPPD:S1399-KELLY | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 84581: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06392 | NConv | 84581: 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84460: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84460: 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543054 CEDARNL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P42:345:AEPW:NES CB 3445A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P42:345:AEPW:NES CB 3445A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04163 | NConv | P23:345:MEC:MONTEZUMA 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04289 | NConv | P23:345:MEC:MONTEZUMA 902 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P12:345:AMMO::AUDRAIN:SPS:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P12:345:AMMO::AUDRAIN:SPS:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04707 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04625 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 852691: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 852691: 640313 PAULINE7 115 997346 PAULINE T1 115 1 640312 PAULINE3 345 997346 PAULINE T1 115 1 640315 PAULINE9 13.8 997346 PAULINE T1 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05666 | NConv | P42:345:NPPD:BKR-SW-3308 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05595 | NConv | P42:345:NPPD:BKR-SW-3308 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04264 | NConv | 105454: 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997960 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04196 | NConv | 105454: 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997960 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P45:345:OPPD:S3451-S3454&FCS 1G | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04264 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04196 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84496: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84496: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P45:345:OPPD:S3454-S3451&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P45:345:OPPD:S3454-S3451&WAG | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03652 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03595 | NConv | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84336: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84336: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | P23:345:MEC:LEHIGH 0350 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | P23:345:MEC:LEHIGH 0350 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:MEC:HILLS 924 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:MEC:HILLS 924 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | P12:345:OKGE:BKRBKR357_1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | P12:345:OKGE:BKRBKR357_1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04707 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04625 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104215: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104215: 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104632: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104632: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03475 | NConv | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03404 | NConv | 69831: 635640 NORWLK3 345 635650 SE POLK 3 345 1 635651 SE POLK 5 161 635653 GRENFLD5 161 1 635651 SE POLK 5 161 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78292: 533416 RENO 3 115 533438 WMCPHER3 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:MEC:SUB TIC 944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:MEC:SUB TIC 944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 940700: 533394 CORONAD3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | P12:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | P12:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03421 | NConv | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104102: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104102: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04421 | NConv | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04787 | NConv | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104633: 541225 PHILL 5 161 541243 LKWINGB5 161 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104633: 541225 PHILL 5 161 541243 LKWINGB5 161 1 541198 PECULR 7 345 541200 PHILL 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 830510: 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 830510: 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03253 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03223 | NConv | 81743: 515375 WWRDEHV7 345 515407 TATONGA7 345 1 515375 WWRDEHV7 345 515407 TATONGA7 345 2 515375 WWRDEHV7 345 515458 BORDER 7 345 1 515375 WWRDEHV7 345 515825 GRTWSRN7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 2 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 515375 WWRDEHV7 345 998244 WWDEHV 138 1 515375 WWRDEHV7 345 998243 WWDEHV-T2 138 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P22:345:OPPD:S3454-S3451 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1387 | NConv | P22:345:OPPD:S3740-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12549 | NConv | P22:345:OPPD:S3740-S3458 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03315 | NConv | P23:345:MEC:WALCOTT 914 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0339 | NConv | P23:345:MEC:WALCOTT 914 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03649 | NConv | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03754 | NConv | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2: 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08998 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09182 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P12:345:MEC:HILLS-SUB T-LOUISA + REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P12:345:MEC:HILLS-SUB T-LOUISA + REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78290: 533416 RENO 3 115 533438 WMCPHER3 115 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | 69833: 631078 WNTRST 5 161 635641 NORWLK5 161 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635635 MADISON3 345 635640 NORWLK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | 69833: 631078 WNTRST 5 161 635641 NORWLK5 161 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635635 MADISON3 345 635640 NORWLK3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | 104209: 542977 CRAIG 7 345 997748 CRAIG22 161 22 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | 104209: 542977 CRAIG 7 345 997748 CRAIG22 161 22 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05832 | NConv | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05271 | NConv | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104071: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104071: 543020 BRMGHAM5 161 543023 CLAYCM25 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 8611: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P22:345:MEC:SUB T | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P22:345:MEC:SUB T | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04042 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04031 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03652 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03595 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03999 | NConv | P12:345:OKGE:BKRBKR400 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03956 | NConv | P12:345:OKGE:BKRBKR400 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04421 | NConv | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04787 | NConv | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | P13:69-161:OPPD:S1217 T1:LT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0721 | NConv | P13:69-161:OPPD:S1217 T1:LT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05191 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05072 | NConv | 40142: 539679 GRTBEND6 230 539695 SPEARVL6 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.29304 | NConv | 82340: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 645454 S3454 3 345 645455 S3455 3 345 1 646206 S1206 5 161 997270 S3456 T4 161 1 648256 S3456T49 13.8 997270 S3456 T4 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104538: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104538: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 542968 STILWEL7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06403 | NConv | 104536: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06406 | NConv | 104536: 541198 PECULR 7 345 541200 PHILL 7 345 1 541198 PECULR 7 345 997781 PECULIAR11 161 11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:AMMO-MEC::SUBT:T944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:AMMO-MEC::SUBT:T944 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03632 | NConv | 104979: 515852 DGRASSE7 345 539801 THISTLE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03596 | NConv | 104979: 515852 DGRASSE7 345 539801 THISTLE7 345 1 515375 WWRDEHV7 345 515852 DGRASSE7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 635014 OVRLND 3 345 635590 FALLOW 3 345 1: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 635014 OVRLND 3 345 635590 FALLOW 3 345 1: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08476 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08253 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69824: 635633 ADAIR 5 161 638050 ATLANTC5 161 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69824: 635633 ADAIR 5 161 638050 ATLANTC5 161 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | P42:345:OKGE:SB_RARD7393 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | P42:345:OKGE:SB_RARD7393 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104514: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104514: 541198 PECULR 7 345 541200 PHILL 7 345 1 541200 PHILL 7 345 997778 P HILL 11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16085 | NConv | P22:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15664 | NConv | P22:345:OPPD:S3458-COOPER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04163 | NConv | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04289 | NConv | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.39295 | NConv | P23:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P23:345:OPPD:S3454-S3451&T1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03561 | NConv | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03793 | NConv | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 84327: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541227 OAKGRV 5 161 541229 ODESSA 5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 84327: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541227 OAKGRV 5 161 541229 ODESSA 5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69820: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635012 QUICK 5 161 635015 OVRLND 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69820: 635014 OVRLND 3 345 635590 FALLOW 3 345 1 635012 QUICK 5 161 635015 OVRLND 5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104150: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104150: 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.14433 | NConv | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.29304 | NConv | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 84329: 300320 5LEVASY 161 548808 ECKLES-161 161 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104144: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104144: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08622 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08548 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 69825: 635631 BOONVIL5 161 635632 EARLHAM5 161 1 635632 EARLHAM5 161 635633 ADAIR 5 161 1 635632 EARLHAM5 161 635833 EARLHAM8 69.0 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 69825: 635631 BOONVIL5 161 635632 EARLHAM5 161 1 635632 EARLHAM5 161 635633 ADAIR 5 161 1 635632 EARLHAM5 161 635833 EARLHAM8 69.0 1 635014 OVRLND 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0379 | NConv | P23:345:MEC:MADISON CO 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03677 | NConv | P23:345:MEC:MADISON CO 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | P12:345:AEPW-WERE:DELWARE7:NEOSHO7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | P12:345:AEPW-WERE:DELWARE7:NEOSHO7 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05832 | NConv | 104804: 650214 NW68HOLDRG7 115 650216 SW27&F 7 115 1 650316 SW27&F 9 12.5 997234 T161 12.5 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 650216 SW27&F 7 115 650230 2&N 7 115 1 650216 SW27&F 7 115 997234 T161 12.5 1 650516 161TERTIARY 7.20 997234 T161 12.5 1 650230 2&N 7 115 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05271 | NConv | 104804: 650214 NW68HOLDRG7 115 650216 SW27&F 7 115 1 650316 SW27&F 9 12.5 997234 T161 12.5 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 650216 SW27&F 7 115 650230 2&N 7 115 1 650216 SW27&F 7 115 997234 T161 12.5 1 650516 161TERTIARY 7.20 997234 T161 12.5 1 650230 2&N 7 115 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | 82851: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | 82851: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03999 | NConv | P42:345:OKGE:SB_WONG7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03956 | NConv | P42:345:OKGE:SB_WONG7383 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03649 | NConv | P23:345:MEC:SYCAMORE 904 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03754 | NConv | P23:345:MEC:SYCAMORE 904 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 830520: 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 830520: 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 532873 SUMMIT 6 230 997946 SUMM TX-1 230 1 532813 SUMMIT 1 14.4 997946 SUMM TX-1 230 1 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05191 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05072 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | 84807: 541254 EAST 5 161 541401 EASTOWN5 161 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | 84807: 541254 EAST 5 161 541401 EASTOWN5 161 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.19286 | NConv | P23:345:OPPD:S3454-S3455&WAGNER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.18031 | NConv | P23:345:OPPD:S3454-S3455&WAGNER | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84353: 532775 87TH 7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997749 CRAIG11 161 11 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84353: 532775 87TH 7 345 542977 CRAIG 7 345 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542977 CRAIG 7 345 997749 CRAIG11 161 11 542977 CRAIG 7 345 997748 CRAIG22 161 22 542977 CRAIG 7 345 997747 CRAIG33 161 33 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 104255: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 104255: 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06105 | NConv | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1: 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0633 | NConv | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1: 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03357 | NConv | P12:161:OPPD:HUMBOLT-S1398-S1399 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03346 | NConv | P12:161:OPPD:HUMBOLT-S1398-S1399 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04867 | NConv | P21:345:AMMO::SPENCER:PALMYRATAP | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0506 | NConv | P21:345:AMMO::SPENCER:PALMYRATAP | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 42931: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03489 | NConv | P23:345:MEC:WEBSTER 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03526 | NConv | P23:345:MEC:WEBSTER 901 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1: 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1: 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04421 | NConv | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1: 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04787 | NConv | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1: 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03561 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03793 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:MEC:LOUISA 964 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:MEC:LOUISA 964 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04557 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0452 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03561 | NConv | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1: 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03793 | NConv | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1: 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05191 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05072 | NConv | 38762: 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | 82850: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | 82850: 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532780 CANEYRV7 345 588544 G17-009-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03846 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03973 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | P12:345:WERE:VIOL-OGE_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | P12:345:WERE:VIOL-OGE_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05071 | NConv | 104267: 532772 STRANGR7 345 532775 87TH 7 345 1 532775 87TH 7 345 542977 CRAIG 7 345 1 532775 87TH 7 345 997943 87TH TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05017 | NConv | 104267: 532772 STRANGR7 345 532775 87TH 7 345 1 532775 87TH 7 345 542977 CRAIG 7 345 1 532775 87TH 7 345 997943 87TH TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03349 | NConv | P12:345:XEL:SPS WLM-SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03518 | NConv | P12:345:XEL:SPS WLM-SSL | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 78001: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 78001: 587884 G16-111-TAP 345 587894 G16-122-TAP 345 1 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07286 | NConv | 635580 ARBR HL 3 345 635590 FALLOW 3 345 1: 635580 ARBR HL 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07501 | NConv | 635580 ARBR HL 3 345 635590 FALLOW 3 345 1: 635580 ARBR HL 3 345 635590 FALLOW 3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03629 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03817 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0718 | NConv | 85451: 640066 AXTELL 7 115 640275 MINDEN 7 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0686 | NConv | 85451: 640066 AXTELL 7 115 640275 MINDEN 7 115 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 921961: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 921961: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09699 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09508 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 104265: 532767 GEARY 7 345 532773 SUMMIT 7 345 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 532773 SUMMIT 7 345 997946 SUMM TX-1 230 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04408 | NConv | P23:345:AEPW:DELAWARE CB 3409A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04392 | NConv | P23:345:AEPW:DELAWARE CB 3409A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03131 | NConv | 82902: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03099 | NConv | 82902: 532771 RENO 7 345 997949 RENO TX-2 115 1 533416 RENO 3 115 997949 RENO TX-2 115 1 532810 RENO 2X1 14.4 997949 RENO TX-2 115 1 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04042 | NConv | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04031 | NConv | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12937 | NConv | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12878 | NConv | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.17392 | NConv | 83256: 646209 S1209 5 161 646231 S1231 5 161 1 646209 S1209 5 161 646231 S1231 5 161 2 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0435 | NConv | P23:345:AEPW:DELAWARE CB 3401A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04335 | NConv | P23:345:AEPW:DELAWARE CB 3401A NBTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | P23:345:WERE:RENO_345-160:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | P23:345:WERE:RENO_345-160:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | P55:161-345:KCPL:CRAIG_BUS_22_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | P55:161-345:KCPL:CRAIG_BUS_22_345:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0749 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07287 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03999 | NConv | P42:345:OKGE:SB_WONG7313 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03956 | NConv | P42:345:OKGE:SB_WONG7313 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P41:345:OPPD:S3451-S3454&FCS 1G | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08476 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08253 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04402 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04539 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04483 | NConv | P12:345:OKGE-WERE:BKRBKR422 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04437 | NConv | P12:345:OKGE-WERE:BKRBKR422 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92288: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92288: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0311 | NConv | P23:345:AMMO::LOOSECREEK:V9 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03153 | NConv | P23:345:AMMO::LOOSECREEK:V9 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03956 | NConv | P23:345:WERE:WICH_345-50:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03897 | NConv | P23:345:WERE:WICH_345-50:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06586 | NConv | P23:345:OPPD:S3451-S3454 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05064 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05005 | NConv | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0375 | NConv | P23:345:WERE:WICH_345-116:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03711 | NConv | P23:345:WERE:WICH_345-116:: | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 92261: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 92261: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05904 | NConv | 84340: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05874 | NConv | 84340: 542965 W.GRDNR7 345 542977 CRAIG 7 345 1 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11733 | NConv | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11648 | NConv | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04855 | NConv | 104208: 542977 CRAIG 7 345 997749 CRAIG11 161 11 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04796 | NConv | 104208: 542977 CRAIG 7 345 997749 CRAIG11 161 11 532775 87TH 7 345 542977 CRAIG 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04051 | NConv | 104107: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03976 | NConv | 104107: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06669 | NConv | 104518: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06659 | NConv | 104518: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03999 | NConv | P12:345:OKGE:BKRBKR421 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03956 | NConv | P12:345:OKGE:BKRBKR421 | NA
Non-Converge | 00NR | S2 | 20SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.48674 | NConv | P1-1 POI - S1363: 646281 S1281 5 161 646363 S1363 5 161 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04521 | NConv | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04889 | NConv | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06341 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06326 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03798 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03728 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P23:345:MEC:MONTEZUMA 903 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P23:345:MEC:MONTEZUMA 903 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03004 | NConv | 812120: 514803 SOONER 7 345 514806 SOONER2G 20.0 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P23:345:MEC:SYCAMORE 901 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P23:345:MEC:SYCAMORE 901 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.116 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11509 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P23:345:XEL:8S72 HNA | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P23:345:XEL:8S72 HNA | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04846 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04904 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06559 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06547 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05484 | NConv | P23:345:WAPA:SIOUXCY:8592-8696 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05982 | NConv | P23:345:WAPA:SIOUXCY:8592-8696 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11779 | NConv | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11091 | NConv | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03815 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0382 | NConv | 8616: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04545 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998316 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04508 | NConv | 81740: 514803 SOONER 7 345 515576 RANCHRD7 345 1 514803 SOONER 7 345 515894 THUNDER7 345 1 514803 SOONER 7 345 560056 G15066_T 345 1 514803 SOONER 7 345 560084 G16-061-TAP 345 1 514803 SOONER 7 345 587804 G16-100-TAP 345 1 514803 SOONER 7 345 998316 SOONER5 138 1 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04304 | NConv | 104890: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03174 | NConv | 104890: 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04521 | NConv | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04889 | NConv | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03878 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04065 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P23:345:MEC:SYCAMORE 902 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P23:345:MEC:SYCAMORE 902 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0406 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03983 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04087 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0401 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05009 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04914 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03772 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03919 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16023 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15607 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05002 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04881 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16023 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15607 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05009 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04914 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0406 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03983 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03798 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03728 | NConv | 105468: 528219 CHINA_DRAW 1 13.2 997999 UPDATE LATER 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03435 | NConv | P23:345:AMMO::ZACHARY:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03513 | NConv | P23:345:AMMO::ZACHARY:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P23:345:MEC:MONTEZUMA 901 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P23:345:MEC:MONTEZUMA 901 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06341 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06326 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0406 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03983 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P23:345:MEC:BONDURANT 906 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P23:345:MEC:BONDURANT 906 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04846 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04904 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03888 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0383 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0329 | NConv | P23:345:MEC:LOUISA 954 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03364 | NConv | P23:345:MEC:LOUISA 954 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0857 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08491 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03815 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0382 | NConv | 104275: 532791 BENTON 7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 532797 WOLFCRK7 345 997932 WOLF TX-6 69.0 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0568 | NConv | P42:345:NPPD:BKR-MOR-3310 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05218 | NConv | P42:345:NPPD:BKR-MOR-3310 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11779 | NConv | P42:345:NPPD:BKR-MOR-3306 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11091 | NConv | P42:345:NPPD:BKR-MOR-3306 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03772 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03919 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12815 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12553 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03906 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04094 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12789 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12724 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0559 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0552 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03772 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03919 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03798 | NConv | 105454: 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997960 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03728 | NConv | 105454: 531511 HARBNGR-T 13.8 997960 HARBGR345 115 1 523823 CARPENTER 7 345 531512 HARBNGR7 345 Z1 531512 HARBNGR7 345 997960 HARBGR345 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523823 CARPENTER 7 345 523853 FINNEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03798 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03728 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07104 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06775 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03878 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04065 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.116 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11509 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07385 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07602 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08894 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09073 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05009 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04914 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04545 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04508 | NConv | 8609: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03888 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0383 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03268 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03209 | NConv | P23:345:SUNC:HLC_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05009 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04914 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04521 | NConv | P23:345:MEC:OBRIEN 903 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04889 | NConv | P23:345:MEC:OBRIEN 903 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06559 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06547 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05484 | NConv | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05982 | NConv | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05002 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04881 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04521 | NConv | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04889 | NConv | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04521 | NConv | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1: 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04889 | NConv | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1: 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04545 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04508 | NConv | 104273: 532791 BENTON 7 345 532794 ROSEHIL7 345 1 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 532794 ROSEHIL7 345 560053 G15052_T 345 1 532794 ROSEHIL7 345 997883 ROSE TX-1 138 1 532794 ROSEHIL7 345 997882 ROSE TX-3 138 1 532794 ROSEHIL7 345 997881 ROSE TX-5 138 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05009 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04914 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07332 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07123 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04369 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04505 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09643 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0945 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-ALTE:AUTO-SINGLE:HCKRYCK3:EDEN345:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03878 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04065 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03772 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 29SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03919 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04826 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04731 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05796 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05782 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 1045321: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 1045321: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04358 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04275 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:MONTEZUMA 903 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:MONTEZUMA 903 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05564 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05494 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:GDMEC 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:GDMEC 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:SYCAMORE 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:SYCAMORE 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P23:345:XEL:8S72 HNA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P23:345:XEL:8S72 HNA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0482 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04878 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06243 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06232 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04165 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04354 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03348 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03426 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03472 | NConv | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07001 | NConv | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07006 | NConv | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04165 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04354 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03952 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04075 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03685 | NConv | P23:345:MEC:SYCAMORE 905 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03792 | NConv | P23:345:MEC:SYCAMORE 905 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | 104487: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541254 EAST 5 161 541401 EASTOWN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | 104487: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541254 EAST 5 161 541401 EASTOWN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04826 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04731 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07001 | NConv | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07006 | NConv | 300039 7FAIRPT 345 541199 ST JOE 3 345 1: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04941 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03952 | NConv | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04075 | NConv | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08109 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07881 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08109 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07881 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04358 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04275 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03348 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03426 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.15962 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15546 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04918 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04798 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05564 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05494 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.15962 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15546 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | P23:345:SUNC:HLC_BRK382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:SUNC:HLC_BRK382 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03348 | NConv | P23:345:AMMO::ZACHARY:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03426 | NConv | P23:345:AMMO::ZACHARY:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:MONTEZUMA 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:MONTEZUMA 901 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05796 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05782 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04358 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04275 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03348 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03426 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05564 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05494 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:BONDURANT 906 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:BONDURANT 906 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03982 | NConv | 4013: 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | 4013: 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0482 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04878 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03089 | NConv | P23:500:EES-EAI:INDEP2:B6126 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03133 | NConv | P23:500:EES-EAI:INDEP2:B6126 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0482 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04878 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:SYCAMORE 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:SYCAMORE 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03952 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04075 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04826 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04731 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 846851: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 846851: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07001 | NConv | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07006 | NConv | P23:161-345:GMO-AECI:STJOE_R3-22::STJOE-FAIRPORT-STJOET33 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05564 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05494 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12361 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12099 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04358 | NConv | P23:345:SUNC:SB_BRK488 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04275 | NConv | P23:345:SUNC:SB_BRK488 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05564 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05494 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03952 | NConv | P23:345:MEC:MONTEZUMA 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04075 | NConv | P23:345:MEC:MONTEZUMA 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04165 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04354 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07354 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0757 | NConv | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1: 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04826 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04731 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04358 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04275 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03403 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03345 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04826 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04731 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08109 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07881 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03952 | NConv | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04075 | NConv | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06243 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06232 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08149 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08071 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04918 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04798 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11333 | NConv | 84807: 541254 EAST 5 161 541401 EASTOWN5 161 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11243 | NConv | 84807: 541254 EAST 5 161 541401 EASTOWN5 161 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06429 | NConv | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03668 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03795 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08772 | NConv | P23:345:MEC:GDMEC 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08953 | NConv | P23:345:MEC:GDMEC 902 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12495 | NConv | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.1243 | NConv | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07169 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06961 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.09321 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09128 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08109 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07881 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03665 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03589 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04244 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04381 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04195 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 24WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04385 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | P22:345:MEC:SUB 92 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03397 | NConv | P22:345:MEC:SUB 92 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12773 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12512 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12773 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12512 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12773 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12512 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | P45:345:UMZW:# 1328 #: GI IN NE. | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11575 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11485 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04849 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04907 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06609 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06597 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03397 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05041 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04946 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05187 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05128 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16111 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15696 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.16111 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15696 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03459 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03537 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12773 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12512 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | P23:345:MEC:HILLS 934 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03397 | NConv | P23:345:MEC:HILLS 934 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03323 | NConv | P23:345:MEC:HILLS 9114 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03397 | NConv | P23:345:MEC:HILLS 9114 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04849 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04907 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04849 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04907 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03989 | NConv | P12:345:XEL:SPS HNA-SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04179 | NConv | P12:345:XEL:SPS HNA-SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03989 | NConv | P23:345:XEL:SPS 8S81 SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04179 | NConv | P23:345:XEL:SPS 8S81 SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05041 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04946 | NConv | P42:345:NPPD:BKR-RW-3302 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05041 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04946 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12773 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12512 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05713 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05643 | NConv | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.11575 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11485 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08931 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09112 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05041 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04946 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06609 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06597 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0655 | NConv | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03826 | NConv | P23:345:MEC:LOUISA 924 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03952 | NConv | P23:345:MEC:LOUISA 924 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03961 | NConv | P12:345:XEL:SPS WLM-SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0415 | NConv | P12:345:XEL:SPS WLM-SSL | NA
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04397 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04534 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0964 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 24SP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09446 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04318 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04242 | NConv | P23:345:SUNC:HLC_BRK282 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104113: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07031 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06711 | NConv | P42:345:NPPD:BKR-AXT-3308 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805055: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104119: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84354: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 542972 HAWTH 7 345 997751 HAWTHORN22 161 22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177403: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104096: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104096: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08346 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08122 | NConv | 300039 7FAIRPT 345 640139 COOPER 3 345 1: 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | 84356: 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532799 WAVERLY7 345 542981 LACYGNE7 345 1 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 542968 STILWEL7 345 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543629 LACYGNE11_7 345 1 542981 LACYGNE7 345 543632 LACYGNE22_7 345 1 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 542981 LACYGNE7 345 543667 LAC3_STAR7 345 H 542981 LACYGNE7 345 543669 LAC8_STAR7 345 H 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P23:345:MEC:HILLS 924 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:MEC:HILLS 924 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05911 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.059 | NConv | 104264: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04893 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04952 | NConv | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1: 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 84378: 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P23:345:OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P23:345:MEC:HILLS 9114 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P23:345:MEC:HILLS 9114 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | 104216: 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | 104216: 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92251: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04272 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04203 | NConv | 105456: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P44:345:OPPD:S3458-HOL&R1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177405: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04272 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04203 | NConv | 93023: 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523094 HITCHLD_TR21 13.2 998152 SIEM 8743067 230 2 523097 HITCHLAND 7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04092 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04082 | NConv | 104274: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P23:345:MEC:SUB TIC 944 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:MEC:SUB TIC 944 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04893 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04952 | NConv | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z: 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03516 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03685 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104214: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104214: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 997752 HAWTHORN20 161 20 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | 84388: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92244: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104115: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03391 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03522 | NConv | P23:345:MEC:KOSSUTH 904 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08346 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08122 | NConv | P42:345:NPPD:BKR-C-3322-2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 846850: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08346 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08122 | NConv | P42:345:NPPD:BKR-CPR-3322 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | 104520: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04719 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04638 | NConv | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104082: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P23:345:AMMO-MEC::SUBT:T944 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:AMMO-MEC::SUBT:T944 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104080: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104080: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104561: 541197 MULLNCR7 345 541500 KETCHEM7 345 1 541413 MC REAC3 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03391 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03522 | NConv | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1: 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P22:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03432 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0351 | NConv | P12:345:AMMO::ZACHARY:MAYWOOD:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84337: 541203 NASHUA 5 161 541247 LBRTYWT5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P23:345:XEL:8S72 HNA | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P23:345:XEL:8S72 HNA | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104084: 542976 LEVEE 5 161 543666 NEASTN5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 104073: 541204 SMTHVL 5 161 541349 POPE 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 104522: 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1625 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15829 | NConv | 83249: 640139 COOPER 3 345 645458 S3458 3 345 1 541510 HOLT 7 345 645458 S3458 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104094: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05138 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05019 | NConv | 805042: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92254: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | 69828: 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635701 SYCAMOR5 161 635705 ANKENY 5 161 1 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1: 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04719 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04638 | NConv | P23:345:SUNC:SB_BRK482 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04092 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04082 | NConv | 8615: 532771 RENO 7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 1 532782 BUFFALO7 345 532796 WICHITA7 345 2 532791 BENTON 7 345 532796 WICHITA7 345 1 532796 WICHITA7 345 532798 VIOLA 7 345 1 532796 WICHITA7 345 562476 G14_001T 345 1 532796 WICHITA7 345 997934 WICH TX-11 138 1 532796 WICHITA7 345 997933 WICH TX-12 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P22:345:MEC:SUB T | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P22:345:MEC:SUB T | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03664 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03607 | NConv | P23:345:SUNC:HLC_BRK188 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03391 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03522 | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03516 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03685 | NConv | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P23:345:MEC:HILLS 914 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:MEC:HILLS 914 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 84314: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1625 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.15829 | NConv | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104510: 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P12:345:GMO-OPPD:S3458-HOLT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805052: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | 636400 HILLS 3 345 636645 SUB T HSK 3 345 1: 636400 HILLS 3 345 636645 SUB T HSK 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | P23:345:WERE:N345_345-80:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | P23:345:WERE:N345_345-80:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 852721: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04746 | NConv | P23:345:AMMO::MAYWOOD:2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04939 | NConv | P23:345:AMMO::MAYWOOD:2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 40910: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92268: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P23:345:MEC:HILLS 934 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P23:345:MEC:HILLS 934 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05251 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05158 | NConv | P23:345:SUNC:MO_BRK188 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03161 | NConv | P23:500:EES-EAI:INDEP2:B6126 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03205 | NConv | P23:500:EES-EAI:INDEP2:B6126 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805050: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04318 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04242 | NConv | P23:345:SUNC:HLC_BRK382 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04828 | NConv | P23:345:WERE:87TH_345_BKRS:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04773 | NConv | P23:345:WERE:87TH_345_BKRS:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | P42:345:NPPD:BKR-CPR-3304 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06605 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06595 | NConv | 104516: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 84339: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541204 SMTHVL 5 161 541349 POPE 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805054: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04719 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04638 | NConv | P23:345:SUNC:MO_BRK182 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104083: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | 104524: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177401: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:MEC:MONTEZUMA 903 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84447: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84825: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 371300: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03432 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0351 | NConv | P23:345:AMMO::ZACHARY:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92242: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 371301: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:MEC:MONTEZUMA 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 84379: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | 601050 HELENA 3 345 601072 SHEAS LK3 345 1: 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P21:345:MEC:AUTO-SINGLE:HILLS3:SUBT3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:MEC:SYCAMORE 901 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84371: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84371: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | 104631: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92245: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05138 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05019 | NConv | 4010: 531469 SPERVIL7 345 531501 BUCKNER7 345 1 531469 SPERVIL7 345 539800 CLARKCOUNTY7 345 1 531469 SPERVIL7 345 539803 IRONWOOD7 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 531469 SPERVIL7 345 997841 SPEARVL 230 1 531469 SPERVIL7 345 997799 SPEARVILLE 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177404: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05251 | NConv | P42:345:NPPD:BKR-RW-3302 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05158 | NConv | P42:345:NPPD:BKR-RW-3302 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | 601032 FIELD_S3 345 601033 FIELD_N3 345 1: 601032 FIELD_S3 345 601033 FIELD_N3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177402: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P12:345:MEC:HILLS-SUB T-LOUISA + REACTOR | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P12:345:MEC:HILLS-SUB T-LOUISA + REACTOR | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P23:345:XEL:8S22 WLM | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P23:345:XEL:8S22 WLM | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | 69829: 635680 BONDRNT3 345 635690 GDMEC 3 345 1 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 635670 DMOINES5 161 635672 METRO E5 161 1 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 635672 METRO E5 161 635673 ALTONA 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0437 | NConv | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04507 | NConv | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03597 | NConv | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04893 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04952 | NConv | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1: 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P12:345:MEC:WALCOTT-HILLS-LOUISA | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 852711: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P23:345:XEL:8S81 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05251 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05158 | NConv | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84486: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84486: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05911 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.059 | NConv | 8610: 532765 HOYT 7 345 532772 STRANGR7 345 1 532772 STRANGR7 345 532775 87TH 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 532772 STRANGR7 345 588240 GEN-2016-149 345 1 532772 STRANGR7 345 997948 STRA TX-1 115 1 532772 STRANGR7 345 997947 STRA TX-3 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92243: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104095: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P23:345:XEL:8S82 & 8S79 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92256: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92256: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03597 | NConv | 635017 ATCHSN 3 345 640139 COOPER 3 345 1: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03391 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03522 | NConv | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05251 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05158 | NConv | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104091: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P22:345:MEC:SUB 92 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P22:345:MEC:SUB 92 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84445: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84445: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.06605 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.06595 | NConv | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 104625: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104562: 541411 MC REAC1 345 541197 MULLNCR7 345 541510 HOLT 7 345 1 541412 MC REAC2 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104707: 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541201 SIBLEY 7 345 997777 SIBLEY11 161 11 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P14:345:GMO-OPPD:S3458 REACTOR | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92261: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92261: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104099: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104118: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | P12:345:MEC:AUTO-SINGLE:HILLS3:SUB923:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04744 | NConv | P12:345:WERE:N345-LACY_345:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04685 | NConv | P12:345:WERE:N345-LACY_345:: | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03597 | NConv | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805051: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 1045320: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92270: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92270: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 40911: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 177400: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03432 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0351 | NConv | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1: 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03597 | NConv | 82337: 635017 ATCHSN 3 345 640139 COOPER 3 345 1 635000 CBLUFFS3 345 645456 S3456 3 345 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104147: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104147: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84451: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03432 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.0351 | NConv | P23:345:AMMO::ZACHARY:2 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08346 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08122 | NConv | P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03516 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03685 | NConv | 601004 WILMART3 345 601072 SHEAS LK3 345 1: 601004 WILMART3 345 601072 SHEAS LK3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104563: 541510 HOLT 7 345 645458 S3458 3 345 1 541517 HOLT_REACT7 345 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 84431: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 805053: 530583 POSTROCK7 345 997991 POSTROCK T1 230 1 530584 POSTROCK6 230 997991 POSTROCK T1 230 1 530673 POSTROCK1 13.8 997991 POSTROCK T1 230 1 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0437 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04507 | NConv | 344000 7ZACKARY 345 344011 7HUGHES 345 1: 344000 7ZACKARY 345 344011 7HUGHES 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 104072: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04719 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04638 | NConv | P23:345:SUNC:MO_BRK382 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104085: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1: 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | P55:161-345:GMO-KCPL:SIBLEY_BUS_11:: | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104098: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12727 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12471 | NConv | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104560: 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 541414 SIB REA1 345 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04719 | NConv | P23:345:SUNC:SB_BRK488 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04638 | NConv | P23:345:SUNC:SB_BRK488 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 852710: 640066 AXTELL 7 115 997464 AXTELL T1 115 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 640067 AXTELL 9 13.8 997464 AXTELL T1 115 1 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03778 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03905 | NConv | P23:345:MEC:LOUISA 924 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.1164 | NConv | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.11555 | NConv | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | 601004 WILMART3 345 601033 FIELD_N3 345 1: 601004 WILMART3 345 601033 FIELD_N3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04828 | NConv | 104267: 532772 STRANGR7 345 532775 87TH 7 345 1 532775 87TH 7 345 542977 CRAIG 7 345 1 532775 87TH 7 345 997943 87TH TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04773 | NConv | 104267: 532772 STRANGR7 345 532775 87TH 7 345 1 532775 87TH 7 345 542977 CRAIG 7 345 1 532775 87TH 7 345 997943 87TH TX-1 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104111: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104111: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:MEC:SYCAMORE 902 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | NOT FOUND | NConv | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03797 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03985 | NConv | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03597 | NConv | 635017 ATCHSN 3 345 635018 WESTBORO 3 345 1: 635017 ATCHSN 3 345 635018 WESTBORO 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92274: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03545 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03715 | NConv | P23:345:XEL:8S82 SSL | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.07433 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.07229 | NConv | 852720: 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03309 | NConv | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03384 | NConv | 636400 HILLS 3 345 636630 SUB 92 3 345 1: 636400 HILLS 3 345 636630 SUB 92 3 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104102: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104102: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92240: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92240: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.0959 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09399 | NConv | 104517: 541201 SIBLEY 7 345 541414 SIB REA1 345 Z1 345408 7OVERTON 345 541201 SIBLEY 7 345 1 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08958 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.09141 | NConv | P23:345:MEC:BONDURANT 906 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.05251 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.05158 | NConv | P23:345:SUNC:MO_BRK388 | NA | non-Converged in the BC | N/A
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.12836 | NConv | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12776 | NConv | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04318 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04242 | NConv | P23:345:SUNC:SB_BRK582 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.04318 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.04242 | NConv | 4005: 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 104109: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.03836 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.03761 | NConv | 92255: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_025_028 |  | Non-Converge |  |  | 0.08432 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 00NR | S2 | 19WP0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.08357 | NConv | 84338: 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | NA
Non-Converge | 09NR | S2 | 20G0 | GEN_025_028 |  | Non-Converge |  |  | 0.1288 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA
Non-Converge | 09NR | S2 | 20G0 | GEN_043_044_045 |  | Non-Converge |  |  | 0.12624 | NConv | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | NA

## All Voltage
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | MONITORED ELEMENT | BC Voltage (PU) | TC Voltage (PU) | Voltage Differ (PU) | VINIT (PU) | VMIN (PU) | VMAX (PU) | TDF | CONTINGENCY | Footprint
NRIS | 00NR | S2 | 20SP0 | N/A | EAUCLAIRCAP7 | 0.9334 | 0.8803 | -0.0531 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LAWNRID3 | 0.9156 | 0.8856 | 0.03 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | POSTVIL5 | 0.9673 | 0.9282 | 0.0391 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SIBLEYPL | >0.97 | 0.9417 | >0.0283 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COGGON 5 | 0.9558 | 0.8992 | -0.0566 | 161 | 0.9 | 1.05 | 0.03575 | P23:345:MEC:ATCHISON CO 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | AXTELL 3 | 0.9075 | 0.8725 | 0.035 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MCCOOL 3 | 0.8539 | 0.8313 | 0.0226 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GENOA 5 | 0.968 | 0.939 | 0.029 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEVADA 5 | 0.9232 | 0.885 | -0.0382 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 141 44 5 | 0.9285 | 0.8558 | -0.0727 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WILLOW CRK 5 | 0.9283 | 0.8549 | -0.0734 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SQUARED7 | >0.97 | 0.9394 | >0.0306 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | CHASE 3 | 0.9466 | 0.9247 | 0.0219 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WALCOTT3 | 0.9337 | 0.8997 | 0.034 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5FAIRPT | 0.9279 | 0.8809 | 0.047 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S EAST 5 | 0.9477 | 0.9147 | 0.033 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NASHUA 7 | >0.97 | 0.9397 | >0.0303 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 56&ELK TAP7 | 0.9691 | 0.9478 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CIRCLVL3 | >0.97 | 0.9477 | >0.0223 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5STURGN | 0.9647 | 0.9358 | 0.0289 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HILLS-DT-RX3 | 0.915 | 0.8686 | 0.0464 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BREMER CO5 | 0.9691 | 0.94 | 0.0291 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OAKGRV 5 | 0.9621 | 0.9283 | 0.0338 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NSI TAP3 | 0.9452 | 0.8924 | -0.0528 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-074 | 0.9538 | 0.8922 | -0.0616 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 30&A 7 | 0.9653 | 0.9439 | 0.0214 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MCDONLD3 | 0.9322 | 0.8765 | -0.0557 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CALAMUS7 | 0.9694 | 0.9288 | 0.0406 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | AVENUECTY 5 | 0.9283 | 0.8794 | 0.0489 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5LATHRP | 0.9168 | 0.8741 | 0.0427 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DIAMOND TRL3 | 0.909 | 0.8489 | 0.0601 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 76 5 | 0.9326 | 0.8983 | -0.0343 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | PINE LK7 | 0.9266 | 0.8839 | -0.0427 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LINWELD5 | 0.9308 | 0.8569 | -0.0739 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | TROUT B7 | 0.9279 | 0.8978 | -0.0301 | 115 | 0.9 | 1.05 | NOT FOUND | 71599.0 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 59CRNHUSKR7 | 0.9682 | 0.947 | 0.0212 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COOPER_602 8 | 0.9568 | 0.8943 | -0.0625 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | S967 8 | 0.9653 | 0.9294 | 0.0359 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ENT WAY 5 | 0.934 | 0.8987 | -0.0353 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SLMNFRK3 | 0.9163 | 0.8827 | 0.0336 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BUTLER 5 | 0.9685 | 0.9385 | 0.03 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SLMNFRK7 | 0.9134 | 0.8787 | 0.0347 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OSBORN7 | >0.92 | 0.8964 | >0.0236 | 345 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 40&GERTIE 7 | 0.9692 | 0.9478 | 0.0214 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MALTABN5 | 0.9476 | 0.9149 | 0.0327 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WAFBE_SW5 | 0.9388 | 0.907 | 0.0318 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUMNERMU8 | >0.97 | 0.9496 | >0.0204 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PRAR CK7 | >0.97 | 0.9414 | >0.0286 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MNTZUMA3 | 0.9149 | 0.8522 | 0.0627 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ATWODSW3 | 0.9336 | 0.8802 | -0.0534 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5NODWAY | >0.97 | 0.9481 | >0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ELLIS 2 | 0.9293 | 0.883 | -0.0463 | 69 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DYSART 5 | 0.9597 | 0.9169 | 0.0428 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MRSHLND5 | 0.966 | 0.9448 | 0.0212 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5MOBTAP | >0.97 | 0.9393 | >0.0307 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB 93 3 | 0.9417 | 0.9041 | 0.0376 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TECHILL5 | 0.9625 | 0.9324 | 0.0301 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PAWNEE 3 | 0.964 | 0.944 | 0.02 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 39 3 | 0.9585 | 0.9335 | 0.025 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | COULEE 5 | >0.97 | 0.9484 | >0.0216 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RIVERDL4 | 0.8808 | 0.8566 | 0.0242 | 230 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 4VAN S 3 | 0.9688 | 0.9483 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TREMVAL5 | 0.9328 | 0.9055 | 0.0273 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | LEESUM 5 | >0.97 | 0.9473 | >0.0227 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EDWARVL3 | 0.9439 | 0.9184 | 0.0255 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | P1 MPT PRI | 0.9686 | 0.9485 | 0.0201 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PENTAGN3 | >0.97 | 0.9484 | >0.0216 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | POSTROCK7 | >0.97 | 0.941 | >0.029 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COOPER 8 | >0.97 | 0.9333 | >0.0367 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 2MADISN3 | 0.9689 | 0.9483 | 0.0206 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CRLRIDG5 | 0.9065 | 0.8622 | 0.0443 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | LUFKIN | 0.9279 | 0.8813 | -0.0466 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WEST---5 | 0.9475 | 0.9145 | 0.033 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | UNIONCF5 | 0.9699 | 0.9374 | 0.0325 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 53 5 | 0.9392 | 0.9099 | 0.0293 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DEWITT 5 | 0.9379 | 0.8994 | -0.0385 | 161 | 0.9 | 1.05 | 0.03575 | P23:345:MEC:ATCHISON CO 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BL.PLN.5 | 0.9425 | 0.8916 | 0.0509 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S965 8 | 0.9635 | 0.8944 | -0.0691 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EASTOWN7 | 0.9697 | 0.8936 | -0.0761 | 345 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EASTOWN5 | 0.9589 | 0.9095 | 0.0494 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STONEMAN | 0.9144 | 0.8806 | 0.0338 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BEVERLY5 | 0.9399 | 0.9026 | 0.0373 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ROCK CK3 | 0.9655 | 0.9416 | 0.0239 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MC REAC1 | >0.97 | 0.9188 | >0.0512 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MC REAC3 | >0.97 | 0.9188 | >0.0512 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MC REAC2 | >0.97 | 0.9188 | >0.0512 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BVR CRK 3 | 0.9662 | 0.9363 | 0.0299 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | APL RVR5 | 0.9126 | 0.8697 | -0.0429 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BVR CHN L1 5 | 0.9573 | 0.9309 | 0.0264 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NW12&ARBOR7 | 0.9683 | 0.9475 | 0.0208 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2017-013 | 0.9124 | 0.8778 | 0.0346 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WAFBE5 | 0.9381 | 0.9062 | 0.0319 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HAZLTON L2 5 | >0.97 | 0.9361 | >0.0339 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SALE5 | 0.9674 | 0.9259 | 0.0415 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | WAFBW_SW5 | 0.939 | 0.9071 | 0.0319 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GR MND 5 | 0.9329 | 0.8998 | 0.0331 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | J475-J555POI | 0.9151 | 0.8524 | 0.0627 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5MEADVL | 0.9055 | 0.8789 | 0.0266 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 2MADISN2 | >0.97 | 0.9493 | >0.0207 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HYDROLN5 | 0.9173 | 0.8677 | -0.0496 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BRDGPRT5 | 0.9686 | 0.9078 | 0.0608 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 20PIONEERS7 | >0.97 | 0.9495 | >0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ST CROIG | 0.9285 | 0.8901 | -0.0384 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | S1263 5 | 0.9659 | 0.9265 | 0.0394 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CFUINDP5 | >0.97 | 0.9383 | >0.0317 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SPRINT25 | >0.97 | 0.9468 | >0.0232 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GOODCTY3 | 0.9073 | 0.8754 | 0.0319 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STANGE 5 | 0.9223 | 0.8606 | -0.0617 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 48 5 | 0.9386 | 0.912 | 0.0266 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB T HSK 3 | 0.931 | 0.8886 | 0.0424 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 56&EVERETT7 | 0.9663 | 0.9449 | 0.0214 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CRYSTLCVCAP7 | 0.9294 | 0.8878 | -0.0416 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LACROS 3 | 0.968 | 0.9475 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WTWEST 5 | 0.9661 | 0.9318 | 0.0343 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NATWOOD3 | 0.9335 | 0.8801 | -0.0534 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 88TH 5 | 0.9261 | 0.8528 | -0.0733 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEKOMA 3 | 0.959 | 0.9375 | 0.0215 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RLHILLS3 | >0.97 | 0.9457 | >0.0243 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BVERVLLY | 0.9318 | 0.8761 | -0.0557 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STERLNG7 | 0.9393 | 0.8972 | -0.0421 | 115 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WAPELLO5 | 0.9675 | 0.9121 | 0.0554 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GOFF 3 | >0.97 | 0.9494 | >0.0206 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PINELKT5 | 0.9231 | 0.8807 | -0.0424 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | RICHMND5 | 0.9567 | 0.9213 | 0.0354 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5ADAIR1 | 0.962 | 0.8983 | -0.0637 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5ADAIR3 | 0.962 | 0.8982 | -0.0638 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5ADAIR2 | 0.962 | 0.8982 | -0.0638 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | RULETON3 | 0.9457 | 0.8909 | -0.0548 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | KARMA 5 | 0.9455 | 0.9111 | 0.0344 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | PRASWCP7 | <1.03 | 1.0505 | >0.0205 | 115 | 0.9 | 1.05 | 0.05595 | 105818: 640202 GR ISLD9 34.5 997400 GRAND.ISD T1 34.5 1 640203 G.I.T219 13.8 997402 GRAND.ISD T2 115 1 640131 COLMB.W4 230 640200 GR ISLD4 230 1 640200 GR ISLD4 230 640214 HASTING4 230 1 640200 GR ISLD4 230 640330 RIVERDL4 230 1 640200 GR ISLD4 230 997403 GI KU3A 230 3 640200 GR ISLD4 230 997402 GRAND.ISD T2 115 1 640200 GR ISLD4 230 997401 GRAND.ISD T5 115 2 640200 GR ISLD4 230 997132 GI KU1A 230 1 640200 GR ISLD4 230 997131 GI KU1B 230 2 640063 AURORA_7 115 640201 GR ISLD7 115 1 640107 CENCITY7 115 640201 GR ISLD7 115 1 640201 GR ISLD7 115 640353 ST.LIB 7 115 1 640201 GR ISLD7 115 642071 SUB-D 7 115 1 640201 GR ISLD7 115 642072 SUB-E 7 115 1 640201 GR ISLD7 115 997402 GRAND.ISD T2 115 1 640201 GR ISLD7 115 997401 GRAND.ISD T5 115 2 640201 GR ISLD7 115 997400 GRAND.ISD T1 34.5 1 643070 GR ISLD T5 9 13.8 997401 GRAND.ISD T5 115 2 643071 GR ISLD T6 9 13.8 997403 GI KU3A 230 3 653314 GR ISL19 13.8 997132 GI KU1A 230 1 653316 GR ISL29 13.8 997131 GI KU1B 230 2 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SAINTS RUN7 | >0.97 | 0.9303 | >0.0397 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HCKRYCK5 | >0.97 | 0.9303 | >0.0397 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GRNGRTP5 | 0.929 | 0.8557 | -0.0733 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SWEET W3 | 0.9183 | 0.8876 | 0.0307 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BVR CHN L2 5 | 0.9571 | 0.9307 | 0.0264 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HCKRYCK3 | 0.9382 | 0.893 | 0.0452 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HOYT 7 | >0.97 | 0.9498 | >0.0202 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GRAINVL5 | 0.9645 | 0.9311 | 0.0334 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5OSCEOKC | 0.9526 | 0.9296 | 0.023 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TOLEDO 5 | 0.9664 | 0.8981 | -0.0683 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-163 | >0.97 | 0.9427 | >0.0273 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HILLSIE5 | 0.9233 | 0.8805 | 0.0428 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SPRINT15 | >0.97 | 0.9491 | >0.0209 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MIDPORT5 | 0.9668 | 0.9312 | 0.0356 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SALEM L2 5 | >0.97 | 0.9367 | >0.0333 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 8&N 7 | 0.9671 | 0.9458 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GRENFLD5 | 0.9326 | 0.8587 | -0.0739 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WAFBW5 | 0.9388 | 0.9069 | 0.0319 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SANTAFJ2 | >0.97 | 0.9496 | >0.0204 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SALSBRY5 | 0.9672 | 0.9331 | 0.0341 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LUNDQST5 | 0.9653 | 0.9303 | 0.035 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DOUD 5 | 0.9307 | 0.8717 | -0.059 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 34 NW 5 | 0.9312 | 0.858 | -0.0732 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | DRAGER5 | >0.97 | 0.9487 | >0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DRYCREK7 | >0.97 | 0.9287 | >0.0413 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | PERRY WILLI5 | 0.9389 | 0.8765 | -0.0624 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5GENTRY | 0.9343 | 0.8898 | 0.0445 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HSNVL 5 | 0.9685 | 0.9403 | 0.0282 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HIAWATA5 | 0.9594 | 0.9171 | 0.0423 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HIAWATA7 | >0.97 | 0.9333 | >0.0367 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | WBURGE 5 | 0.9433 | 0.8997 | -0.0436 | 161 | 0.9 | 1.05 | 0.03956 | P42:345:OKGE:SB_REOW7312 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BLSPW 5 | >0.97 | 0.9397 | >0.0303 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STH HILL WD | >0.97 | 0.9349 | >0.0351 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 33SUPERIOR7 | 0.9689 | 0.9478 | 0.0211 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MARION K1 7 | 0.9664 | 0.9247 | 0.0417 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 70 5 | 0.9287 | 0.8967 | -0.032 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | HAZLTON L1 5 | >0.97 | 0.9363 | >0.0337 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | QUINN3 | 0.9137 | 0.8894 | 0.0243 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | COOK 5 | 0.9558 | 0.9052 | 0.0506 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MULLNCR7 | >0.97 | 0.9188 | >0.0512 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LKWOOD 5 | >0.97 | 0.9431 | >0.0269 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | KNLWRTH5 | >0.97 | 0.9496 | >0.0204 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LAXTAP 3 | 0.9685 | 0.948 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TCE TAP8 | 0.9646 | 0.9428 | 0.0218 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GR ISLD3 | 0.8575 | 0.8333 | 0.0242 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ONEOK 3 | 0.9315 | 0.8757 | -0.0558 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-162 | >0.97 | 0.9426 | >0.0274 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GR ISLD4 | 0.8661 | 0.8439 | 0.0222 | 230 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HASTING4 | 0.8746 | 0.8541 | 0.0205 | 230 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5REX | 0.9091 | 0.8639 | 0.0452 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S977 8 | 0.9448 | 0.9093 | 0.0355 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LAUREL_5 | >0.97 | 0.9359 | >0.0341 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | JOHNSTON 5 | 0.9294 | 0.8563 | -0.0731 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB 77 5 | 0.9361 | 0.908 | 0.0281 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HUXLEY 5 | 0.9282 | 0.8645 | -0.0637 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | COOPER 5 | >0.97 | 0.9333 | >0.0367 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 28 5 | 0.9509 | 0.924 | 0.0269 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | KELLY 5 | >0.97 | 0.9401 | >0.0299 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ROCKCK7 | >0.97 | 0.9187 | >0.0513 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SETAB 3 | 0.9572 | 0.9361 | 0.0211 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SETAB 7 | 0.9541 | 0.9291 | 0.025 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TRK RIV5 | 0.9175 | 0.8825 | 0.035 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 19&ALVO 7 | 0.9686 | 0.9479 | 0.0207 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 93&O 7 | 0.97 | 0.9489 | 0.0211 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SO.GVW.5 | >0.97 | 0.9273 | >0.0427 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SAVANAH2 | >0.97 | 0.9429 | >0.0271 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | VINTON 5 | 0.9575 | 0.8986 | -0.0589 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | POPLK_5 | 0.9236 | 0.8838 | -0.0398 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5BUTLER | 0.9337 | 0.8864 | -0.0473 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ASBURY 5 | 0.9597 | 0.9165 | 0.0432 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BEELER 3 | 0.9455 | 0.9223 | 0.0232 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | S HILLS 3 | >0.97 | 0.9347 | >0.0353 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | CNTRLPL3 | 0.9572 | 0.9371 | 0.0201 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PAULINE3 | 0.9196 | 0.8876 | 0.032 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STON PT7 | >0.97 | 0.936 | >0.034 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | STON PT5 | 0.9458 | 0.8983 | 0.0475 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SEGNTP 3 | 0.9099 | 0.8821 | 0.0278 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LIBERTY5 | >0.97 | 0.924 | >0.046 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5HICKCK | 0.8797 | 0.85 | 0.0297 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ORIENT 3 | >0.97 | 0.935 | >0.035 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S1280 5 | 0.9665 | 0.9248 | 0.0417 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 27FLETCHER7 | 0.9685 | 0.9476 | 0.0209 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 4&MORTON 7 | 0.9674 | 0.9464 | 0.021 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BLSPE 5 | >0.97 | 0.938 | >0.032 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BLSPS 5 | >0.97 | 0.9407 | >0.0293 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MANNGT 3 | 0.9531 | 0.9323 | 0.0208 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ROCKCKW5 | 0.9528 | 0.9248 | 0.028 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5SEDALA | 0.9387 | 0.9085 | 0.0302 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | COONRPDS G | 0.9653 | 0.9435 | 0.0218 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DIGHTON3 | 0.9513 | 0.9294 | 0.0219 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BERTRAM5 | 0.9423 | 0.9039 | 0.0384 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MQOKETA5 | 0.9434 | 0.9056 | 0.0378 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BERTRAM7 | >0.97 | 0.9291 | >0.0409 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MADISON3 | 0.9523 | 0.8774 | -0.0749 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | MCKSBRG 5 | 0.9687 | 0.9407 | 0.028 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NORWLK3 | 0.9439 | 0.8678 | -0.0761 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | MOORE 3 | 0.9608 | 0.9371 | 0.0237 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DELWARE5 | 0.9307 | 0.8575 | -0.0732 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NORWLK5 | 0.9397 | 0.8663 | -0.0734 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | AMES 5 | 0.9218 | 0.8592 | -0.0626 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | MIAMI_ 5 | 0.9473 | 0.9142 | 0.0331 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 7FAIRPT | 0.9458 | 0.894 | 0.0518 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 47 5 | 0.9441 | 0.9176 | 0.0265 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | FAIRFAX5 | 0.944 | 0.9031 | 0.0409 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HILLS 3 | 0.9153 | 0.8691 | 0.0462 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HILLS 5 | 0.9073 | 0.862 | 0.0453 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | G15088_T | 0.9632 | 0.8986 | -0.0646 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LUDELLT3 | 0.9096 | 0.8824 | 0.0272 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HALLIE 5 | 0.931 | 0.8783 | -0.0527 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5MOBERLY | >0.97 | 0.9392 | >0.0308 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5HIGBEE | >0.97 | 0.9416 | >0.0284 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RCK ELM5 | 0.9285 | 0.8892 | -0.0393 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5CHILLI | 0.8895 | 0.8647 | 0.0248 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BONDRNT3 | 0.9314 | 0.8524 | -0.079 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WTCLFTP3 | 0.9457 | 0.8996 | -0.0461 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BONDRNT5 | 0.9319 | 0.8587 | -0.0732 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SIB REA1 | >0.97 | 0.9422 | >0.0278 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EASTRLK5 | 0.9303 | 0.8562 | -0.0741 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | J416_WF3 | 0.9167 | 0.8923 | 0.0244 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | G16-050-TAP | 0.9069 | 0.8678 | 0.0391 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ARCHIE 5 | 0.9657 | 0.9377 | 0.028 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ALMA 5 | 0.9555 | 0.9323 | 0.0232 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 12&CLAY3 | 0.9691 | 0.9485 | 0.0206 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WILOWRV7 | 0.9279 | 0.8978 | -0.0301 | 115 | 0.9 | 1.05 | NOT FOUND | 71599.0 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 18 5 | 0.9465 | 0.9183 | 0.0282 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TECUMSH8 | 0.9646 | 0.9301 | 0.0345 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5LOCUST | 0.8674 | 0.8378 | 0.0296 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DEER RUN5 | 0.94 | 0.9024 | 0.0376 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DIAM TR WIND | 0.9092 | 0.8491 | 0.0601 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S966 8 | >0.97 | 0.948 | >0.022 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NORTON-5 | 0.9487 | 0.9157 | 0.033 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 3&VANDORN 7 | 0.9687 | 0.9474 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CNTRGRV5 | 0.9629 | 0.9197 | 0.0432 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | OLDSETTLERS7 | 0.9678 | 0.9256 | 0.0422 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | CLINTON5 | 0.9661 | 0.9382 | 0.0279 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LAKE RD5 | 0.9556 | 0.9049 | 0.0507 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TOMHAWK5 | >0.97 | 0.9497 | >0.0203 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 70&CALVERT7 | >0.97 | 0.9497 | >0.0203 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 31T 5 | 0.9505 | 0.9237 | 0.0268 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EAST 5 | 0.9561 | 0.9062 | 0.0499 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MGLN TP8 | 0.968 | 0.8928 | -0.0752 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | KERPER 5 | 0.9652 | 0.9213 | 0.0439 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EL FARM5 | >0.97 | 0.9427 | >0.0273 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MECCORD3 | >0.97 | 0.9495 | >0.0205 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | STFRANT3 | 0.9117 | 0.8817 | 0.03 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ATWOOD 3 | 0.9302 | 0.8748 | -0.0554 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BOONVIL5 | 0.9468 | 0.8725 | -0.0743 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LAW CRK7 | 0.9332 | 0.8982 | -0.035 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LAW CRK5 | 0.9307 | 0.8928 | -0.0379 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | RALSTON8 | 0.9674 | 0.9443 | 0.0231 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5NORTON | 0.9486 | 0.9157 | 0.0329 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEANKNY5 | 0.9294 | 0.8593 | -0.0701 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | P2 MPT PRI | 0.9689 | 0.9488 | 0.0201 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | AUBRNT 8 | 0.9546 | 0.914 | 0.0406 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RHOADES3 | 0.9694 | 0.949 | 0.0204 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HYDCAP 8 | >0.97 | 0.9484 | >0.0216 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DIGHTNT3 | 0.9518 | 0.9299 | 0.0219 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | W.BRCH 7 | >0.97 | 0.9325 | >0.0375 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB E IC 5 | 0.9034 | 0.8582 | 0.0452 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ALICERD5 | 0.92 | 0.8535 | 0.0665 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | DUNCAN 5 | >0.97 | 0.9385 | >0.0315 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RIVER RUN5 | 0.9414 | 0.9037 | 0.0377 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MT VERN5 | 0.9427 | 0.9046 | 0.0381 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 7OVERTON | >0.97 | 0.9489 | >0.0211 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DRFNDRY5 | 0.9656 | 0.931 | 0.0346 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | POWESHK5 | 0.9293 | 0.8722 | 0.0571 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | MUSCOTA2 | >0.97 | 0.9483 | >0.0217 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUB J IC 5 | 0.9074 | 0.8627 | 0.0447 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | DRCOMP 5 | 0.9653 | 0.9304 | 0.0349 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SEGUIN 3 | 0.9333 | 0.8789 | -0.0544 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 29LEIGHTON7 | 0.9665 | 0.9452 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-050 | 0.907 | 0.8678 | 0.0392 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NW70FAIRFD7 | 0.9688 | 0.948 | 0.0208 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PRESTOT5 | 0.9322 | 0.8792 | -0.053 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ATCHSN 3 | >0.97 | 0.9434 | >0.0266 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB U IC 5 | 0.9058 | 0.8614 | 0.0444 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EDMOND5 | 0.9551 | 0.9043 | 0.0508 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EAU CL 3 | 0.8675 | 0.81 | -0.0575 | 345 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | IC ENRON 5 | 0.9074 | 0.8623 | 0.0451 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | UNVERFRT8 | >0.97 | 0.9471 | >0.0229 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BLRSTWN7 | >0.97 | 0.9447 | >0.0253 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SHAULISRD5 | 0.9699 | 0.9369 | 0.033 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HERNDON3 | 0.916 | 0.8906 | 0.0254 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 60TH ST5 | 0.93 | 0.8568 | -0.0732 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BNE JCT5 | 0.9307 | 0.8717 | -0.059 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WHT 56 5 | 0.9366 | 0.8845 | -0.0521 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | TCE8 | 0.9616 | 0.9397 | 0.0219 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OAKGROV5 | 0.9473 | 0.9194 | 0.0279 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-115 | >0.97 | 0.9191 | >0.0509 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OAKGROV3 | 0.9475 | 0.9193 | 0.0282 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | KANARAD3 | 0.9451 | 0.8943 | -0.0508 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | JEFF 5 | 0.9528 | 0.899 | -0.0538 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SANTAFE2 | >0.97 | 0.9496 | >0.0204 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | JASPER 5 | 0.9539 | 0.9058 | 0.0481 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | JOHNSON3 | 0.9473 | 0.9211 | 0.0262 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PH RUN 3 | 0.9269 | 0.8697 | -0.0572 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 56&Q 7 | 0.9667 | 0.9454 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MAGELLN8 | 0.9675 | 0.8995 | -0.068 | 69 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2017-030 | 0.9221 | 0.8821 | 0.04 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NW5&BENTON7 | 0.9671 | 0.9461 | 0.021 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WOODBIN5 | 0.9569 | 0.9068 | 0.0501 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WNTRST 5 | 0.9455 | 0.9113 | 0.0342 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SHARNSP3 | 0.9466 | 0.9248 | 0.0218 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | JULIAN 5 | 0.9631 | 0.9198 | 0.0433 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 52 5 | 0.9389 | 0.9096 | 0.0293 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 88 5 | 0.9284 | 0.8961 | -0.0323 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BENTON 7 | 0.9692 | 0.9415 | -0.0277 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DUNDEE 5 | 0.9599 | 0.8998 | -0.0601 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | CRYSTAL7 | 0.9352 | 0.8958 | -0.0394 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GRINNEL3 | 0.9272 | 0.871 | -0.0562 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 58TAP 5 | 0.9335 | 0.8992 | -0.0343 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 39 5 | 0.9495 | 0.9232 | 0.0263 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5MPLTAP | 0.9139 | 0.8704 | 0.0435 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 100DUG 5 | 0.9263 | 0.8532 | -0.0731 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | CANADAY4 | 0.9321 | 0.8884 | -0.0437 | 230 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ARMYPOS5 | 0.928 | 0.8547 | -0.0733 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 7HPW-S | 0.9683 | 0.9053 | 0.063 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEWHAL5 | 0.9346 | 0.8839 | 0.0507 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SALEM 3 | 0.9199 | 0.8809 | 0.039 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 112 5 | 0.9594 | 0.9327 | 0.0267 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GR ISLD-LNX3 | 0.8577 | 0.8335 | 0.0242 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 31 5 | 0.9498 | 0.9229 | 0.0269 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BNE HARISON5 | 0.9327 | 0.8738 | -0.0589 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 7HPW-N | 0.964 | 0.9024 | 0.0616 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | UNIONTP5 | 0.9675 | 0.9342 | 0.0333 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEWTON 5 | 0.9488 | 0.8992 | 0.0496 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | IANORTH8 | 0.9696 | 0.9432 | 0.0264 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MARION K2 7 | 0.9664 | 0.9247 | 0.0417 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | CLARKCOUNTY7 | 0.9678 | 0.9477 | 0.0201 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ANKENY 5 | 0.9277 | 0.856 | -0.0717 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LARNED3 | 0.963 | 0.943 | 0.02 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GR JCT 5 | 0.9455 | 0.9111 | 0.0344 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | CRYSTAL5 | 0.9293 | 0.8876 | -0.0417 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BRUNSWK5 | 0.9641 | 0.9293 | 0.0348 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | QUINTON3 | 0.9697 | 0.9492 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | EAU CLA5 | 0.9327 | 0.8797 | -0.053 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WINDSR 5 | 0.9524 | 0.9234 | 0.029 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | G17-030-SWYD | 0.9221 | 0.8821 | 0.04 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MUND 3 | 0.9597 | 0.9334 | 0.0263 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 49 5 | 0.9553 | 0.9277 | 0.0276 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | UTICA R5 | 0.9338 | 0.9059 | 0.0279 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NESSCTY3 | 0.9449 | 0.921 | 0.0239 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | S973 8 | 0.9565 | 0.894 | -0.0625 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STROTHR5 | >0.97 | 0.9475 | >0.0225 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BIRDCTY3 | 0.9089 | 0.8792 | 0.0297 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 58 5 | 0.9325 | 0.8982 | -0.0343 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BOONVIL3 | 0.951 | 0.8762 | -0.0748 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | S1399 5 | 0.9689 | 0.9286 | 0.0403 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COFFEY7 | >0.97 | 0.9315 | >0.0385 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | COFFEY5 | 0.9555 | 0.8995 | -0.056 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SIBLEY 5 | >0.97 | 0.9421 | >0.0279 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SIBLEY 7 | >0.97 | 0.9422 | >0.0278 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUB 92 3 | 0.9265 | 0.886 | 0.0405 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | WAVLY JC8 | >0.97 | 0.9484 | >0.0216 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BLACKHAWK 5 | 0.9641 | 0.9282 | 0.0359 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BLACKHAWK 3 | 0.9468 | 0.8986 | -0.0482 | 345 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SHELLRCK8 | 0.9695 | 0.943 | 0.0265 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5EMERSN | 0.9646 | 0.9309 | 0.0337 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ODESSA 5 | 0.9535 | 0.9188 | 0.0347 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PERRY 5 | 0.9389 | 0.8765 | -0.0624 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | JEFRSRD5 | 0.9188 | 0.8818 | 0.037 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5GEORGE | 0.9375 | 0.9067 | 0.0308 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SEDALIA5 | 0.9377 | 0.9073 | 0.0304 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TRICNTY L1 5 | 0.9679 | 0.9071 | 0.0608 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GRANGER5 | 0.9297 | 0.8584 | -0.0713 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | MONROCO5 | 0.9601 | 0.9307 | 0.0294 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SALEM L1 5 | >0.97 | 0.9367 | >0.0333 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | E CALMS5 | 0.933 | 0.9003 | 0.0327 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 7ZACKARY | 0.9592 | 0.9048 | 0.0544 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ARNOLD 5 | 0.9678 | 0.9252 | 0.0426 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB 91 5 | 0.9424 | 0.9147 | 0.0277 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BLUMILS5 | >0.97 | 0.9474 | >0.0226 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BITRSWT5 | 0.9318 | 0.8627 | -0.0691 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB 91 3 | 0.9524 | 0.9253 | 0.0271 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GODLNDT3 | 0.9118 | 0.8801 | 0.0317 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ARNOLD3 | 0.9163 | 0.8916 | 0.0247 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WYOMING5 | 0.9403 | 0.9028 | 0.0375 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GRIMES 3 | 0.9406 | 0.8645 | -0.0761 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GRIMES 5 | 0.9308 | 0.857 | -0.0738 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | BARRON 5 | 0.9255 | 0.8826 | -0.0429 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NEOSHO 7 | >0.97 | 0.9493 | >0.0207 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HOLT 7 | >0.97 | 0.9219 | >0.0481 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MIDWY2 2 | 0.9469 | 0.9066 | 0.0403 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | S968 8 | 0.969 | 0.9347 | 0.0343 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | THREE LAKES7 | 0.9301 | 0.8982 | -0.0319 | 115 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GDMEC 3 | 0.9402 | 0.8627 | -0.0775 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ALTONA 5 | 0.9312 | 0.8577 | -0.0735 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ANITA 5 | >0.97 | 0.9481 | >0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | PCI 5 | 0.938 | 0.9013 | 0.0367 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUTLIFF7 | >0.97 | 0.9322 | >0.0378 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5HARRSBRG | >0.97 | 0.9473 | >0.0227 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GLOWAT 5 | 0.9265 | 0.8537 | -0.0728 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | PRALEE 5 | >0.97 | 0.9448 | >0.0252 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MRSHLJT5 | 0.9482 | 0.9152 | 0.033 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 142ST 5 | 0.9295 | 0.8557 | -0.0738 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NSI | 0.9447 | 0.8919 | -0.0528 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PARNEL 5 | 0.9076 | 0.8538 | 0.0538 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BRKRIDG5 | >0.97 | 0.9484 | >0.0216 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MISNJCT5 | >0.97 | 0.9494 | >0.0206 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COLBY 3 | 0.9138 | 0.8821 | 0.0317 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | COLBY 2 | 0.9136 | 0.8804 | 0.0332 | 69 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LUDELL 3 | 0.9095 | 0.8824 | 0.0271 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | KETCHEM7 | >0.92 | 0.8963 | >0.0237 | 345 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | YORK 5 | 0.9514 | 0.9205 | 0.0309 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | PINE LK5 | 0.9231 | 0.8808 | -0.0423 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 43 5 | 0.9471 | 0.9198 | 0.0273 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NORTHGATE 5 | 0.9054 | 0.8606 | 0.0448 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RISING SUN 5 | 0.9305 | 0.8804 | 0.0501 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ORRICK 5 | >0.97 | 0.935 | >0.035 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BROWNCO3 | 0.9681 | 0.9395 | 0.0286 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | W LINCOLN 7 | 0.9672 | 0.9461 | 0.0211 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 17&HOLDRGE7 | 0.9658 | 0.9444 | 0.0214 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PLSNT CRNR 5 | >0.97 | 0.912 | >0.058 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GOODLND3 | 0.9116 | 0.8799 | 0.0317 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | FIRTH 7 | 0.9604 | 0.9377 | 0.0227 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WASHBRN5 | 0.9673 | 0.9312 | 0.0361 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RALSTONT8 | 0.9675 | 0.9444 | 0.0231 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | LORE 5 | 0.956 | 0.8997 | -0.0563 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | CAROLTN5 | 0.9617 | 0.9263 | 0.0354 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SWAVCAP5 | 0.9476 | 0.9151 | 0.0325 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | BEACON 5 | 0.9441 | 0.8838 | 0.0603 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5LATHROP | 0.9138 | 0.8702 | 0.0436 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | IRVINE_5 | 0.9373 | 0.8789 | 0.0584 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | LEX161 5 | 0.9531 | 0.9182 | 0.0349 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 84LEIGHTON7 | >0.97 | 0.9494 | >0.0206 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OBER T 3 | 0.949 | 0.9231 | 0.0259 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 109CLK 5 | 0.9257 | 0.8527 | -0.073 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | PLKCTY5 | 0.9284 | 0.8584 | -0.07 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | RANSOM 2 | 0.915 | 0.8908 | 0.0242 | 69 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RANSOM 3 | 0.9182 | 0.894 | 0.0242 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | REASNOR5 | 0.934 | 0.8812 | 0.0528 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5SRIVER | >0.97 | 0.9468 | >0.0232 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 17 5 | 0.9576 | 0.9299 | 0.0277 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NCU903 8 | 0.9354 | 0.902 | 0.0334 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 57&GARLAND7 | 0.9682 | 0.9471 | 0.0211 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GRAVL ISLE 5 | 0.9313 | 0.8789 | -0.0524 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SWAVRLY5 | 0.9476 | 0.9151 | 0.0325 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SENECA 5 | 0.9176 | 0.8859 | 0.0317 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | G17-030-TAP | >0.97 | 0.938 | >0.032 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DR ENG 5 | >0.97 | 0.9384 | >0.0316 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 16 WABASH 5 | 0.9249 | 0.8531 | -0.0718 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5NOVELY_SW | 0.9517 | 0.8999 | -0.0518 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5ZACKARY | 0.9612 | 0.9099 | 0.0513 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ARNOLD 3 | 0.9225 | 0.878 | 0.0445 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SEVN ML5 | 0.9146 | 0.864 | -0.0506 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SAVANNA5 | 0.9526 | 0.9193 | 0.0333 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TRAER 5 | 0.9698 | 0.9249 | 0.0449 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | REDWILO3 | 0.9555 | 0.8912 | -0.0643 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ASHAWA5 | 0.9267 | 0.854 | -0.0727 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GALENA 5 | 0.9483 | 0.9083 | 0.04 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RIVFL T7 | 0.9249 | 0.8965 | -0.0284 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ALBANY 6 | 0.9672 | 0.9444 | 0.0228 | 138 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ALBANY 5 | 0.9568 | 0.9307 | 0.0261 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HLSBORO5 | 0.8963 | 0.8687 | 0.0276 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HARMONY5 | 0.9483 | 0.9239 | 0.0244 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SCRANTN5 | 0.9485 | 0.8975 | -0.051 | 161 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | External
NRIS | 00NR | S2 | 20SP0 | N/A | IND PRK5 | 0.9577 | 0.9081 | 0.0496 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | REDCDR 5 | 0.9151 | 0.8671 | -0.048 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | S3458 3 | >0.97 | 0.948 | >0.022 | 345 | 0.95 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 91&A 7 | >0.97 | 0.949 | >0.021 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUB A 5 | 0.9294 | 0.8975 | -0.0319 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | MINGO 7 | 0.9124 | 0.8778 | 0.0346 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MINGO 3 | 0.916 | 0.8824 | 0.0336 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | QC ENRON 5 | 0.9399 | 0.912 | 0.0279 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BREWSTR3 | 0.9102 | 0.8775 | 0.0327 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SE POLK 5 | 0.9323 | 0.8577 | -0.0746 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5OSCEOL | 0.9526 | 0.9296 | 0.023 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | WAGENER 3 | 0.9692 | 0.9478 | 0.0214 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SE POLK 3 | 0.9402 | 0.8628 | -0.0774 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | COOPER 3 | >0.97 | 0.9359 | >0.0341 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HOXIE 3 | 0.912 | 0.8871 | 0.0249 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WGRAND5 | 0.9342 | 0.8605 | -0.0737 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NE 54 AVE 5 | 0.9307 | 0.8566 | -0.0741 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | APANOSE5 | 0.9599 | 0.9049 | 0.055 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUGRCRK5 | 0.9344 | 0.8607 | -0.0737 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2017-008 | 0.9196 | 0.8876 | 0.032 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NW68HOLDRG7 | 0.9692 | 0.9484 | 0.0208 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | NW68HOLDRG3 | 0.9627 | 0.9416 | 0.0211 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUB P IC 5 | 0.9059 | 0.8616 | 0.0443 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | BELLCTR5 | 0.9108 | 0.8812 | 0.0296 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SYCAMOR5 | 0.9311 | 0.8581 | -0.073 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SYCAMOR3 | 0.9359 | 0.8592 | -0.0767 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ROSEHLW5 | 0.9272 | 0.8867 | 0.0405 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S964 8 | 0.9679 | 0.8942 | -0.0737 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ADAIR 5 | >0.97 | 0.9447 | >0.0253 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ALABAMA5 | 0.9573 | 0.9064 | 0.0509 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GRANGRAE | 0.9029 | 0.869 | 0.0339 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ENRON 8 | >0.97 | 0.9484 | >0.0216 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SEDEAST5 | 0.9329 | 0.9031 | 0.0298 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MIDWAY_5 | 0.9469 | 0.9066 | 0.0403 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | TRANSFORMER | 0.9678 | 0.9477 | 0.0201 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GOVE 3 | 0.9084 | 0.8807 | 0.0277 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | HAZLTON3 | 0.9217 | 0.8802 | 0.0415 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | GU CTR 5 | 0.9585 | 0.9317 | 0.0268 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5WINSLOW | 0.9382 | 0.8917 | 0.0465 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | N TYLER3 | 0.9699 | 0.9493 | 0.0206 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2017-090 | 0.9462 | 0.9189 | 0.0273 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ROCK CK5 | 0.953 | 0.925 | 0.028 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EAST BALDWN5 | 0.9245 | 0.8824 | -0.0421 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SWAMPFX7 | 0.9686 | 0.9259 | 0.0427 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | COOPER_ESST8 | >0.97 | 0.9333 | >0.0367 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 21&N 7 | 0.9654 | 0.944 | 0.0214 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 85 5 | 0.9397 | 0.9104 | 0.0293 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 7HUGHES | 0.9602 | 0.899 | 0.0612 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ELK MND5 | 0.9407 | 0.8907 | -0.05 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WINDSOR5 | >0.97 | 0.9292 | >0.0408 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 89 5 | 0.9091 | 0.8711 | 0.038 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RAYTOWN5 | >0.97 | 0.9465 | >0.0235 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | STFRAN 3 | 0.911 | 0.8811 | 0.0299 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MLKING 5 | 0.9255 | 0.8535 | -0.072 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | GEN-2016-088 | >0.92 | 0.8963 | >0.0237 | 345 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5CLINTN | 0.9661 | 0.9383 | 0.0278 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | RIV FLS7 | 0.9108 | 0.8821 | -0.0287 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | C.CREEK4 | 0.9115 | 0.8887 | 0.0228 | 230 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SWITZER5 | >0.97 | 0.9488 | >0.0212 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DWNTWN IND5 | 0.9417 | 0.9034 | 0.0383 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ROSEHIL7 | 0.9616 | 0.9416 | 0.02 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5OSBORN | 0.9093 | 0.8619 | 0.0474 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HOLT_REACT7 | >0.97 | 0.9219 | >0.0481 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | IPSCO 3 | 0.932 | 0.8979 | 0.0341 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | IPSCO 5 | 0.9365 | 0.8998 | -0.0367 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | ECKLES-161 | >0.97 | 0.9433 | >0.0267 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WTCLF 3 | 0.9454 | 0.8993 | -0.0461 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OTTUMWA3 | 0.943 | 0.8798 | 0.0632 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 56 5 | 0.9362 | 0.8995 | -0.0367 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | G15052_T | 0.9656 | 0.9454 | 0.0202 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | PRESTO 5 | 0.932 | 0.879 | -0.053 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 100 54 5 | 0.9285 | 0.8552 | -0.0733 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | OTTUMWA5 | >0.97 | 0.9161 | >0.0539 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | JACKSON5 | 0.9333 | 0.8998 | -0.0335 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | LUCAS 5 | 0.9684 | 0.9105 | 0.0579 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | NESCTY 3 | 0.9449 | 0.921 | 0.0239 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | CSTFRAN3 | 0.9115 | 0.8816 | 0.0299 | 115 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | METRO E5 | 0.9311 | 0.8571 | -0.074 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | SW27&F 7 | 0.9679 | 0.9467 | 0.0212 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SUB Y IC 5 | 0.9035 | 0.8584 | 0.0451 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SUB17-49CAP5 | 0.9576 | 0.9299 | 0.0277 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | E CALMS7 | >0.97 | 0.9395 | >0.0305 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 8TH ST.5 | 0.9677 | 0.9237 | 0.044 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 74 5 | 0.9338 | 0.8997 | -0.0341 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | G15052_1 | 0.9656 | 0.9454 | 0.0202 | 345 | 0.95 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 103&ROKEBY3 | >0.97 | 0.9468 | >0.0232 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SCOTCTY3 | 0.9564 | 0.9364 | 0.02 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | OBERLIN3 | 0.9491 | 0.9232 | 0.0259 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ADRIAN 5 | 0.9462 | 0.9189 | 0.0273 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | W BROCK8 | 0.9612 | 0.899 | -0.0622 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WATHENA2 | >0.97 | 0.9484 | >0.0216 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RIVFLSN7 | 0.9248 | 0.8957 | -0.0291 | 115 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | S963 8 | 0.9586 | 0.8963 | -0.0623 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 5NEWARK | 0.9563 | 0.9182 | 0.0381 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S975 8 | 0.9637 | 0.8947 | -0.069 | 69 | 0.9 | 1.05 | 0.0452 | P42:345:OKGE:SB_OPKY7388 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | 2&N 7 | 0.968 | 0.9467 | 0.0213 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ENEMAHA3 | >0.97 | 0.9439 | >0.0261 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | SB 78 5 | 0.9336 | 0.8989 | -0.0347 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WILLIAMSBRG5 | 0.912 | 0.8586 | 0.0534 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | SB 71 5 | 0.932 | 0.8985 | -0.0335 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | HORIZON8 | >0.97 | 0.9496 | >0.0204 | 69 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | MANNING3 | 0.9518 | 0.931 | 0.0208 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DR NE 5 | 0.9649 | 0.9294 | 0.0355 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | G15088_1 | 0.9633 | 0.8986 | -0.0647 | 345 | 0.9 | 1.05 | 0.1106 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | RILEY 5 | >0.97 | 0.9469 | >0.0231 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | DMOINES5 | 0.9314 | 0.8568 | -0.0746 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | WESTBORO 3 | >0.97 | 0.9443 | >0.0257 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | J476 SHENHLL | >0.97 | 0.9444 | >0.0256 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TRICNTY L2 5 | 0.9679 | 0.9071 | 0.0608 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | TIFFIN 5 | 0.9087 | 0.8645 | 0.0442 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | ARBR HL 3 | >0.92 | 0.8906 | >0.0294 | 345 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | TIFFIN 3 | 0.9145 | 0.8684 | 0.0461 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 5MOCITY | 0.9668 | 0.9317 | 0.0351 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 6 ST 7 | >0.97 | 0.9316 | >0.0384 | 115 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | 4VAN N 3 | 0.9688 | 0.9483 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | VIKRD CFU 5 | >0.97 | 0.9383 | >0.0317 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | S993 8 | 0.9692 | 0.8996 | -0.0696 | 69 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | S1398 5 | 0.9662 | 0.925 | 0.0412 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | J344_COLH | 0.9377 | 0.8792 | 0.0585 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | HUMBOLT5 | 0.9624 | 0.9203 | 0.0421 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | WHT 14 5 | 0.9435 | 0.8923 | -0.0512 | 161 | 0.9 | 1.05 | 0.05961 | 105840: 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z 652304 SIOUXC19 13.8 997139 SC2 KU1A 230 1 652308 SIOUXC39 13.8 997137 SC KV1A 161 1 635200 RAUN 3 345 652564 SIOUXCY3 345 1 652564 SIOUXCY3 345 997139 SC2 KU1A 230 1 652564 SIOUXCY3 345 997138 SC2 KU1B 230 1 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 652509 FTRANDL4 230 652565 SIOUXCY4 230 1 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z 652565 SIOUXCY4 230 652567 DENISON4 230 1 652565 SIOUXCY4 230 655484 RASMUSN-ER4 230 1 652565 SIOUXCY4 230 997137 SC KV1A 161 1 652565 SIOUXCY4 230 997136 SC KV5A 161 1 635223 PLYMOTH5 161 652566 SIOUXCY5 161 1 652563 SPENCER5 161 652566 SIOUXCY5 161 1 652566 SIOUXCY5 161 997137 SC KV1A 161 1 652566 SIOUXCY5 161 997136 SC KV5A 161 1 652566 SIOUXCY5 161 652574 SIOUXCY8 69.0 1 635224 PLYMOTH8 69.0 652574 SIOUXCY8 69.0 1 652574 SIOUXCY8 69.0 659946 K216LIBE-NI8 69.0 1 652574 SIOUXCY8 69.0 659953 K412HTNM-NI8 69.0 1 652574 SIOUXCY8 69.0 659971 K301HINT-NI8 69.0 1 652574 SIOUXCY8 69.0 659980 K135CONC-NI8 69.0 1 652305 SIOUXC29 13.8 997138 SC2 KU1B 230 1 652310 SIOUXC49 13.8 997136 SC KV5A 161 1 | External
NRIS | 00NR | S2 | 20SP0 | N/A | 4VAN 3 | 0.9688 | 0.9483 | 0.0205 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | AMES 5 | 0.9411 | 0.9031 | 0.038 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EIC 5 | 0.968 | 0.9072 | 0.0608 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | EARLHAM5 | 0.9594 | 0.912 | 0.0474 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 20SP0 | N/A | FORVER 5 | 0.9338 | 0.8601 | -0.0737 | 161 | 0.9 | 1.05 | 0.07501 | P23:345:MEC:FALLOW AVE 903 | External
NRIS | 00NR | S2 | 20SP0 | N/A | NORCATR3 | 0.9588 | 0.9355 | 0.0233 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ST JOE 3 | 0.9609 | 0.9112 | 0.0497 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ALXNDR 3 | 0.9542 | 0.9319 | 0.0223 | 115 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 20SP0 | N/A | ST JOE 5 | 0.9582 | 0.9079 | 0.0503 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CHASE 3 | 0.8562 | 0.8299 | 0.0263 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WALCOTT3 | 0.911 | 0.8891 | 0.0219 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 924 | External
NRIS | 00NR | S2 | 29SP0 | N/A | HILLS-DT-RX3 | 0.8783 | 0.8459 | 0.0324 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | DIAMOND TRL3 | 0.8956 | 0.8577 | 0.0379 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 3 VANBU2 | 0.9466 | 0.9265 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | 3 VANBU2 | 0.9466 | 0.9265 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | JOHNCR 3 | 0.867 | 0.837 | 0.03 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SLMNFRK7 | 0.89 | 0.8596 | 0.0304 | 345 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | MNTZUMA3 | 0.9154 | 0.8774 | 0.038 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | TXPHSF 3 | 0.871 | 0.8405 | 0.0305 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB 93 3 | 0.9188 | 0.8951 | 0.0237 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | MAPLE J2 | 0.9478 | 0.9276 | 0.0202 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | MAPLE J2 | 0.9478 | 0.9276 | 0.0202 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | PIONEER3 | 0.9027 | 0.8825 | 0.0202 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CRLRIDG5 | 0.8791 | 0.8484 | 0.0307 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | BL.PLN.5 | >0.92 | 0.8991 | >0.0209 | 161 | 0.9 | 1.05 | 0.09073 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
NRIS | 00NR | S2 | 29SP0 | N/A | EASTOWN5 | >0.92 | 0.8986 | >0.0214 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | EASTOWN5 | >0.92 | 0.8986 | >0.0214 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WATHENA2 | 0.9503 | 0.9298 | -0.0205 | 69 | 0.93 | 1.05 | 0.08491 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-013 | 0.8891 | 0.8587 | 0.0304 | 345 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | FLETCHR3 | 0.8417 | 0.8131 | 0.0286 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | J475-J555POI | 0.9156 | 0.8776 | 0.038 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | REDWILO3 | 0.8906 | 0.8621 | 0.0285 | 345 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | ULYSPLT3 | 0.89 | 0.8667 | 0.0233 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | F MONRO2 | 0.9465 | 0.9264 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | F MONRO2 | 0.9465 | 0.9264 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | 5REX | 0.8871 | 0.8666 | 0.0205 | 161 | 0.9 | 1.05 | 0.0401 | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 5REX | 0.8871 | 0.8666 | 0.0205 | 161 | 0.9 | 1.05 | 0.0401 | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | LAMAR7 | 0.8105 | 0.7733 | 0.0372 | 345 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WILLIAM3 | 0.833 | 0.801 | 0.032 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | QUINN3 | 0.9314 | 0.8911 | -0.0403 | 345 | 0.9 | 1.05 | 0.06565 | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-052 | 0.855 | 0.8238 | 0.0312 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | AVENUECTY 5 | 0.911 | 0.8849 | 0.0261 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | TRIB SW3 | 0.8313 | 0.8009 | 0.0304 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | PALMER3 | 0.8366 | 0.8071 | 0.0295 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CARPENTER 7 | 0.9183 | 0.8981 | -0.0202 | 345 | 0.9 | 1.05 | 0.0494 | P12:345:WERE:87TH-STRA_345:: | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CARPENTER 7 | 0.9183 | 0.8981 | -0.0202 | 345 | 0.9 | 1.05 | 0.0401 | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SETAB 7 | 0.913 | 0.8892 | 0.0238 | 345 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | A16-010_SUB | 0.8441 | 0.8121 | 0.032 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | 5HICKCK | 0.9093 | 0.8753 | -0.034 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 5HICKCK | 0.9093 | 0.8753 | -0.034 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | TC-WHITING 3 | 0.8441 | 0.8121 | 0.032 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | FAIRFAX5 | >0.92 | 0.8999 | >0.0201 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | HILLS 3 | 0.8785 | 0.8462 | 0.0323 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | HILLS 5 | 0.8807 | 0.8496 | 0.0311 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | WTCLFTP3 | 0.876 | 0.8526 | 0.0234 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | J416_WF3 | 0.9344 | 0.894 | -0.0404 | 345 | 0.9 | 1.05 | 0.06565 | 82317: 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | G16-050-TAP | 0.9066 | 0.8848 | 0.0218 | 345 | 0.9 | 1.05 | 0.04415 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | DIAM TR WIND | 0.8958 | 0.8579 | 0.0379 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | LAKE RD5 | >0.92 | 0.8975 | >0.0225 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | LAKE RD5 | >0.92 | 0.8975 | >0.0225 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | EAST 5 | >0.92 | 0.8971 | >0.0229 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | EAST 5 | >0.92 | 0.8971 | >0.0229 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | E MADSN2 | 0.9467 | 0.9266 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | E MADSN2 | 0.9467 | 0.9266 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | G15_021_1 | 0.867 | 0.837 | 0.03 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SYRACUS3 | 0.8328 | 0.7994 | 0.0334 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB E IC 5 | 0.8761 | 0.845 | 0.0311 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | RIVER RUN5 | >0.92 | 0.8999 | >0.0201 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | SUB J IC 5 | 0.8804 | 0.8497 | 0.0307 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2016-050 | 0.9067 | 0.8848 | 0.0219 | 345 | 0.9 | 1.05 | 0.04415 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB U IC 5 | 0.8788 | 0.8483 | 0.0305 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | EDMOND5 | >0.92 | 0.8974 | >0.0226 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | EDMOND5 | >0.92 | 0.8974 | >0.0226 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | IC ENRON 5 | 0.8806 | 0.8496 | 0.031 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | BEARCRK3 | 0.8451 | 0.8129 | 0.0322 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | KANARAD3 | 0.8983 | 0.8781 | 0.0202 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | JOHNSON2 | 0.8692 | 0.84 | 0.0292 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | FINNEY 7 | 0.8536 | 0.824 | 0.0296 | 345 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-032 | 0.8228 | 0.787 | 0.0358 | 345 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-030 | 0.9043 | 0.8816 | 0.0227 | 345 | 0.9 | 1.05 | 0.12724 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-030 | 0.9043 | 0.8816 | 0.0227 | 345 | 0.9 | 1.05 | 0.12724 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SHARNSP3 | 0.8562 | 0.83 | 0.0262 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | GEN-2017-100 | 0.91 | 0.881 | 0.029 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | BEVERLY 3 | 0.8811 | 0.8491 | 0.032 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | G17-030-SWYD | 0.9043 | 0.8816 | 0.0227 | 345 | 0.9 | 1.05 | 0.12724 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | G17-030-SWYD | 0.9043 | 0.8816 | 0.0227 | 345 | 0.9 | 1.05 | 0.12724 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | S1399 5 | >0.97 | 0.9466 | >0.0234 | 161 | 0.95 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB 92 3 | 0.898 | 0.8702 | 0.0278 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | BLACKHAWK 3 | 0.9176 | 0.8962 | 0.0214 | 345 | 0.9 | 1.05 | 0.09073 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | External
NRIS | 00NR | S2 | 29SP0 | N/A | COOK 5 | >0.92 | 0.8985 | >0.0215 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | COOK 5 | >0.92 | 0.8985 | >0.0215 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | HUGOTON3 | 0.8748 | 0.8546 | 0.0202 | 115 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | PUCKET 3 | 0.8781 | 0.8545 | 0.0236 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | PK_GOAB3 | 0.8781 | 0.8546 | 0.0235 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | PCI 5 | >0.92 | 0.8992 | >0.0208 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | PARNEL 5 | 0.9073 | 0.8722 | 0.0351 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | COLBY 2 | 1.4332 | 1.5239 | 0.0907 | 69 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | NORTHGATE 5 | 0.8781 | 0.8473 | 0.0308 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 2ND ELM2 | 0.9474 | 0.9272 | 0.0202 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | 2ND ELM2 | 0.9474 | 0.9272 | 0.0202 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WALKMYR3 | 0.882 | 0.8612 | 0.0208 | 115 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | G17-052-TAP | 0.855 | 0.8238 | 0.0312 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | ARNOLD 3 | 0.8959 | 0.8645 | 0.0314 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | NCTYSVC2 | 0.9314 | 0.9113 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | NCTYSVC2 | 0.9314 | 0.9113 | 0.0201 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | IND PRK5 | >0.92 | 0.8979 | >0.0221 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | IND PRK5 | >0.92 | 0.8979 | >0.0221 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | MINGO 7 | 0.8891 | 0.8587 | 0.0304 | 345 | 0.9 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | TEXAS_CNTY 3 | 0.91 | 0.881 | 0.029 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB P IC 5 | 0.8789 | 0.8484 | 0.0305 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | ALABAMA5 | >0.92 | 0.899 | >0.021 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | ALABAMA5 | >0.92 | 0.899 | >0.021 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | HAZLTON3 | 0.8992 | 0.8712 | 0.028 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | WOODBIN5 | >0.92 | 0.8991 | >0.0209 | 161 | 0.9 | 1.05 | 0.12724 | 847410: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WOODBIN5 | >0.92 | 0.8991 | >0.0209 | 161 | 0.9 | 1.05 | 0.12724 | 848390: 542980 NASHUA 7 345 542982 IATAN 7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SB 89 5 | 0.891 | 0.8645 | 0.0265 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 5OSBORN | 0.8936 | 0.8731 | 0.0205 | 161 | 0.9 | 1.05 | 0.0401 | 104079: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | 5OSBORN | 0.8936 | 0.8731 | 0.0205 | 161 | 0.9 | 1.05 | 0.0401 | 92239: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 29SP0 | N/A | TRIBUNE3 | 0.8289 | 0.798 | 0.0309 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | BIG BOW 3 | 0.8771 | 0.8504 | 0.0267 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | IPSCO 3 | 0.9092 | 0.8873 | 0.0219 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 924 | External
NRIS | 00NR | S2 | 29SP0 | N/A | NEWHAL5 | 0.9625 | 0.8965 | -0.066 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | SB 56 3 | 0.9192 | 0.899 | 0.0202 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 924 | External
NRIS | 00NR | S2 | 29SP0 | N/A | LEOTI 3 | 0.8644 | 0.8403 | 0.0241 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SUB Y IC 5 | 0.8762 | 0.8451 | 0.0311 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | HARBNGR7 | 0.9183 | 0.8981 | -0.0202 | 345 | 0.9 | 1.05 | 0.0494 | P12:345:WERE:87TH-STRA_345:: | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | HARBNGR7 | 0.9183 | 0.8981 | -0.0202 | 345 | 0.9 | 1.05 | 0.0401 | 92258: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | HARBNGR3 | 0.8827 | 0.8618 | 0.0209 | 115 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | SELKIRK3 | 0.8526 | 0.8265 | 0.0261 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WILLIAMSBRG5 | 0.9133 | 0.8771 | 0.0362 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | TC-MCMURRY 3 | 0.9188 | 0.8911 | 0.0277 | 115 | 0.9 | 1.05 | 0.03728 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | BUFF_DUNES 7 | 0.8584 | 0.8287 | 0.0297 | 345 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | TIFFIN 5 | 0.8803 | 0.8492 | 0.0311 | 161 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | TIFFIN 3 | 0.8803 | 0.8481 | 0.0322 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 29SP0 | N/A | S1398 5 | >0.97 | 0.9442 | >0.0258 | 161 | 0.95 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | HUMBOLT5 | >0.97 | 0.9418 | >0.0282 | 161 | 0.95 | 1.05 | 0.07123 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CITYSVC2 | 0.9312 | 0.9112 | 0.02 | 69 | 0.93 | 1.05 | 0.0383 | 104263: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | CITYSVC2 | 0.9312 | 0.9112 | 0.02 | 69 | 0.93 | 1.05 | 0.0383 | 8608: 532771 RENO 7 345 532796 WICHITA7 345 1 532771 RENO 7 345 587884 G16-111-TAP 345 1 532771 RENO 7 345 997950 RENO TX-1 115 1 532771 RENO 7 345 997949 RENO TX-2 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | WTCLF 3 | 0.8757 | 0.8523 | 0.0234 | 115 | 0.9 | 1.05 | 0.03983 | 4009: 531419 DOBSON 3 115 531425 LOWETAP3 115 1 531425 LOWETAP3 115 531426 JAMESON3 115 1 531425 LOWETAP3 115 531435 LOWESUB3 115 1 531392 PIONTAP3 115 531393 PLYMELL3 115 1 531393 PLYMELL3 115 531408 PIERCVL3 115 1 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 531449 HOLCOMB7 345 531465 SETAB 7 345 1 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 531449 HOLCOMB7 345 997964 HOLCOMB 115 1 531379 JONES3 115 531448 HOLCOMB3 115 1 531420 FLETCHR3 115 531448 HOLCOMB3 115 1 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 531448 HOLCOMB3 115 997964 HOLCOMB 115 1 | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | G17-032-TAP | 0.8228 | 0.787 | 0.0358 | 345 | 0.9 | 1.05 | 0.03209 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | Internal
NRIS | 00NR | S2 | 29SP0 | N/A | MORGN VLLY 3 | 0.8844 | 0.8524 | 0.032 | 345 | 0.9 | 1.05 | 0.03903 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 24WP0 | N/A | TAP2 | 0.8948 | 0.8623 | 0.0325 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | LAWNRID3 | 0.9101 | 0.8786 | 0.0315 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | AXTELL 3 | 0.9134 | 0.8832 | 0.0302 | 345 | 0.9 | 1.05 | 0.0678 | P42:345:NPPD:BKR-AXT-3308 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 141 44 5 | 0.9604 | 0.9399 | 0.0205 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | WILLOW CRK 5 | 0.9566 | 0.8999 | -0.0567 | 161 | 0.9 | 1.05 | 0.03694 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | CHASE 3 | >0.92 | 0.8983 | >0.0217 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5FAIRPT | 0.9318 | 0.8602 | -0.0716 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5FAIRPT | 0.9318 | 0.8602 | -0.0716 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | S EAST 5 | 0.899 | 0.875 | 0.024 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | NASHUA 7 | >0.92 | 0.896 | >0.024 | 345 | 0.9 | 1.05 | 0.03589 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5STURGN | 0.9433 | 0.8989 | -0.0444 | 161 | 0.9 | 1.05 | 0.04941 | 104216: 542981 LACYGNE7 345 997734 LACYGNE 7 69.0 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5STURGN | 0.9433 | 0.8989 | -0.0444 | 161 | 0.9 | 1.05 | 0.04941 | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7 | External
NRIS | 00NR | S2 | 24WP0 | N/A | HILLS-DT-RX3 | 0.9331 | 0.8757 | -0.0574 | 345 | 0.9 | 1.05 | 0.04381 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | NSI TAP3 | 0.9139 | 0.883 | 0.0309 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5LATHRP | 0.9226 | 0.8601 | -0.0625 | 161 | 0.9 | 1.05 | 0.03589 | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5LATHRP | 0.9226 | 0.8601 | -0.0625 | 161 | 0.9 | 1.05 | 0.03589 | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | DIAMOND TRL3 | 0.9293 | 0.8992 | 0.0301 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | JOHNSTON 5 | 0.9597 | 0.9386 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SLMNFRK3 | 0.8816 | 0.8461 | 0.0355 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SLMNFRK7 | 0.8685 | 0.8318 | 0.0367 | 345 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | OSBORN7 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | OSBORN7 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MNTZUMA3 | 0.9322 | 0.897 | -0.0352 | 345 | 0.9 | 1.05 | 0.03795 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 24WP0 | N/A | ATWODSW3 | 0.906 | 0.877 | 0.029 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ELLIS 2 | 0.9086 | 0.8829 | 0.0257 | 69 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MARMTNE5 | 0.8679 | 0.8475 | 0.0204 | 161 | 0.93 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MARMTNE5 | 0.8679 | 0.8475 | 0.0204 | 161 | 0.93 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | DAKOTA_5 | 0.861 | 0.8367 | 0.0243 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | DAKOTA_5 | 0.861 | 0.8367 | 0.0243 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SUB 93 3 | 0.9526 | 0.9322 | 0.0204 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | LOAD | 0.8926 | 0.86 | 0.0326 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | STFRAN 3 | 0.9073 | 0.876 | 0.0313 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MARMTNW5 | 0.868 | 0.8476 | 0.0204 | 161 | 0.93 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MARMTNW5 | 0.868 | 0.8476 | 0.0204 | 161 | 0.93 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CRLRIDG5 | 0.9187 | 0.8933 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | WEST---5 | 0.8988 | 0.8749 | 0.0239 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 7ZACKARY | 0.9333 | 0.8817 | -0.0516 | 345 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | KETCHEM7 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | KETCHEM7 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHILB1 | 0.9635 | 0.8885 | -0.075 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHILB1 | 0.9635 | 0.8885 | -0.075 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | EASTOWN7 | >0.92 | 0.8732 | >0.0468 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5HINTON | 0.9597 | 0.8965 | -0.0632 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5HINTON | 0.9597 | 0.8965 | -0.0632 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MC REAC1 | >0.92 | 0.8952 | >0.0248 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MC REAC3 | >0.92 | 0.8952 | >0.0248 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MC REAC2 | >0.92 | 0.8952 | >0.0248 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5EMERSN | 0.9194 | 0.899 | 0.0204 | 161 | 0.9 | 1.05 | 0.0475 | P23:345:AMMO::MAYWOOD:2 | External
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2017-013 | 0.8676 | 0.8309 | 0.0367 | 345 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | J475-J555POI | 0.9324 | 0.8972 | -0.0352 | 345 | 0.9 | 1.05 | 0.03795 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5MEADVL | 0.8983 | 0.8503 | -0.048 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | REDWILO3 | 0.9004 | 0.8704 | 0.03 | 345 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5MOBTAP | 0.9102 | 0.8767 | 0.0335 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB T HSK 3 | 0.9411 | 0.8871 | -0.054 | 345 | 0.9 | 1.05 | 0.03323 | P12:345:MEC:WALCOTT-HILLS-LOUISA | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB T HSK 3 | 0.9411 | 0.8871 | -0.054 | 345 | 0.9 | 1.05 | 0.03323 | P22:345:MEC:SUB 92 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB T HSK 3 | 0.9411 | 0.8871 | -0.054 | 345 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:HILLS 934 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 88TH 5 | 0.9578 | 0.9364 | 0.0214 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | NATWOOD3 | 0.906 | 0.877 | 0.029 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BVERVLLY | 0.9024 | 0.8718 | 0.0306 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5ADAIR1 | 0.9161 | 0.8828 | 0.0333 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5ADAIR3 | 0.9161 | 0.8828 | 0.0333 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5ADAIR2 | 0.9161 | 0.8828 | 0.0333 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | RULETON3 | 0.9134 | 0.8818 | 0.0316 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GRNGRTP5 | 0.96 | 0.9391 | 0.0209 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | MCDONLD3 | 0.9029 | 0.8722 | 0.0307 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GRENFLD5 | 0.9593 | 0.9378 | 0.0215 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SALSBRY5 | 0.9108 | 0.8794 | 0.0314 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2016-115 | >0.92 | 0.8974 | >0.0226 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CNTRVIL5 | 0.8862 | 0.863 | 0.0232 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CNTRVIL5 | 0.8862 | 0.863 | 0.0232 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | COOK 5 | 0.9632 | 0.866 | -0.0972 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | COOK 5 | 0.9632 | 0.866 | -0.0972 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | COOK 5 | 0.9632 | 0.866 | -0.0972 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | AVENUECTY 5 | 0.93 | 0.8573 | -0.0727 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MULLNCR7 | >0.92 | 0.8952 | >0.0248 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ONEOK 3 | 0.902 | 0.8714 | 0.0306 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5REX | 0.9154 | 0.8494 | -0.066 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5REX | 0.9154 | 0.8494 | -0.066 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | LINWELD5 | 0.9605 | 0.9394 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | ROCKCK7 | >0.92 | 0.897 | >0.023 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SETAB 3 | 0.9176 | 0.891 | 0.0266 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SETAB 7 | 0.903 | 0.8736 | 0.0294 | 345 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SAVANAH2 | >0.92 | 0.8993 | >0.0207 | 69 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5NEWARK | 0.932 | 0.8857 | -0.0463 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5NEWARK | 0.932 | 0.8857 | -0.0463 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | BEELER 3 | 0.9615 | 0.898 | -0.0635 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SEGNTP 3 | 0.9014 | 0.872 | 0.0294 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5HICKCK | 0.8804 | 0.8257 | -0.0547 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5HICKCK | 0.8804 | 0.8257 | -0.0547 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MANNGT 3 | 0.9199 | 0.8943 | 0.0256 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB4 | 0.9636 | 0.8887 | -0.0749 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB4 | 0.9636 | 0.8887 | -0.0749 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5MPLTAP | 0.9198 | 0.8568 | -0.063 | 161 | 0.9 | 1.05 | 0.03589 | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5MPLTAP | 0.9198 | 0.8568 | -0.063 | 161 | 0.9 | 1.05 | 0.03589 | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB2 | 0.9635 | 0.8885 | -0.075 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB2 | 0.9635 | 0.8885 | -0.075 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB3 | 0.9635 | 0.8886 | -0.0749 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5THMHLB3 | 0.9635 | 0.8886 | -0.0749 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | DIGHTON3 | 0.9617 | 0.8974 | -0.0643 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MADISON3 | >0.97 | 0.9485 | >0.0215 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | NORWLK3 | 0.9615 | 0.8981 | -0.0634 | 345 | 0.9 | 1.05 | 0.03694 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | DELWARE5 | 0.9604 | 0.9392 | 0.0212 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | NORWLK5 | 0.9624 | 0.9414 | 0.021 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | MIAMI_ 5 | 0.8986 | 0.8747 | 0.0239 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 7FAIRPT | 0.9504 | 0.8697 | -0.0807 | 345 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7FAIRPT | 0.9504 | 0.8697 | -0.0807 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7FAIRPT | 0.9504 | 0.8697 | -0.0807 | 345 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MONOLITH 3 | 0.9179 | 0.8979 | 0.02 | 345 | 0.9 | 1.05 | 0.03331 | 104888: 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640278 SHELDON7 115 997366 MOORE T1 115 1 640277 MOORE 3 345 997366 MOORE T1 115 1 640280 MOORE 9 13.8 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | HILLS 3 | 0.9333 | 0.8761 | -0.0572 | 345 | 0.9 | 1.05 | 0.04381 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | HILLS 5 | 0.9162 | 0.8909 | 0.0253 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | LUDELLT3 | 0.9083 | 0.8797 | 0.0286 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5MOBERLY | 0.9102 | 0.8767 | 0.0335 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5HIGBEE | 0.9125 | 0.8791 | 0.0334 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | BONDRNT3 | 0.9503 | 0.8989 | -0.0514 | 345 | 0.9 | 1.05 | 0.03694 | 69833: 631078 WNTRST 5 161 635641 NORWLK5 161 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635635 MADISON3 345 635640 NORWLK3 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | WTCLFTP3 | 0.9195 | 0.8916 | 0.0279 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BONDRNT5 | 0.9629 | 0.9418 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SIB REA1 | >0.92 | 0.8771 | >0.0429 | 345 | 0.9 | 1.05 | 0.06232 | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SIB REA1 | >0.92 | 0.8771 | >0.0429 | 345 | 0.9 | 1.05 | 0.06232 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | EASTRLK5 | 0.9599 | 0.938 | 0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | G16-050-TAP | 0.9112 | 0.8806 | 0.0306 | 345 | 0.9 | 1.05 | 0.1099 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5LOCUST | 0.8735 | 0.8192 | -0.0543 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5LOCUST | 0.8735 | 0.8192 | -0.0543 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | DIAM TR WIND | 0.9295 | 0.8994 | 0.0301 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | LAKE RD5 | 0.9198 | 0.8639 | 0.0559 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | EAST 5 | 0.9182 | 0.8632 | 0.055 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | STFRANT3 | 0.9077 | 0.8764 | 0.0313 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ATWOOD 3 | 0.9005 | 0.8703 | 0.0302 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BOONVIL3 | >0.97 | 0.9494 | >0.0206 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | DIGHTNT3 | 0.9619 | 0.8977 | -0.0642 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SUB E IC 5 | 0.9165 | 0.891 | 0.0255 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | ALICERD5 | 0.9583 | 0.937 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7OVERTON | 0.9555 | 0.8979 | -0.0576 | 345 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7OVERTON | 0.9555 | 0.8979 | -0.0576 | 345 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | POWESHK5 | 0.9613 | 0.9408 | 0.0205 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB J IC 5 | 0.9196 | 0.8942 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SEGUIN 3 | 0.8976 | 0.8676 | 0.03 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2016-050 | 0.9112 | 0.8806 | 0.0306 | 345 | 0.9 | 1.05 | 0.1099 | 85491: 560062 G15088_T 345 640277 MOORE 3 345 1 640271 MCCOOL 3 345 640277 MOORE 3 345 1 640277 MOORE 3 345 640590 MONOLITH 3 345 1 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 640277 MOORE 3 345 997366 MOORE T1 115 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SUB U IC 5 | 0.919 | 0.8936 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | EDMOND5 | 0.9198 | 0.8643 | 0.0555 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | IC ENRON 5 | 0.9178 | 0.8924 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | HERNDON3 | 0.9164 | 0.8895 | 0.0269 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 60TH ST5 | 0.9606 | 0.9392 | 0.0214 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 34 NW 5 | 0.9618 | 0.9407 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | KANARAD3 | 0.9156 | 0.8855 | 0.0301 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 109CLK 5 | 0.9581 | 0.9368 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | PH RUN 3 | 0.8865 | 0.8548 | 0.0317 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2017-030 | 0.9241 | 0.8496 | -0.0745 | 345 | 0.9 | 1.05 | 0.1243 | 848401: 541256 IND PRK5 161 541401 EASTOWN5 161 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | WOODBIN5 | 0.9629 | 0.866 | -0.0969 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SHARNSP3 | >0.92 | 0.8983 | >0.0217 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GRINNEL3 | 0.8883 | 0.8572 | 0.0311 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 100DUG 5 | 0.9585 | 0.9373 | 0.0212 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | ARMYPOS5 | 0.9568 | 0.9354 | 0.0214 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7HPW-S | 0.9387 | 0.8911 | -0.0476 | 345 | 0.9 | 1.05 | 0.03795 | P23:345:MEC:SUB TIC 944 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SALEM 3 | >0.97 | 0.9483 | >0.0217 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7HPW-N | 0.9376 | 0.8874 | -0.0502 | 345 | 0.9 | 1.05 | 0.03795 | P23:345:MEC:SUB TIC 944 | External
NRIS | 00NR | S2 | 24WP0 | N/A | BRUNSWK5 | 0.9137 | 0.8841 | 0.0296 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | G17-030-SWYD | 0.9241 | 0.8496 | -0.0745 | 345 | 0.9 | 1.05 | 0.1243 | 848401: 541256 IND PRK5 161 541401 EASTOWN5 161 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BIRDCTY3 | 0.9056 | 0.8746 | 0.031 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | LUDELL 3 | 0.9083 | 0.8797 | 0.0286 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5NORTON | 0.8996 | 0.8758 | 0.0238 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SIBLEY 7 | >0.92 | 0.8771 | >0.0429 | 345 | 0.9 | 1.05 | 0.06232 | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SIBLEY 7 | >0.92 | 0.8771 | >0.0429 | 345 | 0.9 | 1.05 | 0.06232 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | NE 54 AVE 5 | 0.9616 | 0.9403 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | EASTOWN5 | 0.918 | 0.8627 | 0.0553 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ODESSA 5 | 0.9597 | 0.8988 | -0.0609 | 161 | 0.9 | 1.05 | 0.06232 | 84327: 541200 PHILL 7 345 541201 SIBLEY 7 345 1 541227 OAKGRV 5 161 541229 ODESSA 5 161 1 541226 GRAINVL5 161 541227 OAKGRV 5 161 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5GEORGE | 0.893 | 0.8724 | 0.0206 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5GEORGE | 0.893 | 0.8724 | 0.0206 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SCOTCTY3 | 0.919 | 0.8932 | 0.0258 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5HARRSBRG | 0.9195 | 0.8879 | 0.0316 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5HARRSBRG | 0.9195 | 0.8879 | 0.0316 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | GODLNDT3 | 0.9011 | 0.8679 | 0.0332 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ARNOLD3 | 0.9114 | 0.8854 | 0.026 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GRIMES 3 | 0.962 | 0.9406 | 0.0214 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | GRIMES 5 | 0.9605 | 0.9395 | 0.021 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | HOLT 7 | >0.97 | 0.9469 | >0.0231 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MIDWY2 2 | 0.9463 | 0.8975 | -0.0488 | 69 | 0.9 | 1.05 | 0.11243 | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MIDWY2 2 | 0.9463 | 0.8975 | -0.0488 | 69 | 0.9 | 1.05 | 0.11243 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GDMEC 3 | 0.955 | 0.8967 | -0.0583 | 345 | 0.9 | 1.05 | 0.03694 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5TURKEYCRK | 0.9608 | 0.9404 | 0.0204 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | ALTONA 5 | 0.9619 | 0.9406 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | GLOWAT 5 | 0.9585 | 0.9366 | 0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | MRSHLJT5 | 0.8993 | 0.8754 | 0.0239 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 142ST 5 | 0.9598 | 0.9387 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | NSI | 0.9127 | 0.8818 | 0.0309 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | PARNEL 5 | 0.9392 | 0.9159 | 0.0233 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | COLBY 3 | 0.8965 | 0.8633 | 0.0332 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | COLBY 2 | 0.9028 | 0.869 | 0.0338 | 69 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | NORTHGATE 5 | 0.9191 | 0.8936 | 0.0255 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | RISING SUN 5 | 0.9609 | 0.9394 | 0.0215 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5CHILLI | 0.8865 | 0.8389 | -0.0476 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5CHILLI | 0.8865 | 0.8389 | -0.0476 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | GOODLND3 | 0.9005 | 0.8673 | 0.0332 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CAROLTN5 | 0.9196 | 0.8918 | 0.0278 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CAROLTN5 | 0.9196 | 0.8918 | 0.0278 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BEACON 5 | >0.97 | 0.9496 | >0.0204 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5LATHROP | 0.9197 | 0.8567 | -0.063 | 161 | 0.9 | 1.05 | 0.03589 | 92249: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5LATHROP | 0.9197 | 0.8567 | -0.063 | 161 | 0.9 | 1.05 | 0.03589 | 104089: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | IRVINE_5 | 0.9691 | 0.9477 | 0.0214 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | RANSOM 2 | 0.9127 | 0.8872 | 0.0255 | 69 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | RANSOM 3 | 0.914 | 0.8886 | 0.0254 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | PRQN_WIND5 | 0.8579 | 0.8327 | 0.0252 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | PRQN_WIND5 | 0.8579 | 0.8327 | 0.0252 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 16 WABASH 5 | 0.9577 | 0.9359 | 0.0218 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB 92 3 | 0.9465 | 0.9245 | 0.022 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5NOVELY_SW | 0.9285 | 0.8803 | -0.0482 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5ZACKARY | 0.9155 | 0.8824 | 0.0331 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | ARNOLD 3 | 1.0345 | 0.9281 | 0.1064 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | POSTROCK7 | >0.97 | 0.9488 | >0.0212 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ASHAWA5 | 0.9583 | 0.9368 | 0.0215 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | IND PRK5 | 0.918 | 0.8626 | 0.0554 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MINGO 3 | 0.8813 | 0.8458 | 0.0355 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MINGO 7 | 0.8676 | 0.8309 | 0.0367 | 345 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | BREWSTR3 | 0.8929 | 0.8586 | 0.0343 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SE POLK 5 | 0.9607 | 0.9387 | 0.022 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SE POLK 3 | 0.9556 | 0.897 | -0.0586 | 345 | 0.9 | 1.05 | 0.03694 | 69834: 635635 MADISON3 345 635640 NORWLK3 345 1 635630 BOONVIL3 345 635635 MADISON3 345 1 635631 BOONVIL5 161 635631 BOONVIL5 161 635641 NORWLK5 161 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | HOXIE 3 | 0.9105 | 0.8839 | 0.0266 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | WGRAND5 | 0.9634 | 0.9421 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | APANOSE5 | 0.9429 | 0.8868 | -0.0561 | 161 | 0.9 | 1.05 | 0.04381 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUGRCRK5 | 0.9636 | 0.9423 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB P IC 5 | 0.9189 | 0.8935 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MANNING3 | 0.9191 | 0.8935 | 0.0256 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SYCAMOR5 | 0.96 | 0.9387 | 0.0213 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SYCAMOR3 | 0.9575 | 0.9353 | 0.0222 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | ALABAMA5 | 0.9663 | 0.8654 | -0.1009 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MIDWAY_5 | 0.9463 | 0.8975 | -0.0488 | 161 | 0.9 | 1.05 | 0.11243 | 104531: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MIDWAY_5 | 0.9463 | 0.8975 | -0.0488 | 161 | 0.9 | 1.05 | 0.11243 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GOVE 3 | 0.8996 | 0.8706 | 0.029 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | HAZLTON3 | 0.967 | 0.9414 | 0.0256 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5WINSLOW | 0.9424 | 0.8714 | -0.071 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5WINSLOW | 0.9424 | 0.8714 | -0.071 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 7HUGHES | 0.9351 | 0.884 | -0.0511 | 345 | 0.9 | 1.05 | 0.03795 | P23:345:MEC:SUB TIC 944 | External
NRIS | 00NR | S2 | 24WP0 | N/A | GOODCTY3 | 0.8985 | 0.8653 | 0.0332 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | SB 89 5 | 0.943 | 0.9223 | 0.0207 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5GENTRY | 0.918 | 0.8737 | 0.0443 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5GENTRY | 0.918 | 0.8737 | 0.0443 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | NEWHILLSITC3 | 0.8684 | 0.8468 | 0.0216 | 345 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:HILLS 9114 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MLKING 5 | 0.9583 | 0.9364 | 0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2016-088 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | 104515: 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | GEN-2016-088 | >0.92 | 0.8959 | >0.0241 | 345 | 0.9 | 1.05 | 0.06232 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | 5OSBORN | 0.9144 | 0.8424 | -0.072 | 161 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5OSBORN | 0.9144 | 0.8424 | -0.072 | 161 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | HOLT_REACT7 | >0.97 | 0.9469 | >0.0231 | 345 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | OTTUMWA3 | 0.9433 | 0.8994 | -0.0439 | 345 | 0.9 | 1.05 | 0.03589 | 104105: 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 100 54 5 | 0.9596 | 0.9386 | 0.021 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | NORTON-5 | 0.8997 | 0.8757 | 0.024 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | CSTFRAN3 | 0.9076 | 0.8763 | 0.0313 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | METRO E5 | 0.9611 | 0.9396 | 0.0215 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | SUB Y IC 5 | 0.9171 | 0.8917 | 0.0254 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5BUTLER | 0.8987 | 0.8783 | 0.0204 | 161 | 0.9 | 1.05 | 0.04941 | 104272: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | 5BUTLER | 0.8987 | 0.8783 | 0.0204 | 161 | 0.9 | 1.05 | 0.04941 | 94117: 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 510380 DELWARE7 345 532793 NEOSHO 7 345 1 532793 NEOSHO 7 345 542981 LACYGNE7 345 1 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 532793 NEOSHO 7 345 997909 N345 TX-2 161 1 532793 NEOSHO 7 345 997897 N345 TX-1 138 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | WILLIAMSBRG5 | 0.9427 | 0.9202 | 0.0225 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | DMOINES5 | 0.9604 | 0.9385 | 0.0219 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | TIFFIN 5 | 0.9189 | 0.8936 | 0.0253 | 161 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | TIFFIN 3 | 0.9158 | 0.8907 | 0.0251 | 345 | 0.9 | 1.05 | 0.03323 | P23:345:MEC:LOUISA 954 | External
NRIS | 00NR | S2 | 24WP0 | N/A | J344_COLH | 0.9698 | 0.9484 | 0.0214 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | WTCLF 3 | 0.9193 | 0.8913 | 0.028 | 115 | 0.9 | 1.05 | 0.05494 | 85487: 587680 GEN-2016-074 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 1 640183 GENTLMN3 345 640374 SWEET W3 345 2 640374 SWEET W3 345 653571 GR ISLD3 345 1 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | FORVER 5 | 0.9641 | 0.9423 | 0.0218 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 24WP0 | N/A | ST JOE 3 | 0.9642 | 0.8736 | -0.0906 | 345 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | ST JOE 5 | 0.9637 | 0.869 | -0.0947 | 161 | 0.9 | 1.05 | 0.1243 | 104704: 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 | Internal
NRIS | 00NR | S2 | 24WP0 | N/A | MORGN VLLY 3 | 0.9407 | 0.8999 | -0.0408 | 345 | 0.9 | 1.05 | 0.1243 | 1045300: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MORGN VLLY 3 | 0.9407 | 0.8999 | -0.0408 | 345 | 0.9 | 1.05 | 0.1243 | 848400: 541256 IND PRK5 161 541401 EASTOWN5 161 1 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24WP0 | N/A | MORGN VLLY 3 | 0.9407 | 0.8999 | -0.0408 | 345 | 0.9 | 1.05 | 0.1243 | 921960: 541400 EASTOWN7 345 997761 EASTOWNE11 161 11 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | External
NRIS | 00NR | S2 | 24SP0 | N/A | TAP2 | 0.9243 | 0.854 | -0.0703 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | LAWNRID3 | 0.9306 | 0.8597 | -0.0709 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | AXTELL 3 | 0.9335 | 0.8364 | -0.0971 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S961 8 | 0.9646 | 0.8431 | -0.1215 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | MCCOOL 3 | 0.9136 | 0.8787 | -0.0349 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | PLTSMTH8 | 0.9684 | 0.8417 | -0.1267 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1244 5 | >0.97 | 0.7531 | >0.2169 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NSI TAP3 | 0.9361 | 0.8632 | -0.0729 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GEN-2016-074 | 0.946 | 0.8581 | -0.0879 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | MCDONLD3 | 0.9213 | 0.8463 | -0.075 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | REDWILO3 | 0.9478 | 0.8795 | -0.0683 | 345 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | COOPER_602 8 | >0.92 | 0.8876 | >0.0324 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | A16-010_SUB | 0.8829 | 0.7904 | 0.0925 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1291 5 | >0.97 | 0.9471 | >0.0229 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SLMNFRK3 | 0.9351 | 0.8601 | -0.075 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SLMNFRK7 | 0.9342 | 0.8572 | -0.077 | 345 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1217 5 | >0.97 | 0.9382 | >0.0318 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S3454 3 | >0.97 | 0.9443 | >0.0257 | 345 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1345 5 | >0.97 | 0.9382 | >0.0318 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ATWODSW3 | 0.9231 | 0.8479 | -0.0752 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ELLIS 2 | 0.9215 | 0.8587 | -0.0628 | 69 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | TXPHSF 3 | >0.92 | 0.8196 | >0.1004 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GOVE 3 | 0.9236 | 0.8534 | -0.0702 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1236 5 | >0.97 | 0.9389 | >0.0311 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | RIVERDL4 | 0.9041 | 0.8397 | -0.0644 | 230 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | LOAD | 0.9222 | 0.8517 | -0.0705 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1258 5 | >0.97 | 0.8475 | >0.1225 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1201 5 | >0.97 | 0.9485 | >0.0215 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NEHAWKA8 | 0.9613 | 0.851 | -0.1103 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S3459 3 | >0.97 | 0.9309 | >0.0391 | 345 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S904 8 | >0.92 | 0.8473 | >0.0727 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | KIN MOR8 | 0.9631 | 0.8758 | -0.0873 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GEN-2017-013 | 0.9332 | 0.8562 | -0.077 | 345 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SAC629 8 | >0.92 | 0.7023 | >0.2177 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1226 5 | >0.97 | 0.9391 | >0.0309 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1263 5 | >0.97 | 0.8926 | >0.0774 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S971 8 | 0.9669 | 0.8829 | -0.084 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NATWOOD3 | 0.923 | 0.8478 | -0.0752 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | BVERVLLY | 0.9209 | 0.8457 | -0.0752 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1305 5 | >0.97 | 0.9325 | >0.0375 | 161 | 0.95 | 1.05 | 0.0655 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ASH GRV8 | 0.9663 | 0.8935 | -0.0728 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SWEET W3 | 0.9414 | 0.8535 | -0.0879 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S6874 8 | >0.92 | 0.6892 | >0.2308 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | CMRIVTP3 | 0.9609 | 0.8964 | -0.0645 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | E-PINE 3 | 0.9676 | 0.8839 | -0.0837 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | STFRAN 3 | 0.9261 | 0.8533 | -0.0728 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | RULETON3 | 0.9361 | 0.8656 | -0.0705 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | AVENUECTY 5 | 0.9401 | 0.8906 | -0.0495 | 161 | 0.9 | 1.05 | 0.12512 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | AVENUECTY 5 | 0.9401 | 0.8906 | -0.0495 | 161 | 0.9 | 1.05 | 0.12512 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | E-LIBER3 | 0.9675 | 0.8839 | -0.0836 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S6815T1&T2 8 | >0.92 | 0.6983 | >0.2217 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GR ISLD3 | 0.8883 | 0.8483 | -0.04 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ONEOK 3 | 0.9206 | 0.8453 | -0.0753 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GR ISLD4 | 0.8926 | 0.8542 | -0.0384 | 230 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | HASTING4 | 0.8967 | 0.8621 | -0.0346 | 230 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | KIN MTP8 | 0.9636 | 0.8764 | -0.0872 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S977 8 | 0.9638 | 0.8701 | -0.0937 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NC SYRA8 | >0.92 | 0.8996 | >0.0204 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S985 8 | >0.92 | 0.8475 | >0.0725 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | BEELER 3 | 0.9387 | 0.8889 | -0.0498 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | TC-MCMURRY 3 | >0.92 | 0.8716 | >0.0484 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | PAULINE3 | 0.942 | 0.8796 | -0.0624 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SEGNTP 3 | 0.9232 | 0.859 | -0.0642 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1280 5 | >0.97 | 0.9161 | >0.0539 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1229 5 | >0.97 | 0.9455 | >0.0245 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1366 5 | >0.97 | 0.7538 | >0.2162 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | TC-WHITING 3 | 0.8829 | 0.7904 | 0.0925 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | DIGHTON3 | 0.9446 | 0.8944 | -0.0502 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | LUDELLT3 | 0.9247 | 0.8497 | -0.075 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S962 8 | 0.9596 | 0.8575 | -0.1021 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | TEKAMAH5 | >0.97 | 0.9321 | >0.0379 | 161 | 0.95 | 1.05 | 0.0655 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1254 5 | >0.97 | 0.9482 | >0.0218 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NLIB 3 | 0.962 | 0.8852 | -0.0768 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S938 8 | >0.92 | 0.6856 | >0.2344 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | G16-050-TAP | 0.9404 | 0.826 | -0.1144 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S995 8 | >0.92 | 0.6904 | >0.2296 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1231 5 | >0.97 | 0.9454 | >0.0246 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1234 5 | >0.97 | 0.9429 | >0.0271 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S6866 8 | >0.92 | 0.7362 | >0.1838 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | FC1A 5 | >0.97 | 0.9362 | >0.0338 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | STFRANT3 | 0.9267 | 0.8542 | -0.0725 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ATWOOD 3 | 0.9195 | 0.8439 | -0.0756 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S982 8 | 0.9611 | 0.8797 | -0.0814 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | AUBRNT 8 | >0.92 | 0.8932 | >0.0268 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1237 5 | >0.97 | 0.9387 | >0.0313 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | DIGHTNT3 | 0.9451 | 0.8948 | -0.0503 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SUB E IC 5 | 0.9337 | 0.8979 | -0.0358 | 161 | 0.9 | 1.05 | 0.03952 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 24SP0 | N/A | SEGUIN 3 | 0.9213 | 0.8559 | -0.0654 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GEN-2016-050 | 0.9404 | 0.826 | -0.1144 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1214 5 | >0.97 | 0.9453 | >0.0247 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S3455 3 | >0.97 | 0.9438 | >0.0262 | 345 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | HERNDON3 | 0.9304 | 0.8572 | -0.0732 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | 6815TP38 | >0.92 | 0.733 | >0.187 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | AUBURN 8 | 0.9665 | 0.8871 | -0.0794 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NATBEEF3 | 0.9661 | 0.8836 | -0.0825 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1298 5 | >0.97 | 0.9329 | >0.0371 | 161 | 0.95 | 1.05 | 0.0655 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S990 8 | 0.9594 | 0.8778 | -0.0816 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | KANARAD3 | 0.9365 | 0.8621 | -0.0744 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | JOHNSON3 | 0.938 | 0.8682 | -0.0698 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | PH RUN 3 | 0.916 | 0.8476 | -0.0684 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GRINNEL3 | 0.9168 | 0.8476 | -0.0692 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GEN-2017-100 | >0.92 | 0.8599 | >0.0601 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | CANADAY4 | 0.9287 | 0.8538 | -0.0749 | 230 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1232 5 | >0.97 | 0.9415 | >0.0285 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SAC NO 8 | >0.92 | 0.7023 | >0.2177 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GR ISLD-LNX3 | 0.8885 | 0.8486 | -0.0399 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1253 5 | >0.97 | 0.9406 | >0.0294 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | MPWSPLIT | 0.9285 | 0.8952 | -0.0333 | 161 | 0.9 | 1.05 | 0.04534 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1: 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | External
NRIS | 00NR | S2 | 24SP0 | N/A | SAC623 8 | >0.92 | 0.735 | >0.185 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NESSCTY3 | 0.9382 | 0.8888 | -0.0494 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S973 8 | >0.92 | 0.8873 | >0.0327 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | BIRDCTY3 | 0.9241 | 0.8502 | -0.0739 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | LUDELL 3 | 0.9247 | 0.8497 | -0.075 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1399 5 | >0.97 | 0.9466 | >0.0234 | 161 | 0.95 | 1.05 | 0.12512 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1399 5 | >0.97 | 0.9466 | >0.0234 | 161 | 0.95 | 1.05 | 0.12512 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SHEAS LK 7 | >0.92 | 0.8696 | >0.0504 | 115 | 0.9 | 1.05 | 0.04179 | P23:345:XEL:8S81 SSL | External
NRIS | 00NR | S2 | 24SP0 | N/A | 6815TP98 | >0.92 | 0.699 | >0.221 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1249 5 | >0.97 | 0.945 | >0.025 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S900 8 | 0.9684 | 0.8957 | -0.0727 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GODLNDT3 | 0.9281 | 0.8575 | -0.0706 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | ARNOLD3 | 0.9305 | 0.866 | -0.0645 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1278 5 | >0.97 | 0.9432 | >0.0268 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1367 5 | >0.97 | 0.9394 | >0.0306 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NSI | 0.9356 | 0.8626 | -0.073 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1216 5 | >0.97 | 0.9375 | >0.0325 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1341 5 | >0.97 | 0.932 | >0.038 | 161 | 0.95 | 1.05 | 0.0655 | 82357: 645100 FC1A 5 161 646251 S1251 5 161 1 646251 S1251 5 161 646297 S1297 5 161 1 646251 S1251 5 161 646298 S1298 5 161 1 646251 S1251 5 161 646341 S1341 5 161 1 646251 S1251 5 161 997275 S3451 T3 161 1 646251 S1251 5 161 997274 S3451 T4 161 1 635200 RAUN 3 345 645451 S3451 3 345 1 645451 S3451 3 345 645454 S3454 3 345 1 645451 S3451 3 345 645459 S3459 3 345 1 645451 S3451 3 345 645001 FT CAL1G 22.0 1 645451 S3451 3 345 997275 S3451 T3 161 1 645451 S3451 3 345 997274 S3451 T4 161 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | COLBY 3 | 0.928 | 0.8565 | -0.0715 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | COLBY 2 | 0.9311 | 0.8421 | -0.089 | 69 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | 5CHILLI | 0.9186 | 0.888 | -0.0306 | 161 | 0.9 | 1.05 | 0.08453 | 104178: 541199 ST JOE 3 345 542980 NASHUA 7 345 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542980 NASHUA 7 345 542982 IATAN 7 345 1 542980 NASHUA 7 345 997746 NASHUA11 161 11 | External
NRIS | 00NR | S2 | 24SP0 | N/A | GOODLND3 | 0.928 | 0.8572 | -0.0708 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | OBER T 3 | 0.9398 | 0.8709 | -0.0689 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | RANSOM 2 | 0.9289 | 0.8668 | -0.0621 | 69 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | RANSOM 3 | 0.932 | 0.8703 | -0.0617 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NCU903 8 | 0.955 | 0.8567 | -0.0983 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1235 5 | >0.97 | 0.9416 | >0.0284 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | POSTROCK7 | >0.92 | 0.8971 | >0.0229 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1256 5 | >0.97 | 0.9429 | >0.0271 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | MINGO 3 | 0.9348 | 0.8598 | -0.075 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | MINGO 7 | 0.9332 | 0.8562 | -0.077 | 345 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | TEXAS_CNTY 3 | >0.92 | 0.8599 | >0.0601 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | BREWSTR3 | 0.9275 | 0.8542 | -0.0733 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1222 5 | >0.97 | 0.9424 | >0.0276 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1227 5 | >0.97 | 0.9412 | >0.0288 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | HOXIE 3 | 0.9245 | 0.8585 | -0.066 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GEN-2017-008 | 0.942 | 0.8796 | -0.0624 | 345 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1210 5 | >0.97 | 0.9398 | >0.0302 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | W-LIBER3 | 0.963 | 0.8859 | -0.0771 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | GOODCTY3 | 0.9237 | 0.8527 | -0.071 | 115 | 0.9 | 1.05 | 0.07184 | 85488: 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 640065 AXTELL 3 345 640312 PAULINE3 345 1 640065 AXTELL 3 345 640374 SWEET W3 345 1 640065 AXTELL 3 345 997464 AXTELL T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | C.CREEK4 | 0.9298 | 0.8554 | -0.0744 | 230 | 0.9 | 1.05 | 0.04946 | 104846: 530583 POSTROCK7 345 640325 REDWILO3 345 1 531451 MINGO 7 345 640325 REDWILO3 345 1 640183 GENTLMN3 345 640325 REDWILO3 345 1 640252 KEYSTON3 345 640325 REDWILO3 345 1 640325 REDWILO3 345 997340 RD.WILLOW T1 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S994 8 | >0.92 | 0.7102 | >0.2098 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SAC SO 8 | >0.92 | 0.735 | >0.185 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | HAYNE3 | 0.9562 | 0.8902 | -0.066 | 115 | 0.9 | 1.05 | 0.03972 | 93167: 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 2 523090 TEXAS_CNTY 3 115 523093 HITCHLAND 3 115 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NESCTY 3 | 0.9383 | 0.8888 | -0.0495 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | PR BRZ 4 | 1.0397 | 1.0599 | 0.0202 | 230 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | CSTFRAN3 | 0.9266 | 0.8541 | -0.0725 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | SUB Y IC 5 | 0.9338 | 0.8982 | -0.0356 | 161 | 0.9 | 1.05 | 0.03952 | P23:345:MEC:LOUISA 964 | External
NRIS | 00NR | S2 | 24SP0 | N/A | S972 8 | 0.9594 | 0.8817 | -0.0777 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | OBERLIN3 | 0.9399 | 0.8711 | -0.0688 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | W BROCK8 | >0.92 | 0.8919 | >0.0281 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1297 5 | >0.97 | 0.9452 | >0.0248 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S963 8 | >0.92 | 0.8896 | >0.0304 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | 990TP 8 | 0.9612 | 0.8797 | -0.0815 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S3451 3 | >0.97 | 0.9368 | >0.0332 | 345 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S6815T3 8 | >0.92 | 0.7309 | >0.1891 | 69 | 0.9 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1221 5 | >0.97 | 0.9455 | >0.0245 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1398 5 | >0.97 | 0.9456 | >0.0244 | 161 | 0.95 | 1.05 | 0.12512 | 104523: 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1398 5 | >0.97 | 0.9456 | >0.0244 | 161 | 0.95 | 1.05 | 0.12512 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | HUMBOLT5 | >0.97 | 0.9262 | >0.0438 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | S1233 5 | >0.97 | 0.9458 | >0.0242 | 161 | 0.95 | 1.05 | 0.16575 | 82358: 635000 CBLUFFS3 345 645456 S3456 3 345 1 645455 S3455 3 345 645456 S3456 3 345 1 645456 S3456 3 345 645458 S3458 3 345 1 645456 S3456 3 345 645459 S3459 3 345 1 645456 S3456 3 345 997270 S3456 T4 161 1 647006 S906 N 8 69.0 647017 6815TP98 69.0 1 647006 S906 N 8 69.0 647079 979TP 8 69.0 1 647006 S906 N 8 69.0 647916 S916 8 69.0 1 647006 S906 N 8 69.0 647928 S928 8 69.0 1 647006 S906 N 8 69.0 647938 S938 8 69.0 1 647006 S906 N 8 69.0 645031 SARPY 1G 13.8 1 647006 S906 N 8 69.0 997265 S1206 T2 69.0 1 635001 CBLUFFS5 161 646206 S1206 5 161 1 646201 S1201 5 161 646206 S1206 5 161 1 646206 S1206 5 161 646216 S1216 5 161 1 646206 S1206 5 161 646232 S1232 5 161 1 646206 S1206 5 161 646244 S1244 5 161 1 646206 S1206 5 161 645033 SARPY 3G 13.8 1 646206 S1206 5 161 997270 S3456 T4 161 1 646206 S1206 5 161 997266 S1206 T1 69.0 1 646206 S1206 5 161 997265 S1206 T2 69.0 1 646206 S1206 5 161 997264 SARPY4&5 GSU 13.8 1 647016 6815TP38 69.0 647906 S906 S 8 69.0 1 647904 S904 8 69.0 647906 S906 S 8 69.0 1 647906 S906 S 8 69.0 647924 S924 8 69.0 1 647906 S906 S 8 69.0 647938 S938 8 69.0 1 647906 S906 S 8 69.0 645032 SARPY 2G 13.8 1 647906 S906 S 8 69.0 997266 S1206 T1 69.0 1 | Internal
NRIS | 00NR | S2 | 24SP0 | N/A | NORCATR3 | 0.9506 | 0.8889 | -0.0617 | 115 | 0.9 | 1.05 | 0.04462 | P23:345:SUNC:SB_BRK482 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | GEN-2016-115 | >0.92 | 0.8922 | >0.0278 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | MULLNCR7 | 0.9054 | 0.874 | 0.0314 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | HOLT 7 | >0.92 | 0.8958 | >0.0242 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | OSBORN7 | 0.893 | 0.8622 | 0.0308 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | GEN-2016-088 | 0.893 | 0.8622 | 0.0308 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | MC REAC1 | 0.9054 | 0.874 | 0.0314 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | HOLT_REACT7 | >0.92 | 0.8958 | >0.0242 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | MC REAC3 | 0.9054 | 0.874 | 0.0314 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | MC REAC2 | 0.9054 | 0.874 | 0.0314 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | KETCHEM7 | 0.893 | 0.8622 | 0.0308 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 09NR | S2 | 24L0 | N/A | ROCKCK7 | >0.92 | 0.8918 | >0.0282 | 345 | 0.9 | 1.05 | 0.09456 | 85498: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 300076 5FAIRPT 161 300039 7FAIRPT 345 3 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR2 3 | >0.97 | 0.9058 | >0.0642 | 345 | 0.95 | 1.05 | 0.0535 | P45:345:UMZW:# 1328 #: GI IN NE. | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR2 3 | >0.97 | 0.9058 | >0.0642 | 345 | 0.95 | 1.05 | 0.0535 | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR2 3 | >0.97 | 0.9058 | >0.0642 | 345 | 0.95 | 1.05 | 0.0535 | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5FAIRPT | 0.9486 | 0.9251 | 0.0235 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | AVENUECTY 5 | 0.9423 | 0.8939 | -0.0484 | 161 | 0.9 | 1.05 | 0.07224 | 104521: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | AVENUECTY 5 | 0.9423 | 0.8939 | -0.0484 | 161 | 0.9 | 1.05 | 0.12776 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | AVENUECTY 5 | 0.9423 | 0.8939 | -0.0484 | 161 | 0.9 | 1.05 | 0.12776 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR1 3 | >0.97 | 0.9052 | >0.0648 | 345 | 0.95 | 1.05 | 0.0535 | P45:345:UMZW:# 1328 #: GI IN NE. | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR1 3 | >0.97 | 0.9052 | >0.0648 | 345 | 0.95 | 1.05 | 0.0535 | 85489: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GRPR1 3 | >0.97 | 0.9052 | >0.0648 | 345 | 0.95 | 1.05 | 0.0535 | 106475: 640271 MCCOOL 3 345 653571 GR ISLD3 345 1 640374 SWEET W3 345 653571 GR ISLD3 345 1 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z 653571 GR ISLD3 345 997403 GI KU3A 230 3 653571 GR ISLD3 345 997132 GI KU1A 230 1 653571 GR ISLD3 345 997131 GI KU1B 230 2 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | NEWPORT5 | 0.9634 | 0.9393 | 0.0241 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | GEN-2017-030 | 0.9045 | 0.8647 | 0.0398 | 345 | 0.9 | 1.05 | 0.12776 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | GEN-2017-030 | 0.9045 | 0.8647 | 0.0398 | 345 | 0.9 | 1.05 | 0.12776 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | DENMARK5 | 0.9404 | 0.8784 | -0.062 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAMOND TRL3 | 0.9589 | 0.8878 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P23:345:MEC:MONTEZUMA 902 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAMOND TRL3 | 0.9589 | 0.8878 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAMOND TRL3 | 0.9589 | 0.8878 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAMOND TRL3 | 0.9589 | 0.8878 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAMOND TRL3 | 0.9589 | 0.8878 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External
NRIS | 00NR | S2 | 19WP0 | N/A | APANOSE5 | 0.9652 | 0.9451 | 0.0201 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | MNTZUMA3 | 0.9626 | 0.9398 | 0.0228 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | WEVER5 | 0.9303 | 0.8633 | -0.067 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5HICKCK | 0.8987 | 0.8671 | -0.0316 | 161 | 0.9 | 1.05 | 0.03879 | P23:345:MEC:SYCAMORE 905 | External
NRIS | 00NR | S2 | 19WP0 | N/A | MPWSPLIT | 0.9535 | 0.8958 | -0.0577 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | BRLGTN 5 | 0.9315 | 0.8606 | -0.0709 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 87TH 7 | >0.97 | 0.9472 | >0.0228 | 345 | 0.95 | 1.05 | 0.03761 | 104092: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 87TH 7 | >0.97 | 0.9472 | >0.0228 | 345 | 0.95 | 1.05 | 0.03761 | 92252: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5MPLTAP | 0.9304 | 0.8746 | -0.0558 | 161 | 0.9 | 1.05 | 0.03761 | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5MPLTAP | 0.9304 | 0.8746 | -0.0558 | 161 | 0.9 | 1.05 | 0.03761 | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5WINSLOW | 0.9591 | 0.9358 | 0.0233 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | G17-030-SWYD | 0.9045 | 0.8647 | 0.0398 | 345 | 0.9 | 1.05 | 0.12776 | 847411: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | G17-030-SWYD | 0.9045 | 0.8647 | 0.0398 | 345 | 0.9 | 1.05 | 0.12776 | 848391: 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | EDWARVL3 | 0.957 | 0.9218 | -0.0352 | 115 | 0.93 | 1.05 | 0.03761 | 92252: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | EDWARVL3 | 0.957 | 0.9218 | -0.0352 | 115 | 0.93 | 1.05 | 0.03761 | 104092: 543080 HAWTH 2 69.0 543114 PLUMRRD2 69.0 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 7FAIRPT | 0.966 | 0.9416 | 0.0244 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | S1398 5 | >0.97 | 0.9492 | >0.0208 | 161 | 0.95 | 1.05 | 0.09141 | P23:345:MEC:GDMEC 901 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | S1398 5 | >0.97 | 0.9492 | >0.0208 | 161 | 0.95 | 1.05 | 0.09141 | P23:345:MEC:GDMEC 902 | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5GENTRY | 0.9487 | 0.9276 | 0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | HENRYCO5 | 0.9342 | 0.8865 | -0.0477 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | COOK 5 | >0.97 | 0.9497 | >0.0203 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5OSBORN | 0.9278 | 0.8768 | -0.051 | 161 | 0.9 | 1.05 | 0.03761 | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5OSBORN | 0.9278 | 0.8768 | -0.051 | 161 | 0.9 | 1.05 | 0.03761 | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAM TR WIND | 0.9591 | 0.888 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P23:345:MEC:MONTEZUMA 902 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAM TR WIND | 0.9591 | 0.888 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P12:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAM TR WIND | 0.9591 | 0.888 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1: 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAM TR WIND | 0.9591 | 0.888 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P21:345:ALTW-MEC:AUTO-SINGLE:OTTUMWA3:MNTZUMA3:1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | DIAM TR WIND | 0.9591 | 0.888 | -0.0711 | 345 | 0.9 | 1.05 | 0.04189 | P23:345:ALTW:PD:OTTUMWA:LN:FK14302 | External
NRIS | 00NR | S2 | 19WP0 | N/A | J475-J555POI | 0.9628 | 0.94 | 0.0228 | 345 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | LAKE RD5 | >0.97 | 0.9496 | >0.0204 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5MEADVL | 0.9197 | 0.8985 | -0.0212 | 161 | 0.9 | 1.05 | 0.04082 | 104260: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5MEADVL | 0.9197 | 0.8985 | -0.0212 | 161 | 0.9 | 1.05 | 0.04082 | 8601: 532768 EMPEC 7 345 532769 LANG 7 345 1 532768 EMPEC 7 345 532770 MORRIS 7 345 1 532768 EMPEC 7 345 532774 SWISVAL7 345 1 532768 EMPEC 7 345 562476 G14_001T 345 1 532768 EMPEC 7 345 585100 GEN-2015-073 345 1 532768 EMPEC 7 345 532740 EMPEC121 13.8 1 532768 EMPEC 7 345 532741 EMPEC341 13.8 1 532768 EMPEC 7 345 532742 EMPEC5 1 18.0 1 532768 EMPEC 7 345 532743 EMPEC6 1 18.0 1 532768 EMPEC 7 345 532744 EMPEC7 1 18.0 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5CARBID T | 0.967 | 0.9431 | 0.0239 | 161 | 0.95 | 1.05 | N/A | Base Case | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5LATHRP | 0.9328 | 0.8772 | -0.0556 | 161 | 0.9 | 1.05 | 0.03761 | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5LATHRP | 0.9328 | 0.8772 | -0.0556 | 161 | 0.9 | 1.05 | 0.03761 | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5REX | 0.9271 | 0.8717 | -0.0554 | 161 | 0.9 | 1.05 | 0.03761 | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5REX | 0.9271 | 0.8717 | -0.0554 | 161 | 0.9 | 1.05 | 0.03761 | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | VIELE 5 | 0.9534 | 0.8937 | -0.0597 | 161 | 0.9 | 1.05 | 0.03384 | P23:345:MEC:WALCOTT 914 | External
NRIS | 00NR | S2 | 19WP0 | N/A | EDMOND5 | >0.97 | 0.9489 | >0.0211 | 161 | 0.95 | 1.05 | N/A | Base Case | Internal
NRIS | 00NR | S2 | 19WP0 | N/A | 5LATHROP | 0.9303 | 0.8744 | -0.0559 | 161 | 0.9 | 1.05 | 0.03761 | 104087: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 00NR | S2 | 19WP0 | N/A | 5LATHROP | 0.9303 | 0.8744 | -0.0559 | 161 | 0.9 | 1.05 | 0.03761 | 92247: 542973 HAWTHS5 161 543020 BRMGHAM5 161 1 542972 HAWTH 7 345 542980 NASHUA 7 345 1 542976 LEVEE 5 161 543666 NEASTN5 161 1 543027 RANDLPH5 161 543665 HAWTHN5 161 1 | External
NRIS | 09NR | S2 | 20G0 | N/A | MAGELLN8 | >0.92 | 0.8995 | >0.0205 | 69 | 0.9 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | GEN-2017-030 | 0.9097 | 0.8824 | 0.0273 | 345 | 0.9 | 1.05 | 0.1307 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | KETCHEM7 | 0.918 | 0.8884 | 0.0296 | 345 | 0.9 | 1.05 | 0.12624 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | KETCHEM7 | 0.918 | 0.8884 | 0.0296 | 345 | 0.9 | 1.05 | 0.12624 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | S1280 5 | 0.9562 | 0.9347 | 0.0215 | 161 | 0.95 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | G17-030-SWYD | 0.9097 | 0.8824 | 0.0273 | 345 | 0.9 | 1.05 | 0.1307 | 84355: 532772 STRANGR7 345 542982 IATAN 7 345 1 532772 STRANGR7 345 542982 IATAN 7 345 2 542980 NASHUA 7 345 542982 IATAN 7 345 1 542982 IATAN 7 345 588736 G17-030-TAP 345 1 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 542982 IATAN 7 345 997745 IATAN11 161 11 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | S1399 5 | 0.9625 | 0.9402 | 0.0223 | 161 | 0.95 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | HUMBOLT5 | 0.9516 | 0.9294 | 0.0222 | 161 | 0.95 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | OSBORN7 | 0.918 | 0.8885 | 0.0295 | 345 | 0.9 | 1.05 | 0.12624 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | OSBORN7 | 0.918 | 0.8885 | 0.0295 | 345 | 0.9 | 1.05 | 0.12624 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | GEN-2016-088 | 0.918 | 0.8884 | 0.0296 | 345 | 0.9 | 1.05 | 0.12624 | 84315: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | GEN-2016-088 | 0.918 | 0.8884 | 0.0296 | 345 | 0.9 | 1.05 | 0.12624 | 104708: 300039 7FAIRPT 345 541199 ST JOE 3 345 1 541199 ST JOE 3 345 541400 EASTOWN7 345 1 541199 ST JOE 3 345 542980 NASHUA 7 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 997780 ST. JOSEPH22 161 22 541199 ST JOE 3 345 997779 ST. JOSEPH33 161 33 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | S1398 5 | 0.9586 | 0.9362 | 0.0224 | 161 | 0.95 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal
NRIS | 09NR | S2 | 20G0 | N/A | S993 8 | 0.9165 | 0.8922 | 0.0243 | 69 | 0.9 | 1.05 | 0.15792 | 85492: 640009 COOPER1G 22.0 to 640140 COOPER 5 161 300039 7FAIRPT 345 640139 COOPER 3 345 1 541199 ST JOE 3 345 640139 COOPER 3 345 1 635017 ATCHSN 3 345 640139 COOPER 3 345 1 640139 COOPER 3 345 640590 MONOLITH 3 345 1 640139 COOPER 3 345 645458 S3458 3 345 1 640139 COOPER 3 345 640009 COOPER1G 22.0 1 640139 COOPER 3 345 997431 COOPER T2 161 1 640139 COOPER 3 345 997430 COOPER T5 161 1 | Internal

## Stability Analysis
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2
9 | 19W | Base | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_1_P1_COOPER3 | Apply 3-phase fault on ST JOE 3 to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_2_P1_COOPER3 | Apply 3-phase fault on 7FAIRPT to COOPER 3 345kV transmission line CKT 1, near COOPER 3 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.24pu, MaxDur: 0.04s
9 | 21L | Base | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_3_P1_S3451 | Apply 3-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_4_P1_S3451 | Apply 3-phase fault on S3451 to S3454 345kV transmission line CKT 1, near S3451 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - J416_GEN1[1] J416_GEN2[2] J416_GEN1[2] J416_GEN2[1] FRMR CTY W1[W ] NEWHRVST W[W ] | Voltage Spike: 13.57pu, MaxDur: 0.05s
9 | 21L | Base | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 19.64pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_5_P1_S3456 | Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.12pu | Yes | No - G10-051-GEN1[1 ] G15-007-GEN1[1] G10-051-GEN3[1 ] FRMR CTY W1[W ] G15-089-GEN1[1] G11-027-GEN3[1 ] G11-027-GEN2[1 ] G11-027-GEN1[1 ] NEWHRVST W[W ] G10-051-GEN2[1 ] | Voltage Spike: 21.73pu, MaxDur: 0.07s
9 | 21L | Sensitivity | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_6_P1_S3456 | Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_7_P1_S3456 | Apply 3-phase fault on S3456 345kV/161kV/13.8kV transformer CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_8_P1_S3456 | Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] ROCKCK_G1_1[W1] ROCKCK_G2_1[W2] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. ROCKCK G1 & G2: It was observed that these units tripped due to action of over-voltage protecion. The simulation was reran with protection of these units disabled and no stability issues was observed.
9 | 19W | Sensitivity | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] ROCKCK_G1_1[W1] ROCKCK_G2_1[W2] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. ROCKCK G1 & G2: It was observed that these units tripped due to action of over-voltage protecion. The simulation was reran with protection of these units disabled and no stability issues was observed.
9 | 21S | Sensitivity | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_9_P1_S3458 | Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] ROCKCK_G1_1[W1] ROCKCK_G2_1[W2] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. ROCKCK G1 & G2: It was observed that these units tripped due to action of over-voltage protecion. The simulation was reran with protection of these units disabled and no stability issues was observed.
9 | 21L | Base | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_10_P1_S3458 | Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_11_P1_S3459 | Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_12_P1_S1209 | Apply 3-phase fault on S1209 161kV/69kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_13_P1_S1209 | Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_14_P1_S1209 | Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_15_P1_S1209 | Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_16_P1_S1226 | Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_17_P1_S1226 | Apply 3-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_18_P1_S1231 | Apply 3-phase fault on S1231 to S1235 161kV transmission line CKT 1, near S1231 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_19_P1_S1231 | Apply 3-phase fault on S1227 to S1231 161kV transmission line CKT 1, near S1231 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1217 to S1227 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1217 to S1227 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1217 to S1227 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_20_P1_S1250 | Apply 3-phase fault on S1250 to S1297 161kV transmission line CKT 1, near S1250 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1251 to S1297 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1251 to S1297 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1251 to S1297 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_21_P1_S1254 | Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1253 to S1256 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1253 to S1256 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1253 to S1256 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_22_P1_S1254 | Apply 3-phase fault on S3454 345kV/161kV/13.8kV transformer CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_23_P1_S1255 | Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_24_P1_S1260 | Apply 3-phase fault on S1259 to S1260 161kV transmission line CKT 1, near S1260 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_25_P1_S1281 | Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_26_P1_S1281 | Apply 3-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1214 to S1287 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1214 to S1287 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_27_P1_S1347 | Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_28_P1_S1347 | Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_29_P1_S1361 | Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_30_P1_S1361 | Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_31_P1_S1362 | Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_32_P1_S1362 | Apply 3-phase fault on S1361 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_33_P1_S1363 | Apply 3-phase fault on S1362 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_34_P1_S1363 | Apply 3-phase fault on S1281 to S1363 161kV transmission line CKT 1, near S1363 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21S | Base | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_35_P4_S3451 | Apply single-phase fault on RAUN to S3451 345kV transmission line CKT 1, near S3451 345kV for 16 cycles with stuck breaker at S3451. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_36_P4_S3454 | Apply single-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 16 cycles with stuck breaker at S3454. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3454 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_37_P4_S3455 | Apply single-phase fault on S3455 to S3761 345kV transmission line CKT 1, near S3455 345kV for 16 cycles with stuck breaker at S3455. Open the faulted Transmission Circuit. Simultaneously open S3454 to S3455 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_38_P4_S3456 | Apply single-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 16 cycles with stuck breaker at S3456. Open the faulted Transmission Circuit. Simultaneously open S3456 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Transfer | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_39_P4_S3458 | Apply single-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Transfer | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_40_P4_S3458 | Apply single-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 16 cycles with stuck breaker at S3458. Open the faulted Transmission Circuit. Simultaneously open HOLT to S3458 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_41_P4_S3459 | Apply single-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 16 cycles with stuck breaker at S3459. Open the faulted Transmission Circuit. Simultaneously open S3451 to S3459 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_42_P4_S1209 | Apply single-phase fault on S1209 to S1250 161kV transmission line CKT 2, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1250 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_43_P4_S1209 | Apply single-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Three Winding. Simultaneously open S3459 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_44_P4_S1209 | Apply single-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 16 cycles with stuck breaker at S1209. Open the faulted Transmission Circuit. Simultaneously open S1209 to S1231 161kV transmission line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21S | Base | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_45_P4_S1226 | Apply single-phase fault on S1226 to S1291 161kV transmission line CKT 1, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1237 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21S | Base | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_46_P4_S1226 | Apply single-phase fault on S1226 to S1298 161kV transmission line CKT 2, near S1226 161kV for 16 cycles with stuck breaker at S1226. Open the faulted Transmission Circuit. Simultaneously open S1226 to S1298 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21S | Base | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_47_P4_S1254 | Apply single-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 16 cycles with stuck breaker at S1254. Open the faulted Transmission Circuit. Simultaneously open S3454 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_48_P4_S1255 | Apply single-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 16 cycles with stuck breaker at S1255. Open the faulted Three Winding. Simultaneously open S3455 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21S | Base | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_49_P4_S1281 | Apply single-phase fault on S1281 to S1287 161kV transmission line CKT 1, near S1281 161kV for 16 cycles with stuck breaker at S1281. Open the faulted Transmission Circuit. Simultaneously open S1214 to S1287 161kV transmission line CKT 1.Simultaneously open S1254 to S1281 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_50_P4_S1361 | Apply single-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 16 cycles with stuck breaker at S1361. Open the faulted Transmission Circuit. Simultaneously open S3761 345kV/161kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_51_P4_S1362 | Apply single-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 16 cycles with stuck breaker at S1362. Open the faulted Transmission Circuit. Simultaneously open S1361 to S1362 161kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_52_P6_S3454 | Prior Outage of RAUN to S3451 345kV transmission line CKT 1Apply 3-phase fault on S3454 to WAGENER 345kV transmission line CKT 1, near S3454 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.28pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Transfer | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_53_P6_S3456 | Prior Outage of COOPER 3 to S3458 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.05s
9 | 21L | Sensitivity | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_54_P6_S3456 | Prior Outage of S3455 to S3456 345kV transmission line CKT 1Apply 3-phase fault on CBLUFFS3 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_55_P6_S3456 | Prior Outage of CBLUFFS3 to S3456 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3458 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - G573 G1[1 ] FRMR CTY W1[W ] POCHPRAIRIEW[W ] G947_GEN[1 ] G573 G2[1 ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. G573 G1[1 ], POCHPRAIRIEW[W ], G947_GEN[1 ] & G573 G2[1 ]: It was observed that these units tripped under this contingency. The simulation was reran with protection of these units disabled and no stability issues was observed. Voltage Spike: 1.27pu, MaxDur: 0.06s
9 | 21L | Sensitivity | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_56_P6_S3456 | Prior Outage of S3456 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 to S3456 345kV transmission line CKT 1, near S3456 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] ROCKCK_G1_1[W1] ROCKCK_G2_1[W2] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. ROCKCK G1 & G2: It was observed that these units tripped due to action of over-voltage protecion. The simulation was reran with protection of these units disabled and no stability issues was observed.
9 | 21L | Base | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | No - MaxV: 1.25pu, MaxDur: 10.21s | No - Min: 0.82pu | No - Max: 1.10pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] ROCKCK_G1_1[W1] ROCKCK_G2_1[W2] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. ROCKCK G1 & G2: It was observed that these units tripped due to action of over-voltage protecion. The simulation was reran with protection of these units disabled and no stability issues was observed.
9 | 21S | Sensitivity | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_57_P6_S3458 | Prior Outage of ST JOE 3 to COOPER 3 345kV transmission line CKT 1Apply 3-phase fault on HOLT to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_58_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on S3458 to 103&ROKEBY3 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Sensitivity | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Transfer | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Sensitivity | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Transfer | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Base | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Sensitivity | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21S | Transfer | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Base | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Sensitivity | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 28S | Transfer | FLT_59_P6_S3458 | Prior Outage of HOLT to S3458 345kV transmission line CKT 1Apply 3-phase fault on COOPER 3 to S3458 345kV transmission line CKT 1, near S3458 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 19W | Base | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken. Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Base | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_60_P6_S3459 | Prior Outage of S3451 to S3459 345kV transmission line CKT 1Apply 3-phase fault on S3456 to S3459 345kV transmission line CKT 1, near S3459 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_61_P6_S1209 | Prior Outage of S3459 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3459 345kV/161kV/13.8kV transformer CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_62_P6_S1209 | Prior Outage of S1209 to S1231 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1231 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
9 | 21L | Sensitivity | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_63_P6_S1209 | Prior Outage of S1209 to S1250 161kV transmission line CKT 2Apply 3-phase fault on S1209 to S1250 161kV transmission line CKT 1, near S1209 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_64_P6_S1226 | Prior Outage of S1226 to S1291 161kV transmission line CKT 1Apply 3-phase fault on S1226 to S1237 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_65_P6_S1226 | Prior Outage of S1226 to S1298 161kV transmission line CKT 2Apply 3-phase fault on S1226 to S1298 161kV transmission line CKT 1, near S1226 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_66_P6_S1254 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1249 to S1254 161kV transmission line CKT 1, near S1254 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No - FRMR CTY W1[W ] | FRMR CTY W1[W ]: This unit tripped under several contingnecies in the BC, TC and SC cases. Due to its dispatched MW and location (MEC), no further action was taken.
9 | 21L | Base | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_67_P6_S1255 | Prior Outage of S3455 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3455 345kV/161kV/13.8kV transformer CKT 1, near S1255 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_68_P6_S1281 | Prior Outage of S1281 to S1287 161kV transmission line CKT 1Prior Outage of S1214 to S1287 161kV transmission line CKT 1Apply 3-phase fault on S1254 to S1281 161kV transmission line CKT 1, near S1281 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_69_P6_S1347 | Prior Outage of S1226 to S1237 161kV transmission line CKT 1Apply 3-phase fault on S1209 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_70_P6_S1347 | Prior Outage of S1209 to S1231 161kV transmission line CKT 1Apply 3-phase fault on S1252 to S1347 161kV transmission line CKT 1, near S1347 161kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S1226 to S1252 161kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S1226 to S1252 161kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S1226 to S1252 161kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_71_P6_S1361 | Prior Outage of S3761 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S1255 to S1361 161kV transmission line CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_72_P6_S1361 | Prior Outage of S3454 345kV/161kV/13.8kV transformer CKT 1Apply 3-phase fault on S3761 345kV/161kV/13.8kV transformer CKT 1, near S1361 161kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Base | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Transfer | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Base | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.11pu | Yes | Yes
9 | 21L | Sensitivity | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21L | Transfer | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No - Max: 1.10pu | Yes | Yes
9 | 21S | Base | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Transfer | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Base | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Transfer | FLT_73_P6_S1362 | Prior Outage of S1361 to S1362 161kV transmission line CKT 1Apply 3-phase fault on S1260 to S1362 161kV transmission line CKT 1, near S1362 161kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Note on C1: • Base: Starting model + include/exclude projects identified in the SOW – without Group 9 interim requests) • Transfer: Base + Group 9 interim requests dispatched at 100% • Sensitivity: Transfer + nearby SC generators dispatched at 100% (the list of these units are provided in sensitivity Tap). The purpose is to evaluate the impact of the interim requests on these units.

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
GEN-2020-043 & GEN-2020-044 & GEN-2020-045 | 999901 - 999903 | Bus: 645031 ID: 1 Name: SARPY 1G | 09 - Nebraska | ALL | 55.4
GEN-2020-043 & GEN-2020-044 & GEN-2020-045 | 999901 - 999903 | Bus: 645032 ID: 2 Name: SARPY 2G | 09 - Nebraska | ALL | 56.5
GEN-2020-043 & GEN-2020-044 & GEN-2020-045 | 999901 - 999903 | Bus: 645033 ID: 3 Name: SARPY 3G | 09 - Nebraska | ALL | 108.2
GEN-2020-043 & GEN-2020-044 & GEN-2020-045 | 999901 - 999903 | Bus: 645034 ID: 4 Name: SARPY 4G | 09 - Nebraska | ALL | 49.6
GEN-2020-043 & GEN-2020-044 & GEN-2020-045 | 999901 - 999903 | Bus: 645035 ID: 5 Name: SARPY 5G | 09 - Nebraska | ALL | 48.7
GEN-2020-025 & GEN-2020-028 | 999921 - 999922 | None | 09 - Nebraska | ALL | NA

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 28SP Fault Current 3-Phase (kA) | Request In Service 28SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2020-025-028 | 09 - Nebraska | 635200 | RAUN 3 | 345 | 25.9141 | 26.0897 | 0.17554
GEN-2020-025-028 | 09 - Nebraska | 645451 | S3451 3 | 345 | 19.9481 | 20.8745 | 0.92635
GEN-2020-025-028 | 09 - Nebraska | 645454 | S3454 3 | 345 | 24.5255 | 26.349 | 1.8235
GEN-2020-025-028 | 09 - Nebraska | 645455 | S3455 3 | 345 | 28.8065 | 31.1681 | 2.3615
GEN-2020-025-028 | 09 - Nebraska | 645456 | S3456 3 | 345 | 31.6639 | 33.7444 | 2.0805
GEN-2020-025-028 | 09 - Nebraska | 645459 | S3459 3 | 345 | 23.079 | 24.4951 | 1.4161
GEN-2020-025-028 | 09 - Nebraska | 645740 | S3740 3 | 345 | 17.5106 | 18.0137 | 0.5031
GEN-2020-025-028 | 09 - Nebraska | 645761 | S3761 3 | 345 | 22.1706 | 23.752 | 1.5814
GEN-2020-025-028 | 09 - Nebraska | 646214 | S1214 5 | 161 | 10.8864 | 11.5056 | 0.6192
GEN-2020-025-028 | 09 - Nebraska | 646221 | S1221 5 | 161 | 32.2441 | 34.1504 | 1.9063
GEN-2020-025-028 | 09 - Nebraska | 646231 | S1231 5 | 161 | 38.8484 | 41.6029 | 2.7546
GEN-2020-025-028 | 09 - Nebraska | 646232 | S1232 5 | 161 | 24.6391 | 25.4994 | 0.86027
GEN-2020-025-028 | 09 - Nebraska | 646233 | S1233 5 | 161 | 26.3711 | 27.7838 | 1.4127
GEN-2020-025-028 | 09 - Nebraska | 646234 | S1234 5 | 161 | 23.8132 | 24.9841 | 1.1708
GEN-2020-025-028 | 09 - Nebraska | 646249 | S1249 5 | 161 | 21.2707 | 23.0885 | 1.8178
GEN-2020-025-028 | 09 - Nebraska | 646251 | S1251 5 | 161 | 29.7899 | 30.8777 | 1.0878
GEN-2020-025-028 | 09 - Nebraska | 646253 | S1253 5 | 161 | 23.1472 | 24.4495 | 1.3023
GEN-2020-025-028 | 09 - Nebraska | 646254 | S1254 5 | 161 | 25.8947 | 29.1028 | 3.2081
GEN-2020-025-028 | 09 - Nebraska | 646255 | S1255 5 | 161 | 42.7991 | 46.4893 | 3.6902
GEN-2020-025-028 | 09 - Nebraska | 646256 | S1256 5 | 161 | 19.7854 | 21.0676 | 1.2822
GEN-2020-025-028 | 09 - Nebraska | 646259 | S1259 5 | 161 | 33.5866 | 36.2222 | 2.6357
GEN-2020-025-028 | 09 - Nebraska | 646260 | S1260 5 | 161 | 33.0153 | 36.5594 | 3.5442
GEN-2020-025-028 | 09 - Nebraska | 646278 | S1278 5 | 161 | 24.9079 | 26.1351 | 1.2272
GEN-2020-025-028 | 09 - Nebraska | 646281 | S1281 5 | 161 | 22.7047 | 27.4164 | 4.7117
GEN-2020-025-028 | 09 - Nebraska | 646287 | S1287 5 | 161 | 16.5187 | 18.6274 | 2.1086
GEN-2020-025-028 | 09 - Nebraska | 646361 | S1361 5 | 161 | 34.9225 | 38.6595 | 3.737
GEN-2020-025-028 | 09 - Nebraska | 646362 | S1362 5 | 161 | 32.1765 | 36.1288 | 3.9524
GEN-2020-025-028 | 09 - Nebraska | 646363 | S1363 5 | 161 | 21.7076 | 29.0156 | 7.308
GEN-2020-025-028 | 09 - Nebraska | 647014 | S914A 8 | 69 | 10.6137 | 10.8203 | 0.20664
GEN-2020-025-028 | 09 - Nebraska | 647079 | 979TP 8 | 69 | 6.5872 | 6.662 | 0.074814
GEN-2020-025-028 | 09 - Nebraska | 647846 | S6846 8 | 69 | 6.9874 | 7.0669 | 0.079482
GEN-2020-025-028 | 09 - Nebraska | 647900 | S900 8 | 69 | 7.5874 | 7.6737 | 0.086313
GEN-2020-025-028 | 09 - Nebraska | 647914 | S914 8 | 69 | 7.3345 | 7.4368 | 0.10232
GEN-2020-025-028 | 09 - Nebraska | 647921 | S921 8 | 69 | 25.1072 | 25.5456 | 0.43838
GEN-2020-025-028 | 09 - Nebraska | 647960 | S960 8 | 69 | 7.0029 | 7.0886 | 0.085611
GEN-2020-025-028 | 09 - Nebraska | 647979 | S979 8 | 69 | 6.4469 | 6.5194 | 0.072465
GEN-2020-025-028 | 09 - Nebraska | 647988 | S988 8 | 69 | 2.7345 | 2.7599 | 0.025382
GEN-2020-025-028 | 09 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 16.7063 | 16.9132 | 0.20683
GEN-2020-025-028 | 09 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.272 | 8.4378 | 0.16579
GEN-2020-025-028 | 09 - Nebraska | 650185 | WAGENER 3 | 345 | 20.0197 | 20.4321 | 0.41247
GEN-2020-025-028 | 09 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 20.124 | 20.4571 | 0.33303
GEN-2020-025-028 | 09 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 24.8856 | 25.178 | 0.29242
GEN-2020-025-028 | 09 - Nebraska | 650285 | WAGENER 7 | 115 | 31.1417 | 31.5029 | 0.36124
GEN-2020-043-044-045 | 09 - Nebraska | 87487 | J748POI | 345 | 12.5496 | 12.6013 | 0.051707
GEN-2020-043-044-045 | 09 - Nebraska | 541510 | HOLT 7 | 345 | 9.6194 | 9.6561 | 0.036721
GEN-2020-043-044-045 | 09 - Nebraska | 635000 | CBLUFFS3 | 345 | 30.3131 | 31.3919 | 1.0787
GEN-2020-043-044-045 | 09 - Nebraska | 635001 | CBLUFFS5 | 161 | 37.3479 | 38.2604 | 0.91244
GEN-2020-043-044-045 | 09 - Nebraska | 635003 | SUB701 5 | 161 | 20.1214 | 20.493 | 0.37157
GEN-2020-043-044-045 | 09 - Nebraska | 635004 | SUB701 8 | 69 | 16.7828 | 16.9182 | 0.13543
GEN-2020-043-044-045 | 09 - Nebraska | 635005 | SUB702 5 | 161 | 19.6671 | 20.009 | 0.34188
GEN-2020-043-044-045 | 09 - Nebraska | 635013 | PNYCRK 3 | 345 | 27.6867 | 28.5737 | 0.88708
GEN-2020-043-044-045 | 09 - Nebraska | 635014 | OVRLND 3 | 345 | 25.9766 | 26.7543 | 0.77772
GEN-2020-043-044-045 | 09 - Nebraska | 635016 | STHLND 3 | 345 | 27.6539 | 28.5394 | 0.88549
GEN-2020-043-044-045 | 09 - Nebraska | 635200 | RAUN 3 | 345 | 25.9141 | 26.0897 | 0.17554
GEN-2020-043-044-045 | 09 - Nebraska | 635201 | RAUN 5 | 161 | 27.4377 | 27.5797 | 0.14193
GEN-2020-043-044-045 | 09 - Nebraska | 635202 | NEAL S 5 | 161 | 19.0332 | 19.1213 | 0.088031
GEN-2020-043-044-045 | 09 - Nebraska | 635203 | NEAL N 5 | 161 | 26.0088 | 26.1406 | 0.13175
GEN-2020-043-044-045 | 09 - Nebraska | 635220 | INTCHG 5 | 161 | 14.8602 | 14.9221 | 0.061905
GEN-2020-043-044-045 | 09 - Nebraska | 635230 | LIBERTY5 | 161 | 25.2965 | 25.4233 | 0.1268
GEN-2020-043-044-045 | 09 - Nebraska | 635252 | IDA CO W 3 | 345 | 10.1696 | 10.2139 | 0.044225
GEN-2020-043-044-045 | 09 - Nebraska | 640139 | COOPER 3 | 345 | 25.1867 | 25.4193 | 0.23263
GEN-2020-043-044-045 | 09 - Nebraska | 640226 | HOSKINS3 | 345 | 11.8501 | 11.8983 | 0.048198
GEN-2020-043-044-045 | 09 - Nebraska | 640300 | OAKLAND7 | 115 | 7.7758 | 7.817 | 0.041178
GEN-2020-043-044-045 | 09 - Nebraska | 640377 | TEKAMAH5 | 161 | 8.8258 | 8.8998 | 0.074021
GEN-2020-043-044-045 | 09 - Nebraska | 640378 | TEKAMAH7 | 115 | 8.2725 | 8.3251 | 0.052604
GEN-2020-043-044-045 | 09 - Nebraska | 645100 | FC1A 5 | 161 | 27.4831 | 28.4162 | 0.9331
GEN-2020-043-044-045 | 09 - Nebraska | 645451 | S3451 3 | 345 | 19.9481 | 20.8745 | 0.92635
GEN-2020-043-044-045 | 09 - Nebraska | 645454 | S3454 3 | 345 | 24.5255 | 26.349 | 1.8235
GEN-2020-043-044-045 | 09 - Nebraska | 645455 | S3455 3 | 345 | 28.8065 | 31.1681 | 2.3615
GEN-2020-043-044-045 | 09 - Nebraska | 645456 | S3456 3 | 345 | 31.6639 | 33.7444 | 2.0805
GEN-2020-043-044-045 | 09 - Nebraska | 645458 | S3458 3 | 345 | 28.3754 | 28.8804 | 0.50501
GEN-2020-043-044-045 | 09 - Nebraska | 645459 | S3459 3 | 345 | 23.079 | 24.4951 | 1.4161
GEN-2020-043-044-045 | 09 - Nebraska | 645740 | S3740 3 | 345 | 17.5106 | 18.0137 | 0.5031
GEN-2020-043-044-045 | 09 - Nebraska | 645761 | S3761 3 | 345 | 22.1706 | 23.752 | 1.5814
GEN-2020-043-044-045 | 09 - Nebraska | 646201 | S1201 5 | 161 | 29.9085 | 30.8835 | 0.97501
GEN-2020-043-044-045 | 09 - Nebraska | 646206 | S1206 5 | 161 | 42.5006 | 44.3112 | 1.8106
GEN-2020-043-044-045 | 09 - Nebraska | 646209 | S1209 5 | 161 | 41.1532 | 44.5947 | 3.4415
GEN-2020-043-044-045 | 09 - Nebraska | 646210 | S1210 5 | 161 | 26.4097 | 27.2463 | 0.8366
GEN-2020-043-044-045 | 09 - Nebraska | 646211 | S1211 5 | 161 | 33.5773 | 34.7953 | 1.2181
GEN-2020-043-044-045 | 09 - Nebraska | 646216 | S1216 5 | 161 | 28.8351 | 29.8453 | 1.0103
GEN-2020-043-044-045 | 09 - Nebraska | 646217 | S1217 5 | 161 | 31.1907 | 32.4542 | 1.2635
GEN-2020-043-044-045 | 09 - Nebraska | 646220 | S1220 5 | 161 | 26.7852 | 27.5737 | 0.78849
GEN-2020-043-044-045 | 09 - Nebraska | 646221 | S1221 5 | 161 | 32.2441 | 34.1504 | 1.9063
GEN-2020-043-044-045 | 09 - Nebraska | 646226 | S1226 5 | 161 | 23.2059 | 23.9862 | 0.78034
GEN-2020-043-044-045 | 09 - Nebraska | 646227 | S1227 5 | 161 | 30.2289 | 31.6296 | 1.4007
GEN-2020-043-044-045 | 09 - Nebraska | 646231 | S1231 5 | 161 | 38.8484 | 41.6029 | 2.7546
GEN-2020-043-044-045 | 09 - Nebraska | 646232 | S1232 5 | 161 | 24.6391 | 25.4994 | 0.86027
GEN-2020-043-044-045 | 09 - Nebraska | 646233 | S1233 5 | 161 | 26.3711 | 27.7838 | 1.4127
GEN-2020-043-044-045 | 09 - Nebraska | 646234 | S1234 5 | 161 | 23.8132 | 24.9841 | 1.1708
GEN-2020-043-044-045 | 09 - Nebraska | 646235 | S1235 5 | 161 | 28.4584 | 30.1568 | 1.6984
GEN-2020-043-044-045 | 09 - Nebraska | 646236 | S1236 5 | 161 | 17.3091 | 17.9469 | 0.63777
GEN-2020-043-044-045 | 09 - Nebraska | 646237 | S1237 5 | 161 | 16.8893 | 17.4964 | 0.60712
GEN-2020-043-044-045 | 09 - Nebraska | 646244 | S1244 5 | 161 | 21.1389 | 21.5985 | 0.45952
GEN-2020-043-044-045 | 09 - Nebraska | 646250 | S1250 5 | 161 | 32.5177 | 33.921 | 1.4032
GEN-2020-043-044-045 | 09 - Nebraska | 646251 | S1251 5 | 161 | 29.7899 | 30.8777 | 1.0878
GEN-2020-043-044-045 | 09 - Nebraska | 646252 | S1252 5 | 161 | 19.2204 | 20.6335 | 1.4131
GEN-2020-043-044-045 | 09 - Nebraska | 646253 | S1253 5 | 161 | 23.1472 | 24.4495 | 1.3023
GEN-2020-043-044-045 | 09 - Nebraska | 646254 | S1254 5 | 161 | 25.8947 | 29.1028 | 3.2081
GEN-2020-043-044-045 | 09 - Nebraska | 646255 | S1255 5 | 161 | 42.7991 | 46.4893 | 3.6902
GEN-2020-043-044-045 | 09 - Nebraska | 646256 | S1256 5 | 161 | 19.7854 | 21.0676 | 1.2822
GEN-2020-043-044-045 | 09 - Nebraska | 646259 | S1259 5 | 161 | 33.5866 | 36.2222 | 2.6357
GEN-2020-043-044-045 | 09 - Nebraska | 646286 | S1286 5 | 161 | 25.0679 | 25.7624 | 0.69449
GEN-2020-043-044-045 | 09 - Nebraska | 646291 | S1291 5 | 161 | 7.4008 | 7.4783 | 0.077494
GEN-2020-043-044-045 | 09 - Nebraska | 646297 | S1297 5 | 161 | 17.84 | 18.2663 | 0.42632
GEN-2020-043-044-045 | 09 - Nebraska | 646298 | S1298 5 | 161 | 27.307 | 28.2535 | 0.94652
GEN-2020-043-044-045 | 09 - Nebraska | 646299 | S1299 5 | 161 | 25.9755 | 26.7186 | 0.74302
GEN-2020-043-044-045 | 09 - Nebraska | 646305 | S1305 5 | 161 | 26.0154 | 26.8741 | 0.85873
GEN-2020-043-044-045 | 09 - Nebraska | 646341 | S1341 5 | 161 | 25.3422 | 26.155 | 0.81278
GEN-2020-043-044-045 | 09 - Nebraska | 646345 | S1345 5 | 161 | 14.8398 | 15.314 | 0.47422
GEN-2020-043-044-045 | 09 - Nebraska | 646347 | S1347 | 161 | 25.0786 | 27.8558 | 2.7773
GEN-2020-043-044-045 | 09 - Nebraska | 646361 | S1361 5 | 161 | 34.9225 | 38.6595 | 3.737
GEN-2020-043-044-045 | 09 - Nebraska | 646367 | S1367 5 | 161 | 17.8672 | 18.5973 | 0.73005
GEN-2020-043-044-045 | 09 - Nebraska | 647006 | S906 N 8 | 69 | 31.1628 | 31.6459 | 0.4831
GEN-2020-043-044-045 | 09 - Nebraska | 647104 | MUD LNG8 | 69 | 13.9789 | 14.1388 | 0.1599
GEN-2020-043-044-045 | 09 - Nebraska | 647291 | S991 E 8 | 69 | 12.3826 | 12.4609 | 0.078237
GEN-2020-043-044-045 | 09 - Nebraska | 647422 | FREM B 8 | 69 | 13.9027 | 13.9745 | 0.071783
GEN-2020-043-044-045 | 09 - Nebraska | 647902 | S902 8 | 69 | 8.6239 | 8.6962 | 0.072337
GEN-2020-043-044-045 | 09 - Nebraska | 647906 | S906 S 8 | 69 | 31.5225 | 31.9762 | 0.45376
GEN-2020-043-044-045 | 09 - Nebraska | 647907 | S907 8 | 69 | 17.2047 | 17.3955 | 0.19083
GEN-2020-043-044-045 | 09 - Nebraska | 647909 | S909 8 | 69 | 25.6537 | 26.1157 | 0.46201
GEN-2020-043-044-045 | 09 - Nebraska | 647911 | S911 8 | 69 | 20.3679 | 20.6124 | 0.2445
GEN-2020-043-044-045 | 09 - Nebraska | 647913 | S913 8 | 69 | 15.5457 | 15.6979 | 0.15213
GEN-2020-043-044-045 | 09 - Nebraska | 647916 | S916 8 | 69 | 22.7794 | 23.1188 | 0.33949
GEN-2020-043-044-045 | 09 - Nebraska | 647917 | S917 8 | 69 | 24.7839 | 25.1818 | 0.39787
GEN-2020-043-044-045 | 09 - Nebraska | 647918 | S918 8 | 69 | 21.8495 | 22.1807 | 0.33111
GEN-2020-043-044-045 | 09 - Nebraska | 647919 | S919 8 | 69 | 20.5573 | 20.8356 | 0.27829
GEN-2020-043-044-045 | 09 - Nebraska | 647921 | S921 8 | 69 | 25.1072 | 25.5456 | 0.43838
GEN-2020-043-044-045 | 09 - Nebraska | 647928 | S928 8 | 69 | 16.1815 | 16.3606 | 0.17914
GEN-2020-043-044-045 | 09 - Nebraska | 647930 | S930 8 | 69 | 20.5725 | 20.8673 | 0.2948
GEN-2020-043-044-045 | 09 - Nebraska | 647937 | S937 8 | 69 | 8.7397 | 8.8092 | 0.069423
GEN-2020-043-044-045 | 09 - Nebraska | 647939 | S939 8 | 69 | 19.1992 | 19.4684 | 0.26925
GEN-2020-043-044-045 | 09 - Nebraska | 647940 | S940 8 | 69 | 20.0108 | 20.2913 | 0.28052
GEN-2020-043-044-045 | 09 - Nebraska | 647942 | S942 8 | 69 | 15.2599 | 15.4322 | 0.17226
GEN-2020-043-044-045 | 09 - Nebraska | 647950 | S950 8 | 69 | 19.4319 | 19.6839 | 0.25204
GEN-2020-043-044-045 | 09 - Nebraska | 647983 | S983 8 | 69 | 6.8164 | 6.8854 | 0.068917
GEN-2020-043-044-045 | 09 - Nebraska | 647984 | S984 8 | 69 | 7.5462 | 7.5996 | 0.053434
GEN-2020-043-044-045 | 09 - Nebraska | 650185 | WAGENER 3 | 345 | 20.0197 | 20.4321 | 0.41247
GEN-2020-043-044-045 | 09 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 20.124 | 20.4571 | 0.33303
GEN-2020-043-044-045 | 09 - Nebraska | 652564 | SIOUXCY3 | 345 | 15.4493 | 15.5177 | 0.068351
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X