## Executive Summary
Executive Summary: Group 04, Group 08 and Group 09 Interim Availability Interconnection System Impact Study
Interconnection Customers GEN-2019-018 (Group 04), GEN-2019-001 (Group 08) and GEN-2018-070 (Group 09) have requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
Models Used in Study
Power Flow Analysis: DIS1701TC
Summer: 2020 (20SP)
Spring: 2020 (20G)
Winter: 2019 (19WP)
Author: CF Power Ltd.
Published: 12/02/2021

## Revision History
Revision History
Date | Author | Change Description
2021-12-02 | CF Power | First Draft

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | Service | Area | POI | Status
GEN-2019-001 | 08 - North Oklahoma/South Central Kansas |  | DIS-19-1 | Wind | 25 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-018 | 04 - Northwest Kansas |  | DIS-19-1 | Thermal | 15.56 | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2018-070 | 09 - Nebraska |  | DIS-18-2 | Wind | 18.31 | ER/NR | WAPA | Utica Junction 230 kV substation | DISIS STAGE
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 2.5 | ER | SPS | Wolfforth 115kV | DISIS STAGE
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 4.2 | ER/NR | SPS | SPS Erskine 115kV | DISIS STAGE
GEN-2016-005 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | ER/NR | SUNC | Clark-Thistle 345kV | DISIS STAGE
GEN-2016-034 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 90 | ER | WAPA | Laramie River Station (GEN-2016-023 Tap)-Sidney 345kV | withdrawn
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | ER/NR | AEPW | Chisholm-Gracemont 345kV | DISIS STAGE
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | ER | SPS | Swisher 115kV | DISIS STAGE
GEN-2016-049 | 03 - Spearville | 18 | DIS-17-1 | Wind | 310.2 | ER | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 300 | ER | OKGE | Renfrow 345kV | DISIS STAGE
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 54 | ER/NR | SPS | Lakeview-Brownfield 69kV line | DISIS STAGE
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 108 | ER/NR | SPS | Bailey County 115kV | DISIS STAGE
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 100 | ER/NR | SPS | Yoakum-Seagraves 115kV circuit | DISIS STAGE
GEN-2016-093 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 70 | ER | NPPD | Bobcat 115kV | withdrawn
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 250.7 | ER/NR | WAPA | Fort Thompson-Leland Olds 345kV | DISIS STAGE
GEN-2016-107 | 01 - Woodward | 18 | DIS-17-1 | Wind | 141.75 | ER/NR | WFEC | Okeene-Cederdale 138kV Line | DISIS STAGE
GEN-2016-109 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 102 | ER/NR | NPPD | Fairbury 115kV | withdrawn
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | ER/NR | AEPW | Shidler 138kV | DISIS STAGE
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | ER/NR | NPPD | Turtle Creek 345kV | withdrawn
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 64 | ER | SPS | Hobbs-Yoakum 230kV | DISIS STAGE
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | ER | SPS | Newhart 115kV | DISIS STAGE
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 42 | ER/NR | WERE | Creswell 69kV Sub | DISIS STAGE
GEN-2017-001 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 250 | ER/NR | NPPD | Sweetwater 345kV | withdrawn
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | ER/NR | SUNC | Elm Creek - Summit 345kV | DISIS STAGE
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 195 | ER | WERE | Marmaton - Litchfield 161kV | DISIS STAGE
GEN-2017-006 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 73.6 | ER | NPPD | Moore (GEN-2015-088 Tap)-Pauline 345kV | withdrawn
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | ER | SPS | Pleasant Hill 230kV sub | DISIS STAGE
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | ER | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | withdrawn
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302.5 | ER | WERE | Neosho - Caney River 345kV | DISIS STAGE
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | ER | WAPA | Rhame 230kV Sub | DISIS STAGE
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | ER/NR | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 201.6 | ER/NR | SPS | Newhart-Potter County 230kV | DISIS STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | ER/NR | SUNC | Mingo 345kV | DISIS STAGE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | ER/NR | WAPA | Underwood - Philip Tap 230kV | DISIS STAGE
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 190 | ER/NR | SUNC | Thistle 345kV sub | DISIS STAGE
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | DISIS STAGE
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | ER/NR | WFEC | Frogville 138kV sub | DISIS STAGE
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | ER/NR | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | ER/NR | OKGE | El Reno SW 138kV switch station | DISIS STAGE
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | ER | NPPD | Wildhorse - Covalt 115kV | withdrawn
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | ER/NR | SPS | Finney - Lamar 345kV | DISIS STAGE
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | ER/NR | WFEC | Snyder 138kV | DISIS STAGE
GEN-2017-037 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 20 | ER | NPPD | Bobcat 115kV | withdrawn
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | ER | SPS | Needmore 230kV sub | DISIS STAGE
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | ER/NR | SPS | Cole 115kV | DISIS STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | ER/NR | WAPA | Neset 230kV | DISIS STAGE
GEN-2017-049 | 03 - Spearville | 18 | DIS-17-1 | Solar | 50 | ER | MIDW | Tap Pawnee Valley - Hanston 69kV | DISIS STAGE
GEN-2017-050 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 25 | ER | WERE | Tap Neosho â€“ Crawford 69kV | DISIS STAGE
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | DISIS STAGE
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | DISIS STAGE
GEN-2017-053 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 50 | ER | WFEC | Tap Hollister SW - PSO Walters 69kV | DISIS STAGE
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | ER/NR | LES | Wagener 115kV Sub | withdrawn
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | ER/NR | AEPW | Hosston 69kV | DISIS STAGE
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | ER | SPS | Hereford Northeast 115kV | DISIS STAGE
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | ER/NR | SPS | TUCO 230kV | DISIS STAGE
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | ER | EMDE | LaRussell Energy Center 161kV | DISIS STAGE
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | ER/NR | WAPA | Underwood - Wayside 230kV | DISIS STAGE
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-066 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 150.75 | ER/NR | WFEC | Oney 138kV Sub | DISIS STAGE
GEN-2017-067 | 01 - Woodward | 18 | DIS-17-1 | Solar | 200.25 | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | ER/NR | WERE | Wichita 345kV | DISIS STAGE
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 3.6 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | ER/NR | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | ER/NR | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | ER/NR | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | ER/NR | AEPW | Pryor Junction 138kV sub | DISIS STAGE
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | ER/NR | OKGE | Hugo-Sunnyside 345kV | DISIS STAGE
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | ER/NR | AEPW | Chamber Springs 161kV sub | DISIS STAGE
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | ER/NR | AEPW | Explorer Claremore Tap EXCLART4 | DISIS STAGE
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 300 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | DISIS STAGE
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 49.88 | ER | SPS | Hart Industrial 115kV sub | DISIS STAGE
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | ER | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 300 | ER | SPS | Amarillo South-Swisher 230kV | DISIS STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | ER | EMDE | Asbury Plant 161kV | DISIS STAGE
GEN-2017-083 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 100 | ER/NR | SUNC | Mingo 115kV | DISIS STAGE
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 89.25 | ER | SPS | Newhart-Swisher 230kV | DISIS STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | ER/NR | NPPD | Friend 115kV | DISIS STAGE
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | ER/NR | WERE | Viola 345kV | DISIS STAGE
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | ER/NR | SPS | Clovis Interchange 115kV | DISIS STAGE
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | ER | KCPL | Adrian 161kV sub | DISIS STAGE
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 26.25 | ER | SPS | Lamton 115kV | DISIS STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | ER/NR | WAPA | Fort Thompson-Huron 230kV | DISIS STAGE
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | ER/NR | WAPA | Underwood 115kV Sub | DISIS STAGE
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | ER/NR | SPS | Texas County 115kV | DISIS STAGE
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | ER/NR | SPS | Hobbs 230kV | DISIS STAGE
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
AshburyRetired | 08 - North Oklahoma/South Central Kansas | 17.5 | DIS-17-1-PQ | Retired Coal | 198 | ER | EMDE | Asbury Plant 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 | ER | WAPA
ASGI-2016-009 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 3 | ER | SPS | Wolfforth 12.47kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 | ER | NPPD | Gerald Gentleman Station 345kV | withdrawn
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 | ER | WAPA | Laramie River-Stegall 345kV Line | withdrawn
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | withdrawn
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | withdrawn
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | withdrawn
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | withdrawn
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-135 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-136 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-140 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-143 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-144 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-002 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.35 | ER | SPS | SP-Yuma 115kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 0 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
ASGI-2015-006 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Solar | 9 | ER | SWPA | Tupelo 138kV
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Nelson 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 | ER/NR | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 | ER/NR | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 | ER/NR | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 | ER | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-029 | 01 - Woodward | 14 | DIS-15-1 | Wind | 161 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/ON SCHEDULE
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 | ER | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 | ER | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 | ER | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-030 | 02 - Hitchland | 11 | DIS-13-2 | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 | ER | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 30 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 | ER | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 | ER | SPS | Pleasant Hill 69kV | Commerical Operation
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 | ER | SPS | Herring 115kV | Commerical Operation
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 | ER | SPS | Hendricks 69kV | Commerical Operation
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commerical Operation
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commerical Operation
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 | ER | WERE | Westar 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 | ER | AECI | Remington 138kV | GIA Executed
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 | ER | SPS | Martin 115kV | Commerical Operation
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 | ER | OTP

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Group | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Requested Capacity or Upgrade Details | Scenario 1: Status or Available ERIS MW | Scenario 2: Status or Available NRIS MW | Note
GEN-2019-001 | DISIS-2019-001 | 08 | 2018-12-31 | ER | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | NA | 25 | 0 | NA | Detailed analysis on the overloaded lines can be found in the "G19-001 Overload DF Analysis " Tab.
GEN-2019-018 | DISIS-2019-001 | 04 | 2020-03-01 | ER/NR | Saxman 115kV substation | NA | 15.56 | 15.56 | 0
GEN-2018-070 | DISIS-2018-002 | 09 | 2019-12-31 | ER/NR | Utica Junction 230 kV substation | NA | 18.31 | 18.31 | 0

## Constraints Summary
Project | Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name | Details
GEN-2018-070 | 00NR | NR | Thermal | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 19WP, 20SP | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 110.47 |  |  |  | Rebuld St Joe to Cooper 345 kV line to achieve emergency rating of 1321MVA
GEN-2018-070 | 00NR | NR | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 19WP, 20SP | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 319 | 319 | 134.69 |  |  |  | Rebuld Hays to GRTBEND 230 kV line to achieve emergency rating of 430MVA
GEN-2018-070 | 00NR | NR | Thermal | 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 | 20SP | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 600 | 600 | 103.76 |  |  |  | upgrade Postrock Transformer T1 to 623MVA
GEN-2018-070 | 00NR | NR | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 19WP, 20SP | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | 1195 | 1195 | 123.55 |  |  |  | Rebuld STRANGR to 87TH 345 kV line to achieve emergency rating of 1477MVA
GEN-2018-070 | 00NR | NR | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 19WP | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 1195 | 1195 | 106.79 |  |  |  | Rebuld STRANGR to IATAN 345 Kv ckt1 to achieve emergency rating of 1277MVA
GEN-2018-070 | 00NR | NR | Thermal | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 19WP | 631160 LIME CK L2 5 161 630198 LIME CK J2 8 69.0 1 | 1195 | 1195 | 105.55 |  |  |  | Rebuld STRANGR to IATAN 345 Kv ckt2 to achieve emergency rating of 1262MVA
GEN-2018-070 | 00NR | NR | Thermal | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 19WP, 20SP | 588240 GEN-2016-149 345 588250 GEN-2016-174 345 1 | 1314 | 1314 | 104.73 |  |  |  | Rebuld 87TH to CRAIG 345 Kv ckt to achieve emergency rating of 1377MVA
GEN-2018-070 | 00NR | NR | Thermal | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 19WP, 20SP | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | 1195 | 1195 | 115.22 |  |  |  | Rebuld ST JOE to EASTOWN 345 Kv ckt to achieve emergency rating of 1377MVA
GEN-2018-070 | 00NR | NR | Thermal | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 19WP, 20SP | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | 1195 | 1195 | 125.12 |  |  |  | Rebuld ST JOE to NASHUA 345 Kv ckt to achieve emergency rating of 1496MVA
GEN-2018-070 | 00NR | NR | Thermal | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 19WP, 20SP | 'P42:345:NPPD:BKR-CPR-3322' | 1195 | 1195 | 132.76 |  |  |  | Rebuld ST JOE to COOPER 345 Kv ckt to achieve emergency rating of 1587MVA
GEN-2018-070 | 00NR | NR | Thermal | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 19WP, 20SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | 1314 | 1314 | 104.53 |  |  |  | Rebuld EASTOWN to G17-030 TAP 345 Kv ckt to achieve emergency rating of 1374MVA
GEN-2018-070 | 00NR | NR | Thermal | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 19WP, 20SP | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 1432 | 1434 | 114.74 |  |  |  | Rebuld HAWTH to NASHUA 345 Kv ckt to achieve emergency rating of 1646MVA
GEN-2018-070 | 00NR | NR | Thermal | 542980 NASHUA 7 345 997747 NASHUA11 161 11 | 19WP, 20G | 656061 PETERSON8 69.0 656099 STOLTZPARK8 69.0 1 | 650 | 715 | 129.59 |  |  |  | upgrade NASHUA Transformer 11 to achieve emergency rating of 927MVA
GEN-2018-070 | 00NR | NR | Thermal | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 19WP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 1314 | 1314 | 102.19 |  |  |  | Rebuld IATAN to G17-030 TAP 345 Kv ckt to achieve emergency rating of 1343MVA
GEN-2018-070 | 00NR | NR | Thermal | 635200 RAUN 3 345 645451 S3451 3 345 1 | 19WP, 20SP | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 956 | 956 | 122.77 |  |  |  | Rebuld RAUN to S3451 345 Kv ckt to achieve emergency rating of 1174MVA
GEN-2018-070 | 00NR | NR | Thermal | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 19WP, 20SP | 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | 217 | 217 | 127.38 |  |  |  | Rebuld RAUN to TEKAMAH 161 Kv ckt to achieve emergency rating of 277MVA
GEN-2018-070 | 00NR | NR | Thermal | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 20SP | P12:345:OPPD-MEC:S3451-RAUN' | 212 | 212 | 143.58 |  |  |  | Rebuild Webster to Wright 161 kV circuit to achieve Emergency 305 MVA
GEN-2018-070 | 00NR | NR | Thermal | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 20SP | 'P12:345:OPPD-MEC:S3451-RAUN' | 206 | 206 | 119.84 |  |  |  | Rebuild Wright to Wall Lake 161 kV circuit to achieve Emergency rating of 247 MVA
GEN-2018-070 | 00NR | NR | Thermal | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 20SP | 'P12:345:OPPD-MEC:S3451-RAUN' | 201 | 201 | 113.05 |  |  |  | Rebuild Franklin to Wall Lake 161 kV circuit to achieve Emergency rating of 228 MVA
GEN-2018-070 | 00NR | NR | Thermal | 640126 E.COL. 4 230 997447 COL.EAST T3 115 1 | 20SP | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 187 | 187 | 109.58 |  |  |  | upgrade EAST COL Transformer 1 to achieve emergency rating of 205MVA
GEN-2018-070 | 00NR | NR | Thermal | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 20SP | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 120 | 120 | 128.09 |  |  |  | Rebuild ONEILL to SPENCER 115 kV circuit to achieve Emergency rating of 154 MVA
GEN-2018-070 | 00NR | NR | Thermal | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 20SP | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 120 | 121 | 130.54 |  |  |  | Rebuild SPENCER to FTRANDL 115 kV circuit to achieve Emergency rating of 158 MVA
GEN-2018-070 | 00NR | NR | Thermal | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 20SP | 'P23:345:OPPD:S3451-S3454' | 256 | 256 | 103.82 |  |  |  | Rebuld TEKAMAH to S1226 161 Kv ckt to achieve emergency rating of 266MVA
GEN-2018-070 | 00NR | NR | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 19WP, 20SP | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 720 | 720 | 125.1 |  |  |  | Model Correction
GEN-2018-070 | 00NR | NR | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 19WP, 20SP | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1 | 720 | 720 | 141.6 |  |  |  | Model Correction
GEN-2018-070 | 00NR | NR | Thermal | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 20SP | 652526 UTICAJC4 230 655484 RASMUSN-ER4 230 1 | 120 | 120 | 116.67 |  |  |  | Rebuld UTICAJC to NAPA JCT 115 Kv ckt to achieve emergency rating of 141MVA
GEN-2018-070 | 00NR | NR | Thermal | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 20SP | 'P12:345:OPPD-MEC:S3451-RAUN' | 41 | 41 | 110.01 |  |  |  | Rebuild PASSWART to SWEAZY G 69 kV circuit to achieve Emergency rating of 46 MVA
GEN-2018-070 | 00NR | NR | Thermal | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 19WP | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 478 | 478 | 108.5 |  |  |  | Rebuild SIDNEY TS4 to SIDNEY MB4 230kV circuit to achieve Emergency rating of 519 MVA
GEN-2018-070 | 00NR | NR | Thermal | 659210 SIDNEY__-MB4 230 997096 SDQ KV2A 230 1 | 19WP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 400 | 500 | 105.78 |  |  |  | upgrade SIDNEY Transformer to achieve emergency rating of 529MVA
GEN-2019-001 | 08ALL | ER | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G | Base Case | 956 | 956 | 104.44 |  |  |  | Rebuld NEOSHO to G17-009 TAP 345 Kv ckt to achieve normal rating of 999MVA
GEN-2019-001 | 08ALL | ER | Thermal | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 19WP, 20SP | Base Case | 1141 | 1202 | 107.26 |  |  |  | Rebuld WAVERLY to LACYGNE 345 Kv ckt to achieve normal rating of 1224MVA
GEN-2019-018 | 00NR | NR | Thermal | 532791 BENTON 7 345 997909 BENT TX-2 138 1 | 19WP, 20SP | 'P23:345:WERE:BENT_345-50::' | 400 | 440 | 122.59 |  |  |  | upgrade Benton Transformer T2 to achieve emergency rating of 540MVA
GEN-2019-018 | 00NR | NR | Thermal | 533040 EVANS N4 138 997937 WICH TX-12 138 1 | 20SP | 'P23:345:WERE:BENT_345-110::' | 400 | 430 | 101.93 |  |  |  | upgrade WICHITA Transformer T12 to achieve emergency rating of 439MVA
GEN-2019-018 | 00NR | NR | Thermal | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 19WP, 20SP | 532771 RENO 7 345 587884 G16-111-TAP 345 1 | 280 | 308 | 107.38 |  |  |  | upgrade Circle Transformer T1 to achieve emergency rating of 331MVA
GEN-2019-018 | 00NR | NR | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 19WP, 20SP | 'P23:345:WERE:SWIS_345-5::' | 1099 | 1195 | 111.63 |  |  |  | Rebuld STRANGR to 87TH 345 kV line to achieve emergency rating of 1334MVA
GEN-2019-018 | 00NR | NR | Thermal | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 19WP | 'P23:345:WERE:SWIS_345-5::' | 1314 | 1314 | 101.18 |  |  |  | Rebuld 87TH to CRAIG 345 Kv ckt to achieve emergency rating of 1330MVA
G19-018 | 00NR | NR | Thermal | 656353 HOPE5 161 656355 HUMBOLDT8 69.0 1 | 20SP | System Intact | 84 | 84 | 100.35 |  |  |  | upgrade Transformer to 85MVA

## G19-001 Overload DF Analysis
This tab shows the impact of DISIS1701 queue projects (within Group 08) on the overloaded lines limiting interconnection of G19-001
532793 NEOSHO 7 345 588544 G17-009-TAP 345 1
Project | 588503:G17-005-GEN1 | 588543:G17-009-GEN1 | 588663:G17-022-GEN1 | 588813:G17-040-GEN1 | 588817:G17-040-GEN2 | 588993:G17-061-GEN1 | 589063:G17-068-GEN1 | 589093:G17-071-GEN1 | 589103:G17-072-GEN1 | 589113:G17-073-GEN1 | 589123:G17-074-GEN1 | 589153:G17-077-GEN1 | 589243:G17-086-GEN1 | 589245:G17-086-GEN2 | 589303:G17-092-GEN1 | 589307:G17-092-GEN2 | Total
DF | -0.06832 | 0.74438 | -0.06677 | -0.0018 | -0.0018 | -0.03383 | 0.10452 | 0.01206 | 0.01206 | -0.03605 | -0.033 | -0.0308 | 0.09243 | 0.09243 | -0.0018 | -0.0018
Size | 190 | 302 | 65 | 200 |  | 101.5 | 103.5 | 124.7 | 52.2 | 72.5 | 72.5 | 124.7 | 150 |  | 200
MW Impact | -12.9808 | 224.8028 | -4.34 | -0.36 | 0 | -3.4337 | 10.8178 | 1.5039 | 0.62953 | -2.6136 | -2.3925 | -3.8408 | 13.8645 | 0 | -0.36 | 0 | 221.297
532799 WAVERLY7 345 542981 LACYGNE7 345 1
Project | 588503:G17-005-GEN1 | 588543:G17-009-GEN1 | 588663:G17-022-GEN1 | 588813:G17-040-GEN1 | 588817:G17-040-GEN2 | 588993:G17-061-GEN1 | 589063:G17-068-GEN1 | 589093:G17-071-GEN1 | 589103:G17-072-GEN1 | 589113:G17-073-GEN1 | 589123:G17-074-GEN1 | 589153:G17-077-GEN1 | 589243:G17-086-GEN1 | 589245:G17-086-GEN2 | 589303:G17-092-GEN1 | 589307:G17-092-GEN2 | Total
DF | -0.00329 | 0.02453 | 0.03911 | 0.03858 | 0.03858 | 0.02559 | 0.10454 | 0.05026 | 0.05026 | 0.02423 | 0.02572 | 0.02743 | 0.09813 | 0.09813 | 0.03858 | 0.03858
Size | 190 | 302 | 65 | 200 |  | 101.5 | 103.5 | 124.7 | 52.2 | 72.5 | 72.5 | 124.7 | 150 |  | 200
MW Impact | -0.6251 | 7.4081 | 2.5421 | 7.716 | 0 | 2.5974 | 10.8199 | 6.2674 | 2.6236 | 1.7567 | 1.8647 | 3.4205 | 14.7195 | 0 | 7.716 |  | 68.8268
Highlighted cell indicates a distribution factor higher than 3%

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | CONTNAME (id)
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.24817 | 106.56 | 532771 RENO 7 345 587884 G16-111-TAP 345 1 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.24829 | 106.29 | 532771 RENO 7 345 587884 G16-111-TAP 345 1 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.22711 | 102.19 | P23:345:WERE:RENO_345-150::G16111TAP' | 4688X
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.22724 | 102 | P23:345:WERE:RENO_345-150::G16111TAP' | 4688X
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.22711 | 102.19 | P23:345:WERE:RENO_345-140::G16111TAP' | 4689X
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.22724 | 102 | P23:345:WERE:RENO_345-140::G16111TAP' | 4689X
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.06688 | 101.18 | 'P23:345:WERE:SWIS_345-5::' | 4711
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04999 | 111.63 | 'P23:345:WERE:SWIS_345-5::' | 4711
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532791 BENTON 7 345 997906 BENT TX-2 138 1 | 400 | 440 | 0.03264 | 105.42 | 'P23:345:WERE:BENT_345-50::' | 4664
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532986 BENTON 4 138 997906 BENT TX-2 138 1 | 400 | 440 | 0.03251 | 100.55 | 'P23:345:WERE:BENT_345-50::' | 4664
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.24821 | 105.49 | 532771 RENO 7 345 587884 G16-111-TAP 345 1 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 280 | 308 | 0.24833 | 104.3 | 532771 RENO 7 345 587884 G16-111-TAP 345 1 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.22715 | 103.58 | P23:345:WERE:RENO_345-150::G16111TAP' | 4689X
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.22715 | 103.58 | P23:345:WERE:RENO_345-140::G16111TAP' | 4688X
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 280 | 308 | 0.22727 | 102.46 | P23:345:WERE:RENO_345-150::G16111TAP' | 4689X
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 280 | 308 | 0.22727 | 102.46 | P23:345:WERE:RENO_345-140::G16111TAP' | 4688X
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.04987 | 103.25 | 'P23:345:WERE:SWIS_345-5::' | 4711
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532796 WICHITA7 345 997937 WICH TX-12 138 1 | 400 | 430 | 0.0369 | 103.9 | 'P23:345:WERE:BENT_345-110::' | 4663
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 533040 EVANS N4 138 997937 WICH TX-12 138 1 | 400 | 430 | 0.03678 | 101.93 | 'P23:345:WERE:BENT_345-110::' | 4663
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532791 BENTON 7 345 997909 BENT TX-2 138 1 | 400 | 440 | 0.03164 | 122.59 | 'P23:345:WERE:BENT_345-50::' | 4664
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532986 BENTON 4 138 997909 BENT TX-2 138 1 | 400 | 440 | 0.03151 | 116.38 | 'P23:345:WERE:BENT_345-50::' | 4664
Thermal | 08ALL | 1 | 19WP | GEN-2019-001 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 | 956 | 0.0798 | 104.44 | System Intact | Base Case
Thermal | 08ALL | 1 | 20G | GEN-2019-001 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 | 956 | 0.07977 | 104.19 | System Intact | Base Case
Thermal | 08ALL | 1 | 20G | GEN-2019-001 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 | 1254 | 0.08074 | 103.1 | System Intact | Base Case
Thermal | 08ALL | 1 | 20SP | GEN-2019-001 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 | 1202 | 0.08088 | 107.26 | System Intact | Base Case
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09936 | 104.06 | 'P42:345:NPPD:BKR-CPR-3304' | 2044
Thermal | 09NR | 2 | 20G | GEN-2018-070 | 'FROM -> TO' | 542980 NASHUA 7 345 997756 NASHUA11 161 11 | 650 | 715 | 0.03453 | 109.68 | 87486 J748GENTIE 345 87487 J748POI 345 1 | 87486 J748GENTIE 345 87487 J748POI 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10577 | 135.9 | 'P12:345:AEPW:R.S.S.-7:COGENT7' | 424
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0749 | 112.67 | 'P12:345:AEPW:R.S.S.-7:COGENT7' | 424
Thermal | 09NR | 2 | 20G | GEN-2018-070 | 'FROM -> TO' | 543028 NASHUA-5 161 997756 NASHUA11 161 11 | 650 | 715 | 0.03453 | 108.45 | 'P12:069:WERE:2MAD-TEC_69_1::' | 4431
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09982 | 110.47 | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 541199 ST JOE 3 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 319 | 319 | 0.03774 | 134.69 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 319 | 319 | 0.03784 | 106.95 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 101.61 | 'P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE' | 1477
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10607 | 141.56 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07519 | 118.22 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03229 | 112.01 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04056 | 115.28 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04946 | 108.13 | 'P55:345:KCPL:CRAIG_BUS_22' | 1604
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04435 | 100.5 | 'P55:345:KCPL:CRAIG_BUS_33' | 1605
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04711 | 102.89 | 'P23:345:SUNC:MG_BRKXX' | 3847
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04703 | 100.09 | 'P23:345:SUNC:SB_BRK488' | 3849
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04639 | 105.87 | 'P23:345:WERE:WICH_345-50::' | 4715
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04488 | 100.84 | 338142 5ISES% 161 338143 1ISES U1 26.0 1 | 338142 5ISES% 161 338143 1ISES U1 26.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04509 | 100.62 | 338142 5ISES% 161 338143 1ISES U1 26.0 2 | 338142 5ISES% 161 338143 1ISES U1 26.0 2
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04382 | 100.83 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04719 | 102.98 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05257 | 103.13 | 344012 7HPW-N 345 344013 7HPW-S 345 1 | 344012 7HPW-N 345 344013 7HPW-S 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04758 | 102.15 | 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1 | 344225 1CAL G1 25.0 344224 7CALAWY 1 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04436 | 100.4 | 346119 2PERRYVIL 69.0 345489 4PERRYVIL 138 1 | 346119 2PERRYVIL 69.0 345489 4PERRYVIL 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06959 | 106.83 | 'P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006' | 1682
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06959 | 106.05 | 'P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006' | 1682
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07963 | 106.08 | 'P11:022:NPPD:COOPER1G:1:1160' | 1801
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05247 | 117.94 | 'P11:022:NPPD:COOPER1G:1:1160' | 1801
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05247 | 117.8 | 'P11:022:NPPD:COOPER1G:1:1160' | 1801
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 101.04 | 'P11:022:NPPD:COOPER1G:1:1160' | 1801
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06127 | 109.78 | 'P11:023:NPPD:GENTLM1G:1:757' | 1802
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06127 | 109 | 'P11:023:NPPD:GENTLM1G:1:757' | 1802
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05247 | 118.33 | 'P11:023:NPPD:GENTLM1G:1:757' | 1802
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05247 | 118.18 | 'P11:023:NPPD:GENTLM1G:1:757' | 1802
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 102.26 | 'P11:023:NPPD:GENTLM1G:1:757' | 1802
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06127 | 109.8 | 'P11:024:NPPD:GENTLM2G:2:757' | 1803
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06127 | 109.02 | 'P11:024:NPPD:GENTLM2G:2:757' | 1803
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05247 | 118.31 | 'P11:024:NPPD:GENTLM2G:2:757' | 1803
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05247 | 118.16 | 'P11:024:NPPD:GENTLM2G:2:757' | 1803
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 102.32 | 'P11:024:NPPD:GENTLM2G:2:757' | 1803
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05591 | 117.93 | 'P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB' | 1884
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05591 | 117.79 | 'P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB' | 1884
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04443 | 103.77 | 346119 2PERRYVIL 69.0 345489 4PERRYVIL 138 2 | 346119 2PERRYVIL 69.0 345489 4PERRYVIL 138 2
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10591 | 140.6 | 'P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB' | 1886
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07503 | 117.26 | 'P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB' | 1886
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.05205 | 123.59 | 'P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB' | 1886
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03214 | 111.12 | 'P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB' | 1886
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.1049 | 103.03 | 'P13:115-345:NPPD:ANTELOPE:T1' | 1907
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04719 | 102.99 | 500910 WKRAFT 6 230 500915 G1WKRAFT 13.8 1 | 500910 WKRAFT 6 230 500915 G1WKRAFT 13.8 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10591 | 140.61 | 'P42:345:NPPD:BKR-C-3322-2' | 2041
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07503 | 117.27 | 'P42:345:NPPD:BKR-C-3322-2' | 2041
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.05206 | 123.94 | 'P42:345:NPPD:BKR-C-3322-2' | 2041
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03214 | 111.13 | 'P42:345:NPPD:BKR-C-3322-2' | 2041
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.07039 | 108.61 | 'P42:345:NPPD:BKR-CE-3306' | 2042
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.07039 | 107.81 | 'P42:345:NPPD:BKR-CE-3306' | 2042
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05109 | 102.65 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.1059 | 142.66 | 'P42:345:NPPD:BKR-CPR-3304' | 2044
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07503 | 119.29 | 'P42:345:NPPD:BKR-CPR-3304' | 2044
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.05048 | 101.84 | 'P42:345:NPPD:BKR-CPR-3304' | 2044
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03213 | 113.05 | 'P42:345:NPPD:BKR-CPR-3304' | 2044
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.08038 | 106.49 | 'P42:345:NPPD:BKR-CPR-3310' | 2045
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.0319 | 101.45 | 'P42:345:NPPD:BKR-CPR-3310' | 2045
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05149 | 114.3 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.1059 | 140.44 | 'P42:345:NPPD:BKR-CPR-3322' | 2047
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07503 | 117.1 | 'P42:345:NPPD:BKR-CPR-3322' | 2047
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.05344 | 126.05 | 'P42:345:NPPD:BKR-CPR-3322' | 2047
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03213 | 110.99 | 'P42:345:NPPD:BKR-CPR-3322' | 2047
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06129 | 109.84 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06129 | 109.05 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05247 | 118.32 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05247 | 118.17 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03201 | 105.56 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 102.33 | 'P42:345:NPPD:BKR-GGS-3304' | 2048
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.08529 | 105.85 | 'P42:345:NPPD:BKR-HOS-3308' | 2052
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.07464 | 118.14 | 'P42:345:NPPD:BKR-HOS-3308' | 2052
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.07464 | 117.32 | 'P42:345:NPPD:BKR-HOS-3308' | 2052
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04899 | 107.02 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.03814 | 111.56 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10685 | 102.96 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10551 | 140.39 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07466 | 116.95 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07117 | 112.34 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0499 | 122.07 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0499 | 121.93 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04655 | 103.83 | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04815 | 101.7 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 532775 87TH 7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10643 | 104.88 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10547 | 140.27 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07463 | 116.83 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07014 | 111.96 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.04936 | 121.38 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.04936 | 121.26 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.08747 | 107.27 | 'P42:345:NPPD:BKR-HOS-3322' | 2055
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06823 | 114.5 | 'P42:345:NPPD:BKR-HOS-3322' | 2055
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06823 | 113.61 | 'P42:345:NPPD:BKR-HOS-3322' | 2055
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05272 | 119.16 | 'P42:345:NPPD:BKR-KEY-3310' | 2056
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05272 | 119 | 'P42:345:NPPD:BKR-KEY-3310' | 2056
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.0446 | 104.24 | 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1 | 541162 DOGWDSTG 18.0 541225 PHILL 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 100.52 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04462 | 104.35 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9 | 601002 ADAMS 3 345 3WXFMR ADAMS 3 9
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04677 | 104.2 | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | 601004 WILMART3 345 601072 SHEAS LK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.08977 | 107.68 | 'P42:345:NPPD:BKR-SC-3306' | 2065
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06911 | 113.6 | 'P42:345:NPPD:BKR-SC-3306' | 2065
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06911 | 112.73 | 'P42:345:NPPD:BKR-SC-3306' | 2065
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07963 | 106.19 | 'P11:345:OPPD:NEBCTY1G' | 2216
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 101.62 | 'P11:345:OPPD:NEBCTY1G' | 2216
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07963 | 106.83 | 'P11:345:OPPD:NEBCTY1G:LT' | 2217
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 101.1 | 'P11:345:OPPD:NEBCTY1G:LT' | 2217
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.07963 | 105.4 | 'P11:345:OPPD:NEBCTY2G' | 2218
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 101.99 | 'P11:345:OPPD:NEBCTY2G' | 2218
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10605 | 141.3 | 'P12:345:GMO-OPPD:S3458-HOLT' | 2307
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07517 | 117.95 | 'P12:345:GMO-OPPD:S3458-HOLT' | 2307
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.04816 | 106.55 | 'P12:345:GMO-OPPD:S3458-HOLT' | 2307
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.03293 | 101.7 | 'P12:345:GMO-OPPD:S3458-HOLT' | 2307
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03227 | 111.72 | 'P12:345:GMO-OPPD:S3458-HOLT' | 2307
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 102.59 | 601011 SHERCO 3 345 600000 SHERC31G 24.0 1 | 601011 SHERCO 3 345 600000 SHERC31G 24.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04439 | 101.64 | 601011 SHERCO 3 345 600001 SHERC32G 24.0 1 | 601011 SHERCO 3 345 600001 SHERC32G 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10663 | 143.58 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.07571 | 119.84 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06826 | 115.27 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06826 | 114.43 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05511 | 119.62 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05511 | 119.53 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.03536 | 103.2 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03275 | 112.1 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03207 | 110.01 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 103.57 | 601011 SHERCO 3 345 600002 SHERC33G 26.0 1 | 601011 SHERCO 3 345 600002 SHERC33G 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11062 | 106.55 | 'P14:69:OPPD:S3455 T1 REACTOR' | 2484
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05335 | 101.7 | 'P14:69:OPPD:S3455 T1 REACTOR' | 2484
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04542 | 101.24 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04526 | 102.9 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9 | 601044 BRIGGS RD 3 345 3WXFMR 10008630_001 9
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09715 | 114.43 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09702 | 115.27 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06461 | 119.53 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06448 | 119.62 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04994 | 103.2 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03789 | 126.91 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11062 | 106.55 | 'P22:345:OPPD:S3451 FT CAL1G:LT' | 2547
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05335 | 101.7 | 'P22:345:OPPD:S3451 FT CAL1G:LT' | 2547
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04804 | 100.78 | 605578 J512_COLFDR 34.5 605577 J512_MAINTR 115 2 | 605578 J512_COLFDR 34.5 605577 J512_MAINTR 115 2
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04468 | 104.34 | 606077 PLS VLY B1 9 34.5 602056 PLS VLLY W 5 161 1 | 606077 PLS VLY B1 9 34.5 602056 PLS VLLY W 5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09715 | 114.43 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09702 | 115.27 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06461 | 119.53 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06448 | 119.62 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04994 | 103.2 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03789 | 126.91 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04463 | 103.84 | 606078 PLS VLY B2 9 34.5 602056 PLS VLLY W 5 161 2 | 606078 PLS VLY B2 9 34.5 602056 PLS VLLY W 5 161 2
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04552 | 101.41 | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 608615 ARROWHD4 230 699448 AWHD PST 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09715 | 114.43 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09702 | 115.27 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06461 | 119.53 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06448 | 119.62 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04994 | 103.2 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03789 | 126.91 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04748 | 100.59 | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 608698 HOYT LK7 115 608700 43L TAP7 115 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04713 | 105.04 | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 608698 HOYT LK7 115 608700 43L TAP7 115 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09721 | 114.42 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09708 | 115.27 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06462 | 119.53 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0645 | 119.62 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04949 | 103.82 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03758 | 127.38 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11062 | 106.55 | 'P23:345:OPPD:S3458-S3456' | 2608
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05335 | 101.7 | 'P23:345:OPPD:S3458-S3456' | 2608
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04689 | 104.47 | 608698 HOYT LK7 115 608700 43L TAP7 115 1 | 608698 HOYT LK7 115 608700 43L TAP7 115 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04444 | 100.69 | 613330 RICE 5 161 693755 JADE AVE 161 1 | 613330 RICE 5 161 693755 JADE AVE 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09721 | 114.42 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09708 | 115.27 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06462 | 119.53 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0645 | 119.62 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04949 | 103.82 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03758 | 127.38 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04452 | 101.1 | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1 | 631139 HAZLTON3 345 631191 HCKRYCK3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04526 | 103.34 | 631199 KILLDEER3 345 631206 QUINN3 345 1 | 631199 KILLDEER3 345 631206 QUINN3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09721 | 114.42 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09708 | 115.27 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06462 | 119.53 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0645 | 119.62 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04949 | 103.82 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03758 | 127.38 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11062 | 106.55 | 'P45:345:OPPD:S3451-54&FCS 1G:LT' | 2778
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05335 | 101.7 | 'P45:345:OPPD:S3451-54&FCS 1G:LT' | 2778
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04834 | 102.42 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1 | 631206 QUINN3 345 636199 BLACKHAWK 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04446 | 100.34 | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1 | 635200 RAUN 3 345 635214 NEAL 4G 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09721 | 114.42 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09708 | 115.27 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06462 | 119.53 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0645 | 119.62 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 256 | 256 | 0.04949 | 103.82 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03758 | 127.38 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 102.8 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 100.62 | 640077 BEATRCE9 34.5 3WXFMR BEATRICE T1 1 | 640077 BEATRCE9 34.5 3WXFMR BEATRICE T1 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04417 | 104.45 | 640341 SEWARD 9 34.5 3WXFMR SEWARD T1 1 | 640341 SEWARD 9 34.5 3WXFMR SEWARD T1 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05207 | 122.81 | 656301 WELSBRG G 69.0 656309 WELBRGEASTT8 69.0 1 | 656301 WELSBRG G 69.0 656309 WELBRGEASTT8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.05777 | 123.55 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04517 | 101.69 | 681523 GENOA 5 161 681522 GENOA53G 24.0 1 | 681523 GENOA 5 161 681522 GENOA53G 24.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04683 | 102.81 | 681527 BVR CRK5 161 681528 HARMONY5 161 1 | 681527 BVR CRK5 161 681528 HARMONY5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04446 | 100.84 | 681532 WABACO 5 161 681543 ALMA 5 161 1 | 681532 WABACO 5 161 681543 ALMA 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.04522 | 103.04 | System Intact | Base Case
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1195 | 1195 | 0.03171 | 100.22 | System Intact | Base Case
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.09191 | 105.9 | 'P55:345:KCPL:CRAIG_BUS_11' | 1603
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.09173 | 105.44 | 542982 IATAN 7 345 3WXFMR IATAN11 11 | 542982 IATAN 7 345 3WXFMR IATAN11 11
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 107.67 | 'P12:069:UMZW:# 126 #: BB IN ND. FAULT ON AGT-BB-CD2-CDJ-CD-LE 69 KV' | 3999
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 108.45 | 'P12:069:UMZW:# 126 #: BB IN ND. FAULT ON AGT-BB-CD2-CDJ-CD-LE 69 KV' | 3999
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10603 | 103.49 | 'P12:115:UMZW:# 1844 #: YJ IN SD. YJ-UJ LINE FAULT' | 4099
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10603 | 103.49 | 'P12:115:UMZZ:# 2188 #: NJ-YJ IN SD. YANKTON JUNCTION - NAPA JUNCTION TAP.' | 4102
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05741 | 121.36 | 'P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX' | 4116
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05728 | 121.54 | 'P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX' | 4116
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.04942 | 119.58 | 'P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON' | 4149
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0493 | 119.76 | 'P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON' | 4149
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10603 | 103.49 | 'P13:115:UMZW:# 239 #: MC IN MT. LOSS OF TRANSFORMER (KY6A).' | 4162
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.12041 | 112.66 | 'P13:230:UMZW:# 237 #: GF IN MN. LOSS OF TRANSFORMER (KV8A).' | 4169
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11432 | 102.15 | 'P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION W' | 4316
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14178 | 110.7 | 'P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION W' | 4317
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11432 | 102.15 | 'P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION W' | 4319
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11432 | 102.19 | 'P23:345:UMZW:# 2422 #: GI IN NE. GI 1796 BKR FAULT' | 4335
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11432 | 102.19 | 'P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT' | 4336
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT' | 4338
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 2427 #: GI IN NE. GI 1392 BKR FAULT' | 4340
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 2428 #: GI IN NE. GI 1192 BKR FAULT' | 4341
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 2445 #: GI IN NE. GI KU1A TRANSFORMER FAULT & GI 1396 STUCK BKR' | 4351
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 2446 #: GI IN NE. GI-FT2 LINE FAULT & GI 1196 STUCK BKR' | 4352
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P23:345:UMZW:# 628 #: BEF IN ND. BREAKER FAULT (396; 492; 292)' | 4354
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08735 | 107.47 | 'P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)' | 4375
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08723 | 108.21 | 'P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)' | 4375
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0618 | 120.34 | 'P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)' | 4375
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06168 | 120.51 | 'P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)' | 4375
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P44:345:UMZW:# 2436 #: GF IN NE. GI KU4B SW SHUNT FAULT & GI 1192 STUCK BKR' | 4415
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.65 | 'P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT' | 4418
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 1 | 1195 | 1195 | 0.09239 | 106.79 | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 631199 KILLDEER3 345 631048 EMERY 5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08602 | 107.93 | 'P45:345:UMZW:# 1327 #: FT2 IN SD.' | 4420
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.0859 | 108.7 | 'P45:345:UMZW:# 1327 #: FT2 IN SD.' | 4420
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14174 | 110.65 | 'P45:345:UMZW:# 1999 #: WHT IN SD. WHT 345 KV S BUS FAULT' | 4423
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.04956 | 100.04 | 'P14:115:WERE:JARB_115_SS::' | 4631
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09119 | 105.55 | 631160 LIME CK L2 5 161 630198 LIME CK J2 8 69.0 1 | 631160 LIME CK L2 5 161 630198 LIME CK J2 8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09119 | 105.55 | 631160 LIME CK L2 5 161 630198 LIME CK J2 8 69.0 1 | 631160 LIME CK L2 5 161 630198 LIME CK J2 8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 542982 IATAN 7 345 2 | 1195 | 1195 | 0.09055 | 104.33 | 656459 ESTRTAP8 69.0 656591 ESTRJCT8 69.0 1 | 656459 ESTRTAP8 69.0 656591 ESTRJCT8 69.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04464 | 113.62 | 'P23:345:WERE:87TH_345_BKRS::' | 4662
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.04906 | 104.15 | 'P42:345:NPPD:BKR-RW-3302' | 2064
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1314 | 1314 | 0.05644 | 104.73 | 588240 GEN-2016-149 345 588250 GEN-2016-174 345 1 | 588240 GEN-2016-149 345 588250 GEN-2016-174 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1195 | 1195 | 0.1233 | 115.22 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05858 | 110.56 | 'P23:345:WERE:STRA_345-100::' | 4695
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.0516 | 108.91 | 'P23:345:WERE:STRA_345-96P::' | 4698
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04647 | 114.3 | 'P23:345:WERE:STRA_345-99::' | 4703
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.1217 | 123 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.03824 | 102.52 | 'P23:345:WERE:SWIS_345-5::' | 4711
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.12194 | 125.12 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1 | 601029 LKFLDXL3 345 631138 LAKEFLD3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.09803 | 111.11 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11008 | 102.19 | FTTHOMPSON-GRANDPRAIRIE-TLINE-REACTOR-CKT1 | 5002
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11008 | 116.45 | GRANDPRAIRIE-HOLT-TLINE-REACTOR-CKT1 | 5005
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03181 | 105.89 | GRANDPRAIRIE-HOLT-TLINE-REACTOR-CKT1 | 5005
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11008 | 102.12 | GRANDPRAIRIE-FTTHOMPSON-TLINE-REACTORS-CKT1 | 5006
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06155 | 106.76 | SIDNEY-KEYSTONE-TLINE-REACTORS-CKT1 | 5011
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06155 | 106.01 | SIDNEY-KEYSTONE-TLINE-REACTORS-CKT1 | 5011
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05274 | 119 | SIDNEY-KEYSTONE-TLINE-REACTORS-CKT1 | 5011
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05274 | 118.84 | SIDNEY-KEYSTONE-TLINE-REACTORS-CKT1 | 5011
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1195 | 1195 | 0.05769 | 109.9 | 656345 EAGLE GR8 69.0 656885 TROY8 69.0 1 | 656345 EAGLE GR8 69.0 656885 TROY8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.13 | 'P12:161:AEPW:CHAMSPR5:FARMING5' | 355
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09731 | 108.33 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09726 | 108.24 | 'P55:345:GMO:SIBLEY_BUS_11:VALID PRIOR TO 6' | 1602
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09187 | 104.28 | 'P55:345:KCPL:CRAIG_BUS_11' | 1603
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 110.04 | 'P55:345:KCPL:HAWTHORN_BUS_20' | 1606
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 107.43 | 'P55:345:KCPL:HAWTHORN_BUS_20' | 1606
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12252 | 131.04 | 'P12:345:NPPD:3517:COOPER 3:ST JOE 3:BTB' | 1886
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03202 | 106.67 | P42:345:NPPD:BKR-PLN-3310-G1650TAP' | 2063X
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11639 | 111.41 | 300039 7FAIRPT 345 541199 ST JOE 3 345 1 | 300039 7FAIRPT 345 541199 ST JOE 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12265 | 131.33 | 'P42:345:NPPD:BKR-C-3322-2' | 2041
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.12281 | 125.69 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0599 | 113.54 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05978 | 113.68 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12317 | 132.76 | 'P42:345:NPPD:BKR-CPR-3322' | 2047
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 107.41 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 106.99 | 'P42:345:NPPD:BKR-HOS-3310' | 2053
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 106.35 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 105.81 | 'P42:345:NPPD:BKR-HOS-3312' | 2054
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.32 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.07 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.32 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.07 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1 | 303028 8COTNWOOD1! 500 334325 8HARTBRG% 500 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.48 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.23 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09488 | 105.56 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09488 | 105.47 | 'P12:345:OPPD-MEC:S3451-RAUN' | 2310
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.86 | 337909 8ANO% 500 337910 1ANO U1 22.0 1 | 337909 8ANO% 500 337910 1ANO U1 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.62 | 337909 8ANO% 500 337910 1ANO U1 22.0 1 | 337909 8ANO% 500 337910 1ANO U1 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.05 | 337909 8ANO% 500 337911 1ANO U2 22.0 1 | 337909 8ANO% 500 337911 1ANO U2 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.81 | 337909 8ANO% 500 337911 1ANO U2 22.0 1 | 337909 8ANO% 500 337911 1ANO U2 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08611 | 100.88 | 337957 8KEO% 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338162 8W.MEMPHIS% 500 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08599 | 101.62 | 337957 8KEO% 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338162 8W.MEMPHIS% 500 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.09 | 'P12:345:OPPD:S3456-S3458' | 2316
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09477 | 106.54 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09414 | 107.38 | 'P14:69:OPPD:S3456 T4 REACTOR' | 2485
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09415 | 108.92 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09412 | 107.27 | 'P22:345:OPPD:S3451-S3459' | 2550
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09444 | 107.86 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09361 | 107.62 | 'P23:345:OPPD:S3451-S3454' | 2580
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08623 | 102.74 | 344000 7ZACKARY 345 344011 7HUGHES 345 1 | 344000 7ZACKARY 345 344011 7HUGHES 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.0861 | 103.5 | 344000 7ZACKARY 345 344011 7HUGHES 345 1 | 344000 7ZACKARY 345 344011 7HUGHES 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09726 | 108.11 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09517 | 110.09 | 'P23:345:OPPD:S3451-S3454&FCS 1G' | 2581
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0972 | 108.76 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0959 | 108.11 | 'P42:345:OPPD:S3451-S3454&FCS 1G' | 2632
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0972 | 108.19 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09604 | 109 | 'P44:345:OPPD:S3458-HOL&R1' | 2776
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09723 | 108.06 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09528 | 106.78 | 'P45:345:OPPD:S3451-S3459&T3' | 2781
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0924 | 106.97 | 'P23:345:SUNC:MG_BRKXX' | 3847
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0924 | 106.01 | 'P23:345:SUNC:MG_BRKXX' | 3847
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09234 | 105 | 'P23:345:SUNC:SB_BRK488' | 3849
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09229 | 110.56 | 'P23:345:SUNC:SB_BRK488' | 3849
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09731 | 108.44 | 'P23:345:WERE:87TH_345_BKRS::' | 4662
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09731 | 108.33 | 'P23:345:WERE:87TH_345_BKRS::' | 4662
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09853 | 111.26 | P42:345:NPPD:BKR-AXT-3304-G1650TAP' | 2038X
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.12255 | 132.37 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.0859 | 100.48 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08577 | 101.22 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06035 | 113.53 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06023 | 113.68 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 105.45 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.3 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09258 | 109.8 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09257 | 107.49 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08679 | 102.31 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08667 | 103.06 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.09 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 103.99 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09331 | 105.03 | 532772 STRANGR7 345 532775 87TH 7 345 1 | 532772 STRANGR7 345 532775 87TH 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08584 | 100.2 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06041 | 112.74 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06029 | 112.89 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.093 | 106.21 | 532772 STRANGR7 345 532775 87TH 7 345 1 | 532772 STRANGR7 345 532775 87TH 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0915 | 102.87 | 539645 DCBEEF3 115 539671 FTDODGE3 115 1 | 539645 DCBEEF3 115 539671 FTDODGE3 115 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.0915 | 102.84 | 539645 DCBEEF3 115 539671 FTDODGE3 115 1 | 539645 DCBEEF3 115 539671 FTDODGE3 115 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.11008 | 116.98 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.11022 | 117 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09225 | 108.03 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08604 | 102.38 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08592 | 103.13 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1 | 348944 7SANDBURG 345 636635 OAKGROV3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09225 | 104.3 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.10997 | 120.79 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09735 | 109.01 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09735 | 109 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 103.91 | 542982 IATAN 7 345 3WXFMR IATAN11 11 | 542982 IATAN 7 345 3WXFMR IATAN11 11
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09221 | 102.68 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09218 | 106.13 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.10051 | 110.51 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.10048 | 110.89 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.11614 | 127.61 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.4 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.15 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.4 | 511456 O.K.U.-7 345 589030 GEN-2017-065 345 1 | 511456 O.K.U.-7 345 589030 GEN-2017-065 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.15 | 511456 O.K.U.-7 345 589030 GEN-2017-065 345 1 | 511456 O.K.U.-7 345 589030 GEN-2017-065 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09795 | 110.53 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09217 | 106.27 | 631048 EMERY 5 161 629069 EMERYST1 18.0 1 | 631048 EMERY 5 161 629069 EMERYST1 18.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.17 | 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | 514802 SOONER 4 138 514805 SOONER1G 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.93 | 514802 SOONER 4 138 514805 SOONER1G 22.0 1 | 514802 SOONER 4 138 514805 SOONER1G 22.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.16 | 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | 514803 SOONER 7 345 514806 SOONER2G 20.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.92 | 514803 SOONER 7 345 514806 SOONER2G 20.0 1 | 514803 SOONER 7 345 514806 SOONER2G 20.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09201 | 105.89 | 631048 EMERY 5 161 629069 EMERYST1 18.0 1 | 631048 EMERY 5 161 629069 EMERYST1 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09235 | 106.64 | 631199 KILLDEER3 345 631048 EMERY 5 161 1 | 631199 KILLDEER3 345 631048 EMERY 5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.93 | 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 | 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.68 | 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1 | 515045 SEMINOL7 345 515041 SEMINL2G 17.1 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.93 | 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.69 | 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1 | 515045 SEMINOL7 345 515042 SEMINL3G 20.9 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09123 | 102.72 | 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1 | 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09123 | 102.63 | 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1 | 635100 RLHILLS3 345 635101 RLHILLS B1 9 34.5 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 106.76 | 636000 WEBSTER3 345 3WXFMR WEB AB 1 | 636000 WEBSTER3 345 3WXFMR WEB AB 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 106.39 | 636000 WEBSTER3 345 3WXFMR WEB AB 1 | 636000 WEBSTER3 345 3WXFMR WEB AB 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.57 | 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1 | 515224 MUSKOGE7 345 515225 MUSKOG5G 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.08923 | 107.68 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09133 | 102.67 | 656423 BURT5 161 656527 OSGOOD5 161 1 | 656423 BURT5 161 656527 OSGOOD5 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.22 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.98 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.52 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.66 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.38 | 515377 CRESENT4 138 587210 GEN-2016-032 138 1 | 515377 CRESENT4 138 587210 GEN-2016-032 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.13 | 515377 CRESENT4 138 587210 GEN-2016-032 138 1 | 515377 CRESENT4 138 587210 GEN-2016-032 138 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09124 | 102.62 | 656423 BURT5 161 656527 OSGOOD5 161 1 | 656423 BURT5 161 656527 OSGOOD5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09106 | 103.34 | 656459 ESTRTAP8 69.0 656591 ESTRJCT8 69.0 1 | 656459 ESTRTAP8 69.0 656591 ESTRJCT8 69.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.56 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.32 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.47 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.23 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.68 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.82 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.93 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.69 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.96 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.1 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.79 | 527894 HOBBS_INT 6 230 589400 GEN-2017-104 230 1 | 527894 HOBBS_INT 6 230 589400 GEN-2017-104 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.55 | 527894 HOBBS_INT 6 230 589400 GEN-2017-104 230 1 | 527894 HOBBS_INT 6 230 589400 GEN-2017-104 230 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 114.98 | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 681521 SENECA 5 161 681523 GENOA 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 112.23 | 681521 SENECA 5 161 681523 GENOA 5 161 1 | 681521 SENECA 5 161 681523 GENOA 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09184 | 102.92 | 87487 J748POI 345 635399 CHEROKEE 3 345 1 | 87487 J748POI 345 635399 CHEROKEE 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09181 | 103.95 | 87487 J748POI 345 635399 CHEROKEE 3 345 1 | 87487 J748POI 345 635399 CHEROKEE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.65 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.41 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.57 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.72 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1 | 531451 MINGO 7 345 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.25 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 530583 POSTROCK7 345 997995 POSTROCK T1 230 1 | 600 | 600 | 0.06601 | 103.76 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 530584 POSTROCK6 230 997995 POSTROCK T1 230 1 | 600 | 600 | 0.06588 | 103.3 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 297 | 297 | 0.03782 | 131.84 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1 | 531469 SPERVIL7 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.09177 | 104.21 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.91 | 532766 JEC N 7 345 532652 JEC U2 26.0 1 | 532766 JEC N 7 345 532652 JEC U2 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.68 | 532766 JEC N 7 345 532652 JEC U2 26.0 1 | 532766 JEC N 7 345 532652 JEC U2 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 105.44 | 532766 JEC N 7 345 532652 JEC U2 26.0 1 | 532766 JEC N 7 345 532652 JEC U2 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.82 | 532766 JEC N 7 345 532652 JEC U2 26.0 1 | 532766 JEC N 7 345 532652 JEC U2 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.95 | 532766 JEC N 7 345 532652 JEC U2 26.0 1 | 532766 JEC N 7 345 532652 JEC U2 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.86 | 532766 JEC N 7 345 532653 JEC U3 26.0 1 | 532766 JEC N 7 345 532653 JEC U3 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.63 | 532766 JEC N 7 345 532653 JEC U3 26.0 1 | 532766 JEC N 7 345 532653 JEC U3 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 105.4 | 532766 JEC N 7 345 532653 JEC U3 26.0 1 | 532766 JEC N 7 345 532653 JEC U3 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.78 | 532766 JEC N 7 345 532653 JEC U3 26.0 1 | 532766 JEC N 7 345 532653 JEC U3 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.92 | 532766 JEC N 7 345 532653 JEC U3 26.0 1 | 532766 JEC N 7 345 532653 JEC U3 26.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.13381 | 104.53 | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | 601004 WILMART3 345 601072 SHEAS LK3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1432 | 1434 | 0.04449 | 102.17 | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 608615 ARROWHD4 230 699448 AWHD PST 230 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1432 | 1434 | 0.04385 | 100.77 | 631048 EMERY 5 161 636300 FLOYD 5 161 1 | 631048 EMERY 5 161 636300 FLOYD 5 161 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 542980 NASHUA 7 345 997747 NASHUA11 161 11 | 650 | 715 | 0.03668 | 129.59 | 656061 PETERSON8 69.0 656099 STOLTZPARK8 69.0 1 | 656061 PETERSON8 69.0 656099 STOLTZPARK8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 1314 | 1314 | 0.13344 | 102.19 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 601014 AS KING3 345 601028 EAU CL 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04399 | 112.56 | 532772 STRANGR7 345 532775 87TH 7 345 1 | 532772 STRANGR7 345 532775 87TH 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 543028 NASHUA-5 161 997747 NASHUA11 161 11 | 650 | 715 | 0.03668 | 129.18 | 656051 NEWHAMPM G 69.0 656099 STOLTZPARK8 69.0 1 | 656051 NEWHAMPM G 69.0 656099 STOLTZPARK8 69.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04211 | 106.86 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 532775 87TH 7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 103.3 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 106.31 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 107.08 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 117.91 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 118.04 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1 | 532797 WOLFCRK7 345 532751 WCGS U1 25.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.87 | 532852 JEC 6 230 532651 JEC U1 26.0 1 | 532852 JEC 6 230 532651 JEC U1 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.67 | 532852 JEC 6 230 532651 JEC U1 26.0 1 | 532852 JEC 6 230 532651 JEC U1 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 105.44 | 532852 JEC 6 230 532651 JEC U1 26.0 1 | 532852 JEC 6 230 532651 JEC U1 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.8 | 532852 JEC 6 230 532651 JEC U1 26.0 1 | 532852 JEC 6 230 532651 JEC U1 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.94 | 532852 JEC 6 230 532651 JEC U1 26.0 1 | 532852 JEC 6 230 532651 JEC U1 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 100.1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.03 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.79 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.62 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.76 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11033 | 114.76 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05303 | 110.15 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11047 | 114.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05319 | 110.21 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.09826 | 102.02 | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 541199 ST JOE 3 345 541400 EASTOWN7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 1000 | 1136 | 0.13412 | 101.93 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 541400 EASTOWN7 345 1 | 1000 | 1136 | 0.12358 | 103.22 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 1195 | 1195 | 0.10003 | 105.58 | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 541199 ST JOE 3 345 640139 COOPER 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.11022 | 119.62 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.07965 | 103.8 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05291 | 114.74 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14166 | 100.04 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14166 | 100.04 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1 | 344000 7ZACKARY 345 345435 7MAYWOOD 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14164 | 100.21 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.12223 | 111.02 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.21 | 541510 HOLT 7 345 541511 ROCKCK7 345 1 | 541510 HOLT 7 345 541511 ROCKCK7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.57 | 541510 HOLT 7 345 541511 ROCKCK7 345 1 | 541510 HOLT 7 345 541511 ROCKCK7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.72 | 541510 HOLT 7 345 541511 ROCKCK7 345 1 | 541510 HOLT 7 345 541511 ROCKCK7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13955 | 101.42 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13168 | 102.94 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.53 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.93 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 101.14 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.87 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 102.04 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.09196 | 100.39 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.07 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.83 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 103.52 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.09196 | 103.05 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 105.58 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 117.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 117.4 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1284 | 100.42 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13395 | 103.01 | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | 601004 WILMART3 345 601072 SHEAS LK3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13199 | 102.68 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 601014 AS KING3 345 601028 EAU CL 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.05218 | 112.35 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 1099 | 1202 | 0.04915 | 100.49 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.04182 | 113.84 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1 | 601029 LKFLDXL3 345 601074 CRANDAL 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.05785 | 104.97 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | 542980 NASHUA 7 345 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 | 1099 | 1195 | 0.04064 | 107.08 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | 542980 NASHUA 7 345 542982 IATAN 7 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14176 | 100.39 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1 | 635580 ARBR HL 3 345 635600 GRIMES 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1437 | 115.31 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 1000 | 1136 | 0.12199 | 109.63 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1 | 542982 IATAN 7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 100.49 | 560062 G15088_T 345 563220 G15088_1 345 1 | 560062 G15088_T 345 563220 G15088_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 104.45 | 560062 G15088_T 345 563220 G15088_1 345 1 | 560062 G15088_T 345 563220 G15088_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 105.21 | 560062 G15088_T 345 563220 G15088_1 345 1 | 560062 G15088_T 345 563220 G15088_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.57 | 560062 G15088_T 345 563220 G15088_1 345 1 | 560062 G15088_T 345 563220 G15088_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.72 | 560062 G15088_T 345 563220 G15088_1 345 1 | 560062 G15088_T 345 563220 G15088_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08852 | 103.35 | 560062 G15088_T 345 640312 PAULINE3 345 1 | 560062 G15088_T 345 640312 PAULINE3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.0884 | 104.12 | 560062 G15088_T 345 640312 PAULINE3 345 1 | 560062 G15088_T 345 640312 PAULINE3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1437 | 106.69 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14166 | 100.22 | 87487 J748POI 345 635200 RAUN 3 345 1 | 87487 J748POI 345 635200 RAUN 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14166 | 100.04 | 87487 J748POI 345 635200 RAUN 3 345 1 | 87487 J748POI 345 635200 RAUN 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03754 | 118.76 | P42:345:NPPD:BKR-AXT-3304-G1650TAP' | 2038X
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06256 | 115.76 | 560347 DIXONCO 230 640227 HOSKINS4 230 1 | 560347 DIXONCO 230 640227 HOSKINS4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06244 | 115.91 | 560347 DIXONCO 230 640227 HOSKINS4 230 1 | 560347 DIXONCO 230 640227 HOSKINS4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 124.88 | 562711 G15_023_1 345 640510 HOLT.CO3 345 1 | 562711 G15_023_1 345 640510 HOLT.CO3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 125.1 | 562711 G15_023_1 345 640510 HOLT.CO3 345 1 | 562711 G15_023_1 345 640510 HOLT.CO3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 119.66 | 562712 G15_023_2 34.5 562711 G15_023_1 345 1 | 562712 G15_023_2 34.5 562711 G15_023_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 119.85 | 562712 G15_023_2 34.5 562711 G15_023_1 345 1 | 562712 G15_023_2 34.5 562711 G15_023_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 119.66 | 562713 G15_023_3 34.5 562711 G15_023_1 345 1 | 562713 G15_023_3 34.5 562711 G15_023_1 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 119.85 | 562713 G15_023_3 34.5 562711 G15_023_1 345 1 | 562713 G15_023_3 34.5 562711 G15_023_1 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.038 | 118.37 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1 | 344011 7HUGHES 345 631143 OTTUMWA3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03785 | 118.37 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.15 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.91 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.55 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.69 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1 | 587884 G16-111-TAP 345 587910 GEN-2016-114 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03785 | 118.37 | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | 345435 7MAYWOOD 345 345992 7SPENCER 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03754 | 118.76 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1 | 541400 EASTOWN7 345 588736 G17-030-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.65 | 588581 G17-013XFMR1 34.5 588580 GEN-2017-013 345 1 | 588581 G17-013XFMR1 34.5 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 104.41 | 588581 G17-013XFMR1 34.5 588580 GEN-2017-013 345 1 | 588581 G17-013XFMR1 34.5 588580 GEN-2017-013 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 103.19 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.95 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.41 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.55 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1 | 588650 GEN-2017-021 345 588654 G17-021-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.79 | 588654 G17-021-TAP 345 589370 GEN-2017-099 345 1 | 588654 G17-021-TAP 345 589370 GEN-2017-099 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 103.55 | 588654 G17-021-TAP 345 589370 GEN-2017-099 345 1 | 588654 G17-021-TAP 345 589370 GEN-2017-099 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09031 | 109.04 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09019 | 109.75 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06492 | 122.7 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.0648 | 122.91 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09036 | 105.7 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09023 | 106.43 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06497 | 119 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06485 | 119.17 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1 | 589024 G17-064-TAP 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03754 | 118.76 | 656025 FRDRCKSB8 69.0 656039 LAWLERTP8 69.0 1 | 656025 FRDRCKSB8 69.0 656039 LAWLERTP8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03754 | 118.76 | 656039 LAWLERTP8 69.0 656061 PETERSON8 69.0 1 | 656039 LAWLERTP8 69.0 656061 PETERSON8 69.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 635201 RAUN 5 161 640377 TEKAMAH5 161 1 | 217 | 217 | 0.03785 | 118.37 | 681519 STONEMAN 161 699010 NED 161 161 1 | 681519 STONEMAN 161 699010 NED 161 161 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13038 | 104.75 | 601004 WILMART3 345 601033 FIELD_N3 345 1 | 601004 WILMART3 345 601033 FIELD_N3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05734 | 118.94 | 601006 SPLT RK3 345 652537 WHITE 3 345 1 | 601006 SPLT RK3 345 652537 WHITE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05722 | 119.14 | 601006 SPLT RK3 345 652537 WHITE 3 345 1 | 601006 SPLT RK3 345 652537 WHITE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13038 | 104.76 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1 | 601032 FIELD_S3 345 601074 CRANDAL 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06071 | 116.71 | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 608615 ARROWHD4 230 699448 AWHD PST 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06059 | 116.86 | 608615 ARROWHD4 230 699448 AWHD PST 230 1 | 608615 ARROWHD4 230 699448 AWHD PST 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 107.51 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.64 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.78 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1 | 635000 CBLUFFS3 345 635023 WSEC 3G 24.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.12853 | 108.4 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.81 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.95 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1 | 635000 CBLUFFS3 345 635024 WSEC 4G 26.0 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13183 | 112.2 | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 635200 RAUN 3 345 640226 HOSKINS3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11241 | 102.87 | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 635200 RAUN 3 345 640226 HOSKINS3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06156 | 121.75 | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 635200 RAUN 3 345 640226 HOSKINS3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06143 | 121.88 | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 635200 RAUN 3 345 640226 HOSKINS3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13967 | 107.59 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13967 | 112.66 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.13255 | 108.21 | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1 | 635368 OBRIEN 3 345 635400 HIGHLND 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14386 | 122.77 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08896 | 108.81 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08883 | 109.6 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.09645 | 102.07 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14386 | 114.98 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08896 | 106.42 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08883 | 107.19 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09442 | 107.07 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09429 | 107.85 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640126 E.COL. 4 230 997447 COL.EAST T3 115 1 | 187 | 187 | 0.03308 | 109.58 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640127 COLMB.E7 115 997447 COL.EAST T3 115 1 | 187 | 187 | 0.03296 | 107.25 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09481 | 107.74 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09469 | 108.47 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.07347 | 123.17 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.07335 | 123.28 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 121 | 0.03037 | 130.54 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03024 | 128.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.14302 | 106.97 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09999 | 112.71 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.09986 | 113.58 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1 | 640226 HOSKINS3 345 640342 SHELCRK3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08849 | 112.78 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08836 | 113.57 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08687 | 106.03 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08675 | 106.77 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06916 | 141.6 | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06904 | 142.56 | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11429 | 116.67 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 635200 RAUN 3 345 645451 S3451 3 345 1 | 956 | 956 | 0.1418 | 110.89 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.07351 | 119.51 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.07339 | 119.65 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640349 SPENCER7 115 652510 FTRANDL7 115 1 | 120 | 121 | 0.03038 | 122.34 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640305 ONEILL 7 115 640349 SPENCER7 115 1 | 120 | 120 | 0.03026 | 119.84 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10718 | 106.73 | 652502 BERSFRD7 115 652524 SIOUXFL7 115 1 | 652502 BERSFRD7 115 652524 SIOUXFL7 115 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0499 | 119.65 | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.04978 | 119.83 | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.04948 | 119.31 | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.04936 | 119.48 | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10609 | 114.48 | 652510 FTRANDL7 115 655490 WHTSWAN-ER7 115 1 | 652510 FTRANDL7 115 655490 WHTSWAN-ER7 115 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05788 | 119.41 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05776 | 119.57 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10603 | 112.82 | 652525 TYNDALL7 115 655490 WHTSWAN-ER7 115 1 | 652525 TYNDALL7 115 655490 WHTSWAN-ER7 115 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.10437 | 102.77 | 652525 TYNDALL7 115 660006 YKNTJCT7 115 1 | 652525 TYNDALL7 115 660006 YKNTJCT7 115 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.15526 | 104.6 | 652526 UTICAJC4 230 655484 RASMUSN-ER4 230 1 | 652526 UTICAJC4 230 655484 RASMUSN-ER4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.1143 | 116.45 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11431 | 102.18 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05788 | 120.71 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05775 | 120.89 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652626 UTICAJC7 115 660026 NAPA JCT7 115 1 | 120 | 120 | 0.11431 | 102.18 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0601 | 116.22 | 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z | 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05997 | 116.41 | 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z | 659105 LELAND_O-BE3 345 659422 LO.LS-GR-BE3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08602 | 102.85 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08589 | 103.59 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06047 | 115.74 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06035 | 115.89 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1 | 659131 LARAMIE_-MB3 345 659426 SD.LS-LR-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08663 | 104.11 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.0865 | 104.85 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06108 | 117.03 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06096 | 117.19 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08688 | 106.02 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08676 | 106.77 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06133 | 118.83 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06121 | 119 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06008 | 116.23 | 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z | 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05996 | 116.42 | 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z | 659160 GROTON__-BE3 345 659423 GR.LS-LO-BE3 345 Z
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06319 | 116.49 | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06307 | 116.63 | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06009 | 116.27 | 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1 | 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05997 | 116.46 | 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1 | 659422 LO.LS-GR-BE3 345 659423 GR.LS-LO-BE3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.75 | 672512 CONDIE 6 138 672522 CD NORTH 6 138 1 | 672512 CONDIE 6 138 672522 CD NORTH 6 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.9 | 672512 CONDIE 6 138 672522 CD NORTH 6 138 1 | 672512 CONDIE 6 138 672522 CD NORTH 6 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 115.72 | 672537 MARTENSVILL6 138 672545 SNI TAP 6 138 1 | 672537 MARTENSVILL6 138 672545 SNI TAP 6 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 115.88 | 672537 MARTENSVILL6 138 672545 SNI TAP 6 138 1 | 672537 MARTENSVILL6 138 672545 SNI TAP 6 138 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 102.83 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.06033 | 116.05 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.06021 | 116.21 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1 | 672637 MARTENSVILL4 230 672639 ABERDEEN 4 230 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08588 | 100.29 | 87486 J748GENTIE 345 87487 J748POI 345 1 | 87486 J748GENTIE 345 87487 J748POI 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.08575 | 101.02 | 87486 J748GENTIE 345 87487 J748POI 345 1 | 87486 J748GENTIE 345 87487 J748POI 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0594 | 116.45 | 87487 J748POI 345 635200 RAUN 3 345 1 | 87487 J748POI 345 635200 RAUN 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05928 | 116.61 | 87487 J748POI 345 635200 RAUN 3 345 1 | 87487 J748POI 345 635200 RAUN 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.0594 | 115.35 | 87487 J748POI 345 635399 CHEROKEE 3 345 1 | 87487 J748POI 345 635399 CHEROKEE 3 345 1
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05928 | 115.5 | 87487 J748POI 345 635399 CHEROKEE 3 345 1 | 87487 J748POI 345 635399 CHEROKEE 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.0691 | 110.9 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1 | 637089 HEARTLD DIV2 345 637088 J583 COL 34.5 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06898 | 111.72 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997096 SDQ KV2A 230 1 | 400 | 500 | 0.04118 | 105.36 | P42:345:NPPD:BKR-AXT-3306-G1650TAP' | 2039X
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997096 SDQ KV2A 230 1 | 400 | 500 | 0.04147 | 102.8 | 640152 CRESTON9 34.5 3WXFMR CRESTON T2 1 | 640152 CRESTON9 34.5 3WXFMR CRESTON T2 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 478 | 478 | 0.04118 | 108.5 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 478 | 478 | 0.04147 | 105.8 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636001 WEBSTER5 161 636050 WRIGHT 5 161 1 | 212 | 212 | 0.10577 | 138.04 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636050 WRIGHT 5 161 636235 WALL LK5 161 1 | 206 | 206 | 0.0749 | 114.78 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.06127 | 102.35 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.06127 | 101.61 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 | 720 | 0.05247 | 114.65 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 | 720 | 0.05247 | 114.5 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 1073 | 1195 | 0.03901 | 102.05 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 636230 FRANKLN5 161 636235 WALL LK5 161 1 | 201 | 201 | 0.03201 | 108.96 | System Intact | Base Case
Thermal | 00NR | 2 | 20SP | GEN-2018-070 | 'FROM -> TO' | 656879 PASSWATR8 69.0 656887 SWEAZY G 69.0 1 | 41 | 41 | 0.03187 | 104.51 | System Intact | Base Case
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997096 SDQ KV2A 230 1 | 400 | 500 | 0.04118 | 105.78 | 'P12:115:SPS:V90.1.CUNN.MADDOX' | 3109
Thermal | 00NR | 2 | 19WP | GEN-2018-070 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997096 SDQ KV2A 230 1 | 400 | 500 | 0.04147 | 103.17 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | 601014 AS KING3 345 601028 EAU CL 3 345 1
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997922 CIRC TX-1 115 1 | 280 | 308 | 0.24834 | 107.38 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1
Thermal | 00NR | 2 | 19WP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997922 CIRC TX-1 115 1 | 280 | 308 | 0.24846 | 106.72 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 533413 CIRCLE 3 115 997925 CIRC TX-1 115 1 | 280 | 308 | 0.24838 | 105.76 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1
Thermal | 00NR | 2 | 20SP | GEN-2019-018 | 'FROM -> TO' | 532871 CIRCLE 6 230 997925 CIRC TX-1 115 1 | 280 | 308 | 0.24851 | 103.12 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1 | 532773 SUMMIT 7 345 587894 G16-122-TAP 345 1

## All Voltage
Project | SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
No Voltage Vialation Identified